## Rect flume Quality check (hidden)
Date | Comments | SIRIS l/s | Refernece l/s | Error | Revision
11th May 2016 | Updated to v3.1 and checked against BS/ISO Annexe D Flume 2 software B=500 b =200 L=1200 H=300 ks0.6mm | 54.77 | 53.1 | 3.145% | 3.1
11th May 2016 | Checked against BS/ISO 4359:2013 example p55 Section 14.3 B-500 b=200 L=1200 ks=0.6mm | 54.77 | 54.9 | -0.2368% | 3.1
11th May 2016 | Checked against BS/ISO Annexe D Flume 2 software B=200 b =100 L=600 H=300 ks0.6mm | 28.21 | 27.7 | 1.841% | 3.1
11th May 2016 | Checked against Tyler-HR Wallingford (b=100 B=200 L=600 Ks=1.5 H=295mm) | 27.5 | 26.37 | 4.285% | 3.1

## Input Data
Appendix A - Survey Data (Tariff)
Site Details |  |  |  |  | Secondary Device
Site name / flow location |  | Ballyrickard WwTW |  |  | Manufacturer |  | Pulsar
Consent Reference |  | 2025/2006 |  |  | Model |  | Ultra 5
Max Daily Volume M3 |  | 31577 |  |  | Serial no |  | F261255
|  | M3/Day | L/Sec | M3/Hr | MCERTS accredited? |  | No
Q Max Instrument |  | 38993.184 | 451.31 | 1624.716 | Telemetry U(t) |  | 2
FFT |  | 31577 | 365.4745 | 1315.7083 | Look Up Table U(lu) |  | 1
DWF |  | 14778 | 171.0417 | 615.75 | Include % Uncertainty above if required enter 0 if not required
Measurement |  | Approach Channel Width - B |  |  |  | Throat Width - b
Height |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
A | (h Max) | 1046 | 1046 | 1042 | 1027 | 650 | 650 | 652 | 654
B | (.5h Max) | 1046 | 1047 | 1043 | 1029 | 648 | 650 | 651 | 654
C | (Zero) | 1045 | 1046 | 1041 | 1036 | 649 | 649 | 650 | 654
[6 empty] | u(br) Uncertainty in equipment |  |  | 1
[6 empty] | u(bm) Uncertainty in measurements |  |  | 1.7321
Staff | Approach Channel & Flume Levels
Location | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
A | 2388 | 2388 | 2390 | 2390 | 2388 | 2389 | 2386 | 2386 | 2390
B |  |  | 2390 | 2391 | 2389 | 2390 | 2387 | 2388 | 2385
[6 empty] | (Uh0) Uncertainty in gauge zero (mm) |  |  | 17
Appendix B - Survey & Compliance Data (Tariff)
Primary Device (Dimensions in mm) |  | Throat Width - b 5: Sensor Location
Fabriacation Material |  | Approach Channel Width - B 1: Stainless Steel flume and concrete approach; Throat Width - b 5: Sensor Type; Throat Width - b 7: dB6
Overall Length (mm) |  | 2400 | K-Factor (0.6mm or 1.5mm) |  | 0.6 | Sensor Serial No |  | 95573/2008 |  | target | 1993 | 1994
Throat Width (b) |  | 650.9167 | Approach Width (B) |  | 1041.1667 | Temp Compensation |  | Built in |  | base below | 2636 |  | 643
Throat Length(L) |  | 1000 | Approach length |  | 11000 | Distance Upstream |  | 2100 |  | upstream | 2628 |  | 605
Outlet Length |  | 900 | Offset |  | 0 | Sun Shading |  | Yes |  | exit | 2599 |  | 610
Inlet Length |  | 500 | Numerical Coefficient у |  | 1 | Target Level |  | 1756 |  | mid flume | 2602
Flume Depth |  | 570 | Numerical Coefficient Ø |  | 1.5 | Zero level |  | 2365 |  | flume entry | 2603 |  | 608
Scum Mark |  | 450 | Numerical Coefficient ѱ |  | 0 | Target Reference Height |  | 609 |  | flume start | 2613 |  | 608.344
Hump Height (p) |  | 22 | Flume Cheek Staggered |  | 0 | Instrument Reading |  | 608.0662
Vertical Skew (b) |  | 0 | Vertical Skew (B) |  | 0 | Head calibration eror U(h1) |  | -0.9338
Estimated inlet radius |  | Approach Channel Width - B 1: 781; Approach Channel Width - B 2: Required inlet radius; Approach Channel Width - B 4: 780.5
Instrument Flow / Head Listing |  | Throat Width - b 5: mA Output Checks | Site flow meter curve or check points
Point No | Level mm | Flow L/sec | Point No | Level mm | Flow L/sec | Site Meter | Dvm Output | Calc Output | % Diff | Stage | head (H) | Flow (Q)
1 | 157.8 | 71.93 | 12 | 0 | 0 | 112.4 | 7.99 | 7.9848 | -0.064529 | 1 | 157.8 | 71.93
2 | 315.6 | 207.8 | 13 | 0 | 0 | 338.2 | 15.998 | 15.99 | -0.050102 | 2 | 315.6 | 207.8
3 | 0 | 0 | 14 | 0 | 0 | 451.1 | 19.997 | 19.9926 | -0.022228 | 3
4 | 0 | 0 | 15 | 0 | 0 | Mean Error % |  |  | -0.04562 | 4
5 | 0 | 0 | 16 | 0 | 0 | Flow Meter Verification |  |  |  | 5
6 | 0 | 0 | 17 | 0 | 0 | 608.344 | 607.95 | 607.728 | 607.783 | 6
7 | 0 | 0 | 18 | 0 | 0 | 608.43 | 607.794 | 607.728 | 607.783 | 7
8 | 0 | 0 | 19 | 0 | 0 | 608.628 | 607.794 | 607.7 | 608.149 | 8
9 | 0 | 0 | 20 | 0 | 0 | 608.5 | 608.93 | 607.621 | 608.149 | 9
10 | 0 | 0 | 21 | 0 | 0 | 607.85 | 608.93 | 607.621 | 607.912 | 10
11 | 0 | Approach Channel Width - B 1: 0; Throat Width - b 5: Instrument Repeatability U(h2); Throat Width - b 8: 0.42123 | 11
|  | Throat Width - b 5: Average head reading; Throat Width - b 8: 608.0662 | 12
13
14
15
Instrument Critical Parameters |  | Approach Channel Width - B 4: Comparison with published standards | 16
Calibration Units |  | Approach Channel Width - B 1: mm & l/s; Approach Channel Width - B 4: Throat Width variation; Throat Width - b 7: 0.9218% | 17
Function |  | Approach Channel Width - B 1: OCM; Approach Channel Width - B 4: Throat Width <100mm; Throat Width - b 7: 650.9167 | 18
Empty Distance (mm) |  | Approach Channel Width - B 1: 1155; Approach Channel Width - B 4: Throat Level Variation (Transverse); Throat Width - b 7: 0.6145% | 19
Calibrated H Max (mm) |  | Approach Channel Width - B 1: 526; Approach Channel Width - B 4: Throat Level Variation (Longitudinal); Throat Width - b 7: 0.4% | 20
Calibrated Q Max (L/sec) |  | Approach Channel Width - B 1: 451.31; Approach Channel Width - B 4: Approach Level Variation; Throat Width - b 7: 0.02727% | 21
Analogue Output |  | Approach Channel Width - B 1: 4-20mA; Approach Channel Width - B 4: Overall Level Variation; Throat Width - b 7: 0.03731%
Totalizer |  | Approach Channel Width - B 1: m3; Approach Channel Width - B 4: Channel Width Variation; Throat Width - b 7: 1.921%
Calculation Method |  | Approach Channel Width - B 1: 11 Point Curve; Approach Channel Width - B 4: Flume Centrality; Throat Width - b 7: 0%
B mm |  | Approach Channel Width - B 1: 1041.1667; Approach Channel Width - B 4: Staggered Flume Cheeks; Throat Width - b 7: 0%
b mm |  | Approach Channel Width - B 1: 650.9167; Approach Channel Width - B 4: Vertical Skew b; Throat Width - b 7: 0%
L mm |  | Approach Channel Width - B 1: 1000; Approach Channel Width - B 4: Vertical Skew B; Throat Width - b 7: 0%
p mm |  | Approach Channel Width - B 1: 22; Approach Channel Width - B 4: R≥2(B-b); Throat Width - b 7: 781
Compliance Checks Flow Meter |  | Approach Channel Width - B 4: Ratio Hmax /L; Throat Width - b 7: 0.526
Sensor Location |  | Approach Channel Width - B 2: 2100; Approach Channel Width - B 4: Ratio bh/B(h+p); Throat Width - b 7: 0.60008; Throat Width - b 8: 0.99987
Compliant |  | Approach Channel Width - B 2: Note :-
Caution |  | Approach Channel Width - B 2: Dimensions are listed in mm but may be differently programmed into the flow meter.
Non-Compliant |  | Approach Channel Width - B 2: See "Instrument Critical Parameters - Calibration Units"
STAFF READINGS
*
5 x B
6 x h max
*
*
*
*
*
*
3A
*
4A
7A
6A
5A
7B
6B
5B
*
9B
*
4B
*
3B
*
2A
*
1A
8B
8B
*
*
*
9A
9A
(ABC
Sensor
STAFF READINGS
*
5 x B
6 x h max
*
*
*
*
*
*
3A
*
4A
7A
6A
5A
7B
6B
5B
*
9B
*
4B
*
3B
*
2A
*
1A
8B
8B
*
*
*
9A
9A
(ABC
Sensor
1
2
4
5
6
86
5B + 5 x h max
A
B
C
3
7
FLUME DIMENSIONS
P
STAFF READINGS
*
5 x B
6 x h max
*
*
*
*
*
*
3A
*
4A
7A
6A
5A
7B
6B
5B
*
9B
*
4B
*
3B
*
2A
*
1A
8B
8B
*
*
*
9A
9A
(ABC
Sensor
STAFF READINGS
*
5 x B
6 x h max
*
*
*
*
*
*
3A
*
4A
7A
6A
5A
7B
6B
5B
*
9B
*
4B
*
3B
*
2A
*
1A
8B
8B
*
*
*
9A
9A
(ABC
Sensor
1
2
4
5
6
86
5B + 5 x h max
A
B
C
3
7
FLUME DIMENSIONS
P

## Data & Results
Appendix C - Stage discharge Relationship and Flow Uncertainty (Tariff)
Primary Device Critical Dimensions |  |  |  | Stage | Head | [7 empty] | Flow Rate | Uncertainty
Throat breadth in metres | b | 0.65092 | M | 0 | (mm) | CD | Cv | δ*/L | Re/105 | Uc | Uh | Ub | (Q) l/s | U(Q) (±%)
Length of throat in metres | L | 1 | M | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 8
Approach breadth in metres | B | 1.0412 | M | 2 | 27.6842 | 0.83418 | 1.0219 | 0.0027333 | 3.5069 | 2.3769 | 13.0694 | 0.26976 | 4.3574 | 39.7514 | 8
Height of hump in metres | p | 0.022 | M | 3 | 55.3684 | 0.91136 | 1.0423 | 0.0029667 | 5.1679 | 1.8095 | 6.5347 | 0.26976 | 13.7341 | 20.4379 | 8
Roughness value | ks | 0.0006 | M | 4 | 83.0526 | 0.93759 | 1.0533 | 0.0039667 | 6.3848 | 1.6568 | 4.3565 | 0.26976 | 26.2302 | 14.2155 | 8
Viscosity | nu | 1.141e-06 | m2/s | 5 | 110.7368 | 0.95079 | 1.0614 | 0.0041 | 7.4087 | 1.606 | 3.2673 | 0.26976 | 41.269 | 11.2556 | 8
Gravity constant | gn | 9.81 | m/s2 | 6 | 138.4211 | 0.95875 | 1.0673 | 0.0043 | 8.3381 | 1.5851 | 2.6139 | 0.26976 | 58.4789 | 9.5829 | 8
|  |  |  | 7 | 166.1053 | 0.96406 | 1.0714 | 0.0046 | 9.1702 | 1.5735 | 2.1782 | 0.26976 | 77.5995 | 8.538 | 8
Table format |  |  |  | 8 | 193.7895 | 0.96786 | 1.0749 | 0.0046 | 9.9183 | 1.5701 | 1.8671 | 0.26976 | 98.4899 | 7.8438 | 8
Initial gauged height |  | 0 | mm | 9 | 221.4737 | 0.97072 | 1.0776 | 0.0047333 | 10.6339 | 1.5684 | 1.6337 | 0.26976 | 120.9876 | 7.3587 | 8
Step size between stages |  | 27.6842 | mm | 10 | 249.1579 | 0.97294 | 1.0799 | 0.0047333 | 11.3095 | 1.5696 | 1.4522 | 0.26976 | 145.0121 | 7.0088 | 8
Number of stages |  | 20 |  | 11 | 276.8421 | 0.97472 | 1.0818 | 0.0047333 | 11.925 | 1.5705 | 1.3069 | 0.26976 | 170.4462 | 6.7476 | 8
|  |  |  | 12 | 304.5263 | 0.97618 | 1.0833 | 0.0048333 | 12.5278 | 1.5711 | 1.1881 | 0.26976 | 197.2116 | 6.5475 | 8
Uncertainties |  |  |  | 13 | 332.2105 | 0.97739 | 1.0847 | 0.0048333 | 13.1066 | 1.573 | 1.0891 | 0.26976 | 225.2775 | 6.3925 | 8
Uncertainty in equipment | u(br) | 0.28868 | mm | 14 | 359.8947 | 0.97842 | 1.0859 | 0.0048333 | 13.6416 | 1.5744 | 1.0053 | 0.26976 | 254.5579 | 6.2692 | 8
Uncertainty in measurements | u(bm) | 1.7321 | mm | 15 | 387.5789 | 0.9793 | 1.0868 | 0.0049667 | 14.1701 | 1.5747 | 0.93353 | 0.26976 | 284.9811 | 6.1687 | 8
Combined uncertainty in throat width | u(b) | 0.26976 | % | 16 | 415.2632 | 0.98007 | 1.0877 | 0.0049667 | 14.6844 | 1.5764 | 0.87129 | 0.26976 | 316.5731 | 6.088 | 8
Relative datum uncertainty | u(E) | 3.4701 | mm | 17 | 442.9474 | 0.98073 | 1.0885 | 0.0049667 | 15.1639 | 1.5777 | 0.81684 | 0.26976 | 349.2478 | 6.0211 | 8
Uncertainty in flowmeter calibration | u(h1) | -0.9338 | mm | 18 | 470.6316 | 0.98132 | 1.0893 | 0.0049667 | 15.6457 | 1.5793 | 0.76879 | 0.26976 | 382.988 | 5.9655 | 8
Uncertainty in flowmeter repeatability (68%cl) | u(h2) | 0.42123 | mm | 19 | 498.3158 | 0.98185 | 1.0898 | 0.0050667 | 16.1093 | 1.5796 | 0.72608 | 0.26976 | 417.7099 | 5.9175 | 8
Telemetry Uncertainty | u(t) | 2 | % | 20 | 526 | 0.98232 | 1.0904 | 0.0050667 | 16.5635 | 1.581 | 0.68786 | 0.26976 | 453.4662 | 7.8777 | 8
Look Up Table Uncertainty | U(lu) | 1 | % |  | Instrument
Custom Uncertainty 1 | U(a1) | 0 | % |  | Instrument H max (mm) | [8 empty] | 526
Custom Uncertainty 2 | U(a2) | 0 | % |  | Instrument Q Max (l/s) | [8 empty] | 451.31
Daily Weighted uncertainty results |  | Date used | Volume (Q) m3/day | [9 empty] | Uncertainty UQ (±%)
Calculated DWF (24hr diurnal) |  | n/a | 14778 | [9 empty] | ± | 6.834%
Calculated FFT (24hr diurnal) |  | n/a | 31577 | [9 empty] | ± | 6.429%
Real data DWF (24hr) |  | 2025-05-28 | 13734.2934 | [9 empty] | ± | 7.001%
* Average installed dimensions used to correctly calculate flow / head curve
** Quantified Errors & uncertainties following installation of flume by Civil Contrators
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #DIV/0! | 0.26976 |  | #VALUE!
|  |  |  | 1 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 2 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 3 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 4 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 5 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 6 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 7 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 8 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 9 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 10 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 11 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 12 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 13 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 14 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 15 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 16 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 17 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 18 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 19 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
|  |  |  | 20 | [5 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!
[10 empty] | #VALUE! | #VALUE! | 0.26976 |  | #VALUE!

## Uncertainty sheet
Appendix D - Calculated Daily Weighted Uncertainty (Tariff)
Daily Discharge Consent Volume m3/day |  |  | 31577 | Flow Data: | 2025-05-28
Time | Average | 15min | Total | Uncertainty | Contributions
| Flow | Volume | Volume |  | to the
Uncertainty in
| (l/s) | (m3) | (m3) | (±%) | TDV (±%)
0:00 | 141.0427 | 126.9384 | 126.9384 | 7.3587 | 0.068012
0:15 | 142.8556 | 128.57 | 255.5084 | 7.3587 | 0.068887
0:30 | 146.7078 | 132.037 | 387.5454 | 7.0088 | 0.067381
0:45 | 126.4233 | 113.781 | 501.3264 | 7.3587 | 0.060963
1:00 | 212.7167 | 191.445 | 692.7714 | 6.5475 | 0.091266
1:15 | 156.43 | 140.787 | 833.5584 | 7.0088 | 0.071846
1:30 | 140.5433 | 126.489 | 960.0474 | 7.3587 | 0.067772
1:45 | 107.5878 | 96.829 | 1056.8764 | 7.8438 | 0.0553
2:00 | 140.6433 | 126.579 | 1183.4554 | 7.3587 | 0.06782
2:15 | 111.6611 | 100.495 | 1283.9504 | 7.8438 | 0.057394
2:30 | 141.9833 | 127.785 | 1411.7354 | 7.3587 | 0.068466
2:45 | 110.8722 | 99.785 | 1511.5204 | 7.8438 | 0.056988
3:00 | 134.6222 | 121.16 | 1632.6804 | 7.3587 | 0.064916
3:15 | 105.7878 | 95.209 | 1727.8894 | 7.8438 | 0.054375
3:30 | 152.4911 | 137.242 | 1865.1314 | 7.0088 | 0.070037
3:45 | 181.7511 | 163.576 | 2028.7074 | 6.7476 | 0.080364
4:00 | 97.7456 | 87.971 | 2116.6784 | 8.538 | 0.054687
4:15 | 119.6056 | 107.645 | 2224.3234 | 7.8438 | 0.061477
4:30 | 96.2089 | 86.588 | 2310.9114 | 8.538 | 0.053828
4:45 | 91.9489 | 82.754 | 2393.6654 | 8.538 | 0.051444
5:00 | 110.9356 | 99.842 | 2493.5074 | 7.8438 | 0.057021
5:15 | 89.6822 | 80.714 | 2574.2214 | 8.538 | 0.050176
5:30 | 119.9411 | 107.947 | 2682.1684 | 7.8438 | 0.06165
5:45 | 80.8756 | 72.788 | 2754.9564 | 8.538 | 0.045249
6:00 | 115.1156 | 103.604 | 2858.5604 | 7.8438 | 0.059169
6:15 | 194.5422 | 175.088 | 3033.6484 | 6.7476 | 0.08602
6:30 | 151.2667 | 136.14 | 3169.7884 | 7.0088 | 0.069475
6:45 | 153.4778 | 138.13 | 3307.9184 | 7.0088 | 0.07049
7:00 | 121.7589 | 109.583 | 3417.5014 | 7.3587 | 0.058714
7:15 | 153.8589 | 138.473 | 3555.9744 | 7.0088 | 0.070665
7:30 | 158.7278 | 142.855 | 3698.8294 | 7.0088 | 0.072901
7:45 | 210.2244 | 189.202 | 3888.0314 | 6.5475 | 0.090197
8:00 | 233.7278 | 210.355 | 4098.3864 | 6.3925 | 0.097908
8:15 | 146.1622 | 131.546 | 4229.9324 | 7.0088 | 0.06713
8:30 | 184.1722 | 165.755 | 4395.6874 | 6.7476 | 0.081435
8:45 | 145.3756 | 130.838 | 4526.5254 | 7.0088 | 0.066769
9:00 | 167.7867 | 151.008 | 4677.5334 | 7.0088 | 0.077062
9:15 | 229.1456 | 206.231 | 4883.7644 | 6.3925 | 0.095988
9:30 | 165.4644 | 148.918 | 5032.6824 | 7.0088 | 0.075995
9:45 | 172.3811 | 155.143 | 5187.8254 | 6.7476 | 0.076221
10:00 | 124.4178 | 111.976 | 5299.8014 | 7.3587 | 0.059996
10:15 | 172.7467 | 155.472 | 5455.2734 | 6.7476 | 0.076383
10:30 | 127.4967 | 114.747 | 5570.0204 | 7.3587 | 0.06148
10:45 | 174.6578 | 157.192 | 5727.2124 | 6.7476 | 0.077228
11:00 | 246.1178 | 221.506 | 5948.7184 | 6.3925 | 0.1031
11:15 | 159.2433 | 143.319 | 6092.0374 | 7.0088 | 0.073138
11:30 | 153.0444 | 137.74 | 6229.7774 | 7.0088 | 0.070291
11:45 | 105.8333 | 95.25 | 6325.0274 | 7.8438 | 0.054398
12:00 | 154.11 | 138.699 | 6463.7264 | 7.0088 | 0.07078
12:15 | 121.8922 | 109.703 | 6573.4294 | 7.3587 | 0.058778
12:30 | 182.1467 | 163.932 | 6737.3614 | 6.7476 | 0.080539
12:45 | 212.1244 | 190.912 | 6928.2734 | 6.5475 | 0.091012
13:00 | 164.3911 | 147.952 | 7076.2254 | 7.0088 | 0.075502
13:15 | 131.0333 | 117.93 | 7194.1554 | 7.3587 | 0.063186
13:30 | 153.0211 | 137.719 | 7331.8744 | 7.0088 | 0.07028
13:45 | 180.2344 | 162.211 | 7494.0854 | 6.7476 | 0.079693
14:00 | 126.9644 | 114.268 | 7608.3534 | 7.3587 | 0.061224
14:15 | 139.7867 | 125.808 | 7734.1614 | 7.3587 | 0.067407
14:30 | 123.4856 | 111.137 | 7845.2984 | 7.3587 | 0.059546
14:45 | 164.56 | 148.104 | 7993.4024 | 7.0088 | 0.07558
15:00 | 120.8489 | 108.764 | 8102.1664 | 7.8438 | 0.062116
15:15 | 160.0622 | 144.056 | 8246.2224 | 7.0088 | 0.073514
15:30 | 197.5 | 177.75 | 8423.9724 | 6.5475 | 0.084738
15:45 | 205.4289 | 184.886 | 8608.8584 | 6.5475 | 0.088139
16:00 | 120.9378 | 108.844 | 8717.7024 | 7.8438 | 0.062162
16:15 | 158.3978 | 142.558 | 8860.2604 | 7.0088 | 0.07275
16:30 | 114.4689 | 103.022 | 8963.2824 | 7.8438 | 0.058837
16:45 | 145.8556 | 131.27 | 9094.5524 | 7.0088 | 0.066989
17:00 | 117.9611 | 106.165 | 9200.7174 | 7.8438 | 0.060632
17:15 | 192.8456 | 173.561 | 9374.2784 | 6.7476 | 0.08527
17:30 | 233.9178 | 210.526 | 9584.8044 | 6.3925 | 0.097987
17:45 | 142.4578 | 128.212 | 9713.0164 | 7.3587 | 0.068695
18:00 | 158.1656 | 142.349 | 9855.3654 | 7.0088 | 0.072643
18:15 | 128.6044 | 115.744 | 9971.1094 | 7.3587 | 0.062015
18:30 | 172.3344 | 155.101 | 10126.2104 | 6.7476 | 0.0762
18:45 | 184.3178 | 165.886 | 10292.0964 | 6.7476 | 0.081499
19:00 | 232.5544 | 209.299 | 10501.3954 | 6.3925 | 0.097416
19:15 | 148.0378 | 133.234 | 10634.6294 | 7.0088 | 0.067992
19:30 | 154.32 | 138.888 | 10773.5174 | 7.0088 | 0.070877
19:45 | 153.0522 | 137.747 | 10911.2644 | 7.0088 | 0.070295
20:00 | 132.2089 | 118.988 | 11030.2524 | 7.3587 | 0.063753
20:15 | 183.9789 | 165.581 | 11195.8334 | 6.7476 | 0.081349
20:30 | 204.4033 | 183.963 | 11379.7964 | 6.5475 | 0.087699
20:45 | 190.6367 | 171.573 | 11551.3694 | 6.7476 | 0.084293
21:00 | 122.0578 | 109.852 | 11661.2214 | 7.3587 | 0.058858
21:15 | 152.8156 | 137.534 | 11798.7554 | 7.0088 | 0.070186
21:30 | 124.2989 | 111.869 | 11910.6244 | 7.3587 | 0.059938
21:45 | 143.7233 | 129.351 | 12039.9754 | 7.3587 | 0.069305
22:00 | 210.6122 | 189.551 | 12229.5264 | 6.5475 | 0.090363
22:15 | 178.7278 | 160.855 | 12390.3814 | 6.7476 | 0.079027
22:30 | 179.0956 | 161.186 | 12551.5674 | 6.7476 | 0.07919
22:45 | 181.3922 | 163.253 | 12714.8204 | 6.7476 | 0.080205
23:00 | 245.2178 | 220.696 | 12935.5164 | 6.3925 | 0.10272
23:15 | 226.7522 | 204.077 | 13139.5934 | 6.3925 | 0.094986
23:30 | 311.5578 | 280.402 | 13419.9954 | 6.1687 | 0.12594
23:45 | 349.22 | 314.298 | 13734.2934 | 6.088 | 0.13932
|  |  | Q (m3) |  | UQ (±%)
|  | Total | 13734.2934 |  | 7.0009

## DWF (hidden)
DWF | 171.0417 | l/s
Time | DWF | Flow | Time 2 | Time Real | New Flow | Original
0 |  | 173.9907 | 0 | 0:00 | 173.9907 | 173.9907
1 |  | 156.2967 | 0.25 | 0:15 | 169.5672 | #N/A
2 |  | 144.5007 | 0.5 | 0:30 | 165.1437 | #N/A
3 |  | 104.6893 | 0.75 | 0:45 | 160.7202 | #N/A
4 |  | 92.8933 | 1 | 1:00 | 156.2967 | 156.2967
5 |  | 94.3678 | 1.25 | 1:15 | 153.3477 | #N/A
6 |  | 103.2148 | 1.5 | 1:30 | 150.3987 | #N/A
7 |  | 156.2967 | 1.75 | 1:45 | 147.4497 | #N/A
8 |  | 240.343 | 2 | 2:00 | 144.5007 | 144.5007
9 |  | 263.935 | 2.25 | 2:15 | 134.5479 | #N/A
10 |  | 241.8175 | 2.5 | 2:30 | 124.595 | #N/A
11 |  | 215.2766 | 2.75 | 2:45 | 114.6422 | #N/A
12 |  | 187.2611 | 3 | 3:00 | 104.6893 | 104.6893
13 |  | 165.1437 | 3.25 | 3:15 | 101.7403 | #N/A
14 |  | 150.3987 | 3.5 | 3:30 | 98.7913 | #N/A
15 |  | 147.4497 | 3.75 | 3:45 | 95.8423 | #N/A
16 |  | 154.8222 | 4 | 4:00 | 92.8933 | 92.8933
17 |  | 173.9907 | 4.25 | 4:15 | 93.2619 | #N/A
18 |  | 197.5826 | 4.5 | 4:30 | 93.6306 | #N/A
19 |  | 210.8531 | 4.75 | 4:45 | 93.9992 | #N/A
20 |  | 210.8531 | 5 | 5:00 | 94.3678 | 94.3678
21 |  | 200.5316 | 5.25 | 5:15 | 96.5796 | #N/A
22 |  | 202.0061 | 5.5 | 5:30 | 98.7913 | #N/A
23 |  | 188.7356 | 5.75 | 5:45 | 101.0031 | #N/A
24 |  | 173.9907 | 6 | 6:00 | 103.2148 | 103.2148
|  |  | 6.25 | 6:15 | 116.4853 | #N/A
|  |  | 6.5 | 6:30 | 129.7557 | #N/A
|  |  | 6.75 | 6:45 | 143.0262 | #N/A
|  |  | 7 | 7:00 | 156.2967 | 156.2967
|  |  | 7.25 | 7:15 | 177.3083 | #N/A
|  |  | 7.5 | 7:30 | 198.3199 | #N/A
|  |  | 7.75 | 7:45 | 219.3314 | #N/A
|  |  | 8 | 8:00 | 240.343 | 240.343
|  |  | 8.25 | 8:15 | 246.241 | #N/A
|  |  | 8.5 | 8:30 | 252.139 | #N/A
|  |  | 8.75 | 8:45 | 258.037 | #N/A
|  |  | 9 | 9:00 | 263.935 | 263.935
|  |  | 9.25 | 9:15 | 258.4056 | #N/A
|  |  | 9.5 | 9:30 | 252.8763 | #N/A
|  |  | 9.75 | 9:45 | 247.3469 | #N/A
|  |  | 10 | 10:00 | 241.8175 | 241.8175
|  |  | 10.25 | 10:15 | 235.1823 | #N/A
|  |  | 10.5 | 10:30 | 228.5471 | #N/A
|  |  | 10.75 | 10:45 | 221.9118 | #N/A
|  |  | 11 | 11:00 | 215.2766 | 215.2766
|  |  | 11.25 | 11:15 | 208.2727 | #N/A
|  |  | 11.5 | 11:30 | 201.2689 | #N/A
|  |  | 11.75 | 11:45 | 194.265 | #N/A
|  |  | 12 | 12:00 | 187.2611 | 187.2611
|  |  | 12.25 | 12:15 | 181.7318 | #N/A
|  |  | 12.5 | 12:30 | 176.2024 | #N/A
|  |  | 12.75 | 12:45 | 170.673 | #N/A
|  |  | 13 | 13:00 | 165.1437 | 165.1437
|  |  | 13.25 | 13:15 | 161.4574 | #N/A
|  |  | 13.5 | 13:30 | 157.7712 | #N/A
|  |  | 13.75 | 13:45 | 154.0849 | #N/A
|  |  | 14 | 14:00 | 150.3987 | 150.3987
|  |  | 14.25 | 14:15 | 149.6615 | #N/A
|  |  | 14.5 | 14:30 | 148.9242 | #N/A
|  |  | 14.75 | 14:45 | 148.187 | #N/A
|  |  | 15 | 15:00 | 147.4497 | 147.4497
|  |  | 15.25 | 15:15 | 149.2928 | #N/A
|  |  | 15.5 | 15:30 | 151.136 | #N/A
|  |  | 15.75 | 15:45 | 152.9791 | #N/A
|  |  | 16 | 16:00 | 154.8222 | 154.8222
|  |  | 16.25 | 16:15 | 159.6143 | #N/A
|  |  | 16.5 | 16:30 | 164.4064 | #N/A
|  |  | 16.75 | 16:45 | 169.1985 | #N/A
|  |  | 17 | 17:00 | 173.9907 | 173.9907
|  |  | 17.25 | 17:15 | 179.8886 | #N/A
|  |  | 17.5 | 17:30 | 185.7866 | #N/A
|  |  | 17.75 | 17:45 | 191.6846 | #N/A
|  |  | 18 | 18:00 | 197.5826 | 197.5826
|  |  | 18.25 | 18:15 | 200.9002 | #N/A
|  |  | 18.5 | 18:30 | 204.2179 | #N/A
|  |  | 18.75 | 18:45 | 207.5355 | #N/A
|  |  | 19 | 19:00 | 210.8531 | 210.8531
|  |  | 19.25 | 19:15 | 210.8531 | #N/A
|  |  | 19.5 | 19:30 | 210.8531 | #N/A
|  |  | 19.75 | 19:45 | 210.8531 | #N/A
|  |  | 20 | 20:00 | 210.8531 | 210.8531
|  |  | 20.25 | 20:15 | 208.2727 | #N/A
|  |  | 20.5 | 20:30 | 205.6923 | #N/A
|  |  | 20.75 | 20:45 | 203.112 | #N/A
|  |  | 21 | 21:00 | 200.5316 | 200.5316
|  |  | 21.25 | 21:15 | 200.9002 | #N/A
|  |  | 21.5 | 21:30 | 201.2689 | #N/A
|  |  | 21.75 | 21:45 | 201.6375 | #N/A
|  |  | 22 | 22:00 | 202.0061 | 202.0061
|  |  | 22.25 | 22:15 | 198.6885 | #N/A
|  |  | 22.5 | 22:30 | 195.3709 | #N/A
|  |  | 22.75 | 22:45 | 192.0533 | #N/A
|  |  | 23 | 23:00 | 188.7356 | 188.7356
|  |  | 23.25 | 23:15 | 185.0494 | #N/A
|  |  | 23.5 | 23:30 | 181.3631 | #N/A
|  |  | 23.75 | 23:45 | 177.6769 | #N/A

## DWF Uncertainty (hidden)
Time | Average | 15min | Total | Uncertainty | Contributions
| Flow | Volume | Volume |  | to the
Uncertainty in
| (l/s) | (m3) | (m3) | (±%) | TDV (±%)
0:00 | 173.9907 | 156.5916 | 156.5916 | 6.7476 | 0.070263
0:15 | 169.5672 | 152.6105 | 309.202 | 7.0088 | 0.071128
0:30 | 165.1437 | 148.6293 | 457.8314 | 7.0088 | 0.069272
0:45 | 160.7202 | 144.6482 | 602.4795 | 7.0088 | 0.067417
1:00 | 156.2967 | 140.667 | 743.1466 | 7.0088 | 0.065561
1:15 | 153.3477 | 138.0129 | 881.1595 | 7.0088 | 0.064324
1:30 | 150.3987 | 135.3588 | 1016.5183 | 7.0088 | 0.063087
1:45 | 147.4497 | 132.7047 | 1149.2231 | 7.0088 | 0.06185
2:00 | 144.5007 | 130.0506 | 1279.2737 | 7.3587 | 0.063639
2:15 | 134.5479 | 121.0931 | 1400.3668 | 7.3587 | 0.059255
2:30 | 124.595 | 112.1355 | 1512.5023 | 7.3587 | 0.054872
2:45 | 114.6422 | 103.1779 | 1615.6802 | 7.8438 | 0.053817
3:00 | 104.6893 | 94.2204 | 1709.9006 | 7.8438 | 0.049145
3:15 | 101.7403 | 91.5663 | 1801.4669 | 7.8438 | 0.047761
3:30 | 98.7913 | 88.9122 | 1890.379 | 7.8438 | 0.046376
3:45 | 95.8423 | 86.2581 | 1976.6371 | 8.538 | 0.048973
4:00 | 92.8933 | 83.604 | 2060.2411 | 8.538 | 0.047467
4:15 | 93.2619 | 83.9357 | 2144.1769 | 8.538 | 0.047655
4:30 | 93.6306 | 84.2675 | 2228.4444 | 8.538 | 0.047843
4:45 | 93.9992 | 84.5993 | 2313.0436 | 8.538 | 0.048032
5:00 | 94.3678 | 84.931 | 2397.9747 | 8.538 | 0.04822
5:15 | 96.5796 | 86.9216 | 2484.8963 | 8.538 | 0.04935
5:30 | 98.7913 | 88.9122 | 2573.8085 | 7.8438 | 0.046376
5:45 | 101.0031 | 90.9027 | 2664.7112 | 7.8438 | 0.047415
6:00 | 103.2148 | 92.8933 | 2757.6045 | 7.8438 | 0.048453
6:15 | 116.4853 | 104.8367 | 2862.4413 | 7.8438 | 0.054682
6:30 | 129.7557 | 116.7802 | 2979.2214 | 7.3587 | 0.057145
6:45 | 143.0262 | 128.7236 | 3107.945 | 7.3587 | 0.062989
7:00 | 156.2967 | 140.667 | 3248.6121 | 7.0088 | 0.065561
7:15 | 177.3083 | 159.5775 | 3408.1895 | 6.7476 | 0.071602
7:30 | 198.3199 | 178.4879 | 3586.6774 | 6.5475 | 0.077712
7:45 | 219.3314 | 197.3983 | 3784.0757 | 6.5475 | 0.085946
8:00 | 240.343 | 216.3087 | 4000.3844 | 6.3925 | 0.09195
8:15 | 246.241 | 221.6169 | 4222.0013 | 6.3925 | 0.094206
8:30 | 252.139 | 226.9251 | 4448.9265 | 6.3925 | 0.096463
8:45 | 258.037 | 232.2333 | 4681.1598 | 6.2692 | 0.096815
9:00 | 263.935 | 237.5415 | 4918.7012 | 6.2692 | 0.099028
9:15 | 258.4056 | 232.5651 | 5151.2663 | 6.2692 | 0.096953
9:30 | 252.8763 | 227.5886 | 5378.8549 | 6.3925 | 0.096745
9:45 | 247.3469 | 222.6122 | 5601.4671 | 6.3925 | 0.094629
10:00 | 241.8175 | 217.6358 | 5819.1029 | 6.3925 | 0.092514
10:15 | 235.1823 | 211.6641 | 6030.767 | 6.3925 | 0.089975
10:30 | 228.5471 | 205.6923 | 6236.4593 | 6.3925 | 0.087437
10:45 | 221.9118 | 199.7206 | 6436.18 | 6.5475 | 0.086957
11:00 | 215.2766 | 193.7489 | 6629.9289 | 6.5475 | 0.084357
11:15 | 208.2727 | 187.4454 | 6817.3743 | 6.5475 | 0.081612
11:30 | 201.2689 | 181.142 | 6998.5163 | 6.5475 | 0.078868
11:45 | 194.265 | 174.8385 | 7173.3548 | 6.7476 | 0.07845
12:00 | 187.2611 | 168.535 | 7341.8898 | 6.7476 | 0.075622
12:15 | 181.7318 | 163.5586 | 7505.4484 | 6.7476 | 0.073389
12:30 | 176.2024 | 158.5822 | 7664.0306 | 6.7476 | 0.071156
12:45 | 170.673 | 153.6057 | 7817.6363 | 6.7476 | 0.068923
13:00 | 165.1437 | 148.6293 | 7966.2656 | 7.0088 | 0.069272
13:15 | 161.4574 | 145.3117 | 8111.5773 | 7.0088 | 0.067726
13:30 | 157.7712 | 141.9941 | 8253.5714 | 7.0088 | 0.06618
13:45 | 154.0849 | 138.6765 | 8392.2479 | 7.0088 | 0.064633
14:00 | 150.3987 | 135.3588 | 8527.6067 | 7.0088 | 0.063087
14:15 | 149.6615 | 134.6953 | 8662.302 | 7.0088 | 0.062778
14:30 | 148.9242 | 134.0318 | 8796.3338 | 7.0088 | 0.062469
14:45 | 148.187 | 133.3683 | 8929.7021 | 7.0088 | 0.062159
15:00 | 147.4497 | 132.7047 | 9062.4068 | 7.0088 | 0.06185
15:15 | 149.2928 | 134.3636 | 9196.7703 | 7.0088 | 0.062623
15:30 | 151.136 | 136.0224 | 9332.7927 | 7.0088 | 0.063396
15:45 | 152.9791 | 137.6812 | 9470.4739 | 7.0088 | 0.064169
16:00 | 154.8222 | 139.34 | 9609.8139 | 7.0088 | 0.064943
16:15 | 159.6143 | 143.6529 | 9753.4667 | 7.0088 | 0.066953
16:30 | 164.4064 | 147.9658 | 9901.4325 | 7.0088 | 0.068963
16:45 | 169.1985 | 152.2787 | 10053.7112 | 7.0088 | 0.070973
17:00 | 173.9907 | 156.5916 | 10210.3028 | 6.7476 | 0.070263
17:15 | 179.8886 | 161.8998 | 10372.2026 | 6.7476 | 0.072644
17:30 | 185.7866 | 167.208 | 10539.4106 | 6.7476 | 0.075026
17:45 | 191.6846 | 172.5162 | 10711.9267 | 6.7476 | 0.077408
18:00 | 197.5826 | 177.8244 | 10889.7511 | 6.5475 | 0.077423
18:15 | 200.9002 | 180.8102 | 11070.5613 | 6.5475 | 0.078723
18:30 | 204.2179 | 183.7961 | 11254.3574 | 6.5475 | 0.080023
18:45 | 207.5355 | 186.7819 | 11441.1393 | 6.5475 | 0.081323
19:00 | 210.8531 | 189.7678 | 11630.9071 | 6.5475 | 0.082623
19:15 | 210.8531 | 189.7678 | 11820.6748 | 6.5475 | 0.082623
19:30 | 210.8531 | 189.7678 | 12010.4426 | 6.5475 | 0.082623
19:45 | 210.8531 | 189.7678 | 12200.2104 | 6.5475 | 0.082623
20:00 | 210.8531 | 189.7678 | 12389.9782 | 6.5475 | 0.082623
20:15 | 208.2727 | 187.4454 | 12577.4236 | 6.5475 | 0.081612
20:30 | 205.6923 | 185.1231 | 12762.5467 | 6.5475 | 0.080601
20:45 | 203.112 | 182.8008 | 12945.3475 | 6.5475 | 0.07959
21:00 | 200.5316 | 180.4784 | 13125.826 | 6.5475 | 0.078579
21:15 | 200.9002 | 180.8102 | 13306.6362 | 6.5475 | 0.078723
21:30 | 201.2689 | 181.142 | 13487.7782 | 6.5475 | 0.078868
21:45 | 201.6375 | 181.4737 | 13669.2519 | 6.5475 | 0.079012
22:00 | 202.0061 | 181.8055 | 13851.0574 | 6.5475 | 0.079157
22:15 | 198.6885 | 178.8196 | 14029.877 | 6.5475 | 0.077857
22:30 | 195.3709 | 175.8338 | 14205.7108 | 6.7476 | 0.078896
22:45 | 192.0533 | 172.8479 | 14378.5587 | 6.7476 | 0.077557
23:00 | 188.7356 | 169.8621 | 14548.4208 | 6.7476 | 0.076217
23:15 | 185.0494 | 166.5445 | 14714.9653 | 6.7476 | 0.074728
23:30 | 181.3631 | 163.2268 | 14878.1921 | 6.7476 | 0.07324
23:45 | 177.6769 | 159.9092 | 15038.1013 | 6.7476 | 0.071751
|  |  | Q (m3) |  | UQ (±%)
|  | Total | 15038.1013 |  | 6.8337

## FFT (hidden)
DWF | 365.4745 | l/s
Time | DWF | Flow | Time 2 | Time Real | New Flow | Original
0 |  | 371.7758 | 0 | 0:00 | 371.7758 | 371.7758
1 |  | 333.9681 | 0.25 | 0:15 | 362.3239 | #N/A
2 |  | 308.763 | 0.5 | 0:30 | 352.872 | #N/A
3 |  | 223.6956 | 0.75 | 0:45 | 343.42 | #N/A
4 |  | 198.4905 | 1 | 1:00 | 333.9681 | 333.9681
5 |  | 201.6411 | 1.25 | 1:15 | 327.6668 | #N/A
6 |  | 220.545 | 1.5 | 1:30 | 321.3655 | #N/A
7 |  | 333.9681 | 1.75 | 1:45 | 315.0643 | #N/A
8 |  | 513.5547 | 2 | 2:00 | 308.763 | 308.763
9 |  | 563.965 | 2.25 | 2:15 | 287.4961 | #N/A
10 |  | 516.7054 | 2.5 | 2:30 | 266.2293 | #N/A
11 |  | 459.9938 | 2.75 | 2:45 | 244.9625 | #N/A
12 |  | 400.1316 | 3 | 3:00 | 223.6956 | 223.6956
13 |  | 352.872 | 3.25 | 3:15 | 217.3943 | #N/A
14 |  | 321.3655 | 3.5 | 3:30 | 211.0931 | #N/A
15 |  | 315.0643 | 3.75 | 3:45 | 204.7918 | #N/A
16 |  | 330.8175 | 4 | 4:00 | 198.4905 | 198.4905
17 |  | 371.7758 | 4.25 | 4:15 | 199.2781 | #N/A
18 |  | 422.1861 | 4.5 | 4:30 | 200.0658 | #N/A
19 |  | 450.5419 | 4.75 | 4:45 | 200.8535 | #N/A
20 |  | 450.5419 | 5 | 5:00 | 201.6411 | 201.6411
21 |  | 428.4874 | 5.25 | 5:15 | 206.3671 | #N/A
22 |  | 431.638 | 5.5 | 5:30 | 211.0931 | #N/A
23 |  | 403.2822 | 5.75 | 5:45 | 215.819 | #N/A
24 |  | 371.7758 | 6 | 6:00 | 220.545 | 220.545
|  |  | 6.25 | 6:15 | 248.9008 | #N/A
|  |  | 6.5 | 6:30 | 277.2565 | #N/A
|  |  | 6.75 | 6:45 | 305.6123 | #N/A
|  |  | 7 | 7:00 | 333.9681 | 333.9681
|  |  | 7.25 | 7:15 | 378.8648 | #N/A
|  |  | 7.5 | 7:30 | 423.7614 | #N/A
|  |  | 7.75 | 7:45 | 468.6581 | #N/A
|  |  | 8 | 8:00 | 513.5547 | 513.5547
|  |  | 8.25 | 8:15 | 526.1573 | #N/A
|  |  | 8.5 | 8:30 | 538.7599 | #N/A
|  |  | 8.75 | 8:45 | 551.3624 | #N/A
|  |  | 9 | 9:00 | 563.965 | 563.965
|  |  | 9.25 | 9:15 | 552.1501 | #N/A
|  |  | 9.5 | 9:30 | 540.3352 | #N/A
|  |  | 9.75 | 9:45 | 528.5203 | #N/A
|  |  | 10 | 10:00 | 516.7054 | 516.7054
|  |  | 10.25 | 10:15 | 502.5275 | #N/A
|  |  | 10.5 | 10:30 | 488.3496 | #N/A
|  |  | 10.75 | 10:45 | 474.1717 | #N/A
|  |  | 11 | 11:00 | 459.9938 | 459.9938
|  |  | 11.25 | 11:15 | 445.0283 | #N/A
|  |  | 11.5 | 11:30 | 430.0627 | #N/A
|  |  | 11.75 | 11:45 | 415.0972 | #N/A
|  |  | 12 | 12:00 | 400.1316 | 400.1316
|  |  | 12.25 | 12:15 | 388.3167 | #N/A
|  |  | 12.5 | 12:30 | 376.5018 | #N/A
|  |  | 12.75 | 12:45 | 364.6869 | #N/A
|  |  | 13 | 13:00 | 352.872 | 352.872
|  |  | 13.25 | 13:15 | 344.9954 | #N/A
|  |  | 13.5 | 13:30 | 337.1188 | #N/A
|  |  | 13.75 | 13:45 | 329.2421 | #N/A
|  |  | 14 | 14:00 | 321.3655 | 321.3655
|  |  | 14.25 | 14:15 | 319.7902 | #N/A
|  |  | 14.5 | 14:30 | 318.2149 | #N/A
|  |  | 14.75 | 14:45 | 316.6396 | #N/A
|  |  | 15 | 15:00 | 315.0643 | 315.0643
|  |  | 15.25 | 15:15 | 319.0026 | #N/A
|  |  | 15.5 | 15:30 | 322.9409 | #N/A
|  |  | 15.75 | 15:45 | 326.8792 | #N/A
|  |  | 16 | 16:00 | 330.8175 | 330.8175
|  |  | 16.25 | 16:15 | 341.0571 | #N/A
|  |  | 16.5 | 16:30 | 351.2966 | #N/A
|  |  | 16.75 | 16:45 | 361.5362 | #N/A
|  |  | 17 | 17:00 | 371.7758 | 371.7758
|  |  | 17.25 | 17:15 | 384.3784 | #N/A
|  |  | 17.5 | 17:30 | 396.981 | #N/A
|  |  | 17.75 | 17:45 | 409.5835 | #N/A
|  |  | 18 | 18:00 | 422.1861 | 422.1861
|  |  | 18.25 | 18:15 | 429.275 | #N/A
|  |  | 18.5 | 18:30 | 436.364 | #N/A
|  |  | 18.75 | 18:45 | 443.4529 | #N/A
|  |  | 19 | 19:00 | 450.5419 | 450.5419
|  |  | 19.25 | 19:15 | 450.5419 | #N/A
|  |  | 19.5 | 19:30 | 450.5419 | #N/A
|  |  | 19.75 | 19:45 | 450.5419 | #N/A
|  |  | 20 | 20:00 | 450.5419 | 450.5419
|  |  | 20.25 | 20:15 | 445.0283 | #N/A
|  |  | 20.5 | 20:30 | 439.5146 | #N/A
|  |  | 20.75 | 20:45 | 434.001 | #N/A
|  |  | 21 | 21:00 | 428.4874 | 428.4874
|  |  | 21.25 | 21:15 | 429.275 | #N/A
|  |  | 21.5 | 21:30 | 430.0627 | #N/A
|  |  | 21.75 | 21:45 | 430.8504 | #N/A
|  |  | 22 | 22:00 | 431.638 | 431.638
|  |  | 22.25 | 22:15 | 424.5491 | #N/A
|  |  | 22.5 | 22:30 | 417.4601 | #N/A
|  |  | 22.75 | 22:45 | 410.3712 | #N/A
|  |  | 23 | 23:00 | 403.2822 | 403.2822
|  |  | 23.25 | 23:15 | 395.4056 | #N/A
|  |  | 23.5 | 23:30 | 387.529 | #N/A
|  |  | 23.75 | 23:45 | 379.6524 | #N/A

## FFT Uncertainty (hidden)
Time | Average | 15min | Total | Uncertainty | Contributions
| Flow | Volume | Volume |  | to the
Uncertainty in
| (l/s) | (m3) | (m3) | (±%) | TDV (±%)
0:00 | 371.7758 | 334.5982 | 334.5982 | 6.0211 | 0.062697
0:15 | 362.3239 | 326.0915 | 660.6897 | 6.0211 | 0.061103
0:30 | 352.872 | 317.5848 | 978.2745 | 6.0211 | 0.059509
0:45 | 343.42 | 309.078 | 1287.3526 | 6.088 | 0.058559
1:00 | 333.9681 | 300.5713 | 1587.9239 | 6.088 | 0.056947
1:15 | 327.6668 | 294.9001 | 1882.824 | 6.088 | 0.055873
1:30 | 321.3655 | 289.229 | 2172.053 | 6.088 | 0.054798
1:45 | 315.0643 | 283.5578 | 2455.6108 | 6.1687 | 0.054436
2:00 | 308.763 | 277.8867 | 2733.4975 | 6.1687 | 0.053347
2:15 | 287.4961 | 258.7465 | 2992.244 | 6.1687 | 0.049673
2:30 | 266.2293 | 239.6064 | 3231.8504 | 6.2692 | 0.046748
2:45 | 244.9625 | 220.4662 | 3452.3166 | 6.3925 | 0.04386
3:00 | 223.6956 | 201.3261 | 3653.6426 | 6.5475 | 0.041023
3:15 | 217.3943 | 195.6549 | 3849.2975 | 6.5475 | 0.039867
3:30 | 211.0931 | 189.9837 | 4039.2813 | 6.5475 | 0.038712
3:45 | 204.7918 | 184.3126 | 4223.5939 | 6.5475 | 0.037556
4:00 | 198.4905 | 178.6414 | 4402.2353 | 6.5475 | 0.0364
4:15 | 199.2781 | 179.3503 | 4581.5856 | 6.5475 | 0.036545
4:30 | 200.0658 | 180.0592 | 4761.6449 | 6.5475 | 0.036689
4:45 | 200.8535 | 180.7681 | 4942.413 | 6.5475 | 0.036834
5:00 | 201.6411 | 181.477 | 5123.89 | 6.5475 | 0.036978
5:15 | 206.3671 | 185.7304 | 5309.6204 | 6.5475 | 0.037845
5:30 | 211.0931 | 189.9837 | 5499.6041 | 6.5475 | 0.038712
5:45 | 215.819 | 194.2371 | 5693.8412 | 6.5475 | 0.039578
6:00 | 220.545 | 198.4905 | 5892.3317 | 6.5475 | 0.040445
6:15 | 248.9008 | 224.0107 | 6116.3424 | 6.3925 | 0.044565
6:30 | 277.2565 | 249.5309 | 6365.8733 | 6.2692 | 0.048684
6:45 | 305.6123 | 275.0511 | 6640.9244 | 6.1687 | 0.052803
7:00 | 333.9681 | 300.5713 | 6941.4957 | 6.088 | 0.056947
7:15 | 378.8648 | 340.9783 | 7282.474 | 6.0211 | 0.063893
7:30 | 423.7614 | 381.3853 | 7663.8593 | 5.9175 | 0.070235
7:45 | 468.6581 | 421.7923 | 8085.6515 | 7.8777 | 0.10341
8:00 | 513.5547 | 462.1993 | 8547.8508 | 7.8777 | 0.11331
8:15 | 526.1573 | 473.5416 | 9021.3924 | 7.8777 | 0.11609
8:30 | 538.7599 | 484.8839 | 9506.2763 | 7.8777 | 0.11887
8:45 | 551.3624 | 496.2262 | 10002.5025 | 7.8777 | 0.12165
9:00 | 563.965 | 507.5685 | 10510.071 | 7.8777 | 0.12444
9:15 | 552.1501 | 496.9351 | 11007.0061 | 7.8777 | 0.12183
9:30 | 540.3352 | 486.3017 | 11493.3078 | 7.8777 | 0.11922
9:45 | 528.5203 | 475.6683 | 11968.976 | 7.8777 | 0.11661
10:00 | 516.7054 | 465.0348 | 12434.0109 | 7.8777 | 0.11401
10:15 | 502.5275 | 452.2747 | 12886.2856 | 7.8777 | 0.11088
10:30 | 488.3496 | 439.5146 | 13325.8002 | 7.8777 | 0.10775
10:45 | 474.1717 | 426.7545 | 13752.5548 | 7.8777 | 0.10462
11:00 | 459.9938 | 413.9944 | 14166.5492 | 7.8777 | 0.1015
11:15 | 445.0283 | 400.5254 | 14567.0747 | 5.9175 | 0.073759
11:30 | 430.0627 | 387.0564 | 14954.1311 | 5.9175 | 0.071279
11:45 | 415.0972 | 373.5874 | 15327.7185 | 5.9655 | 0.069357
12:00 | 400.1316 | 360.1184 | 15687.837 | 5.9655 | 0.066856
12:15 | 388.3167 | 349.485 | 16037.322 | 5.9655 | 0.064882
12:30 | 376.5018 | 338.8516 | 16376.1736 | 6.0211 | 0.063494
12:45 | 364.6869 | 328.2182 | 16704.3918 | 6.0211 | 0.061502
13:00 | 352.872 | 317.5848 | 17021.9766 | 6.0211 | 0.059509
13:15 | 344.9954 | 310.4958 | 17332.4724 | 6.088 | 0.058828
13:30 | 337.1188 | 303.4069 | 17635.8793 | 6.088 | 0.057485
13:45 | 329.2421 | 296.3179 | 17932.1972 | 6.088 | 0.056141
14:00 | 321.3655 | 289.229 | 18221.4262 | 6.088 | 0.054798
14:15 | 319.7902 | 287.8112 | 18509.2374 | 6.088 | 0.05453
14:30 | 318.2149 | 286.3934 | 18795.6308 | 6.088 | 0.054261
14:45 | 316.6396 | 284.9756 | 19080.6064 | 6.088 | 0.053992
15:00 | 315.0643 | 283.5578 | 19364.1643 | 6.1687 | 0.054436
15:15 | 319.0026 | 287.1023 | 19651.2666 | 6.088 | 0.054395
15:30 | 322.9409 | 290.6468 | 19941.9133 | 6.088 | 0.055067
15:45 | 326.8792 | 294.1912 | 20236.1046 | 6.088 | 0.055738
16:00 | 330.8175 | 297.7357 | 20533.8403 | 6.088 | 0.05641
16:15 | 341.0571 | 306.9514 | 20840.7917 | 6.088 | 0.058156
16:30 | 351.2966 | 316.167 | 21156.9586 | 6.0211 | 0.059244
16:45 | 361.5362 | 325.3826 | 21482.3412 | 6.0211 | 0.06097
17:00 | 371.7758 | 334.5982 | 21816.9395 | 6.0211 | 0.062697
17:15 | 384.3784 | 345.9406 | 22162.88 | 5.9655 | 0.064224
17:30 | 396.981 | 357.2829 | 22520.1629 | 5.9655 | 0.06633
17:45 | 409.5835 | 368.6252 | 22888.7881 | 5.9655 | 0.068436
18:00 | 422.1861 | 379.9675 | 23268.7556 | 5.9175 | 0.069974
18:15 | 429.275 | 386.3475 | 23655.1031 | 5.9175 | 0.071148
18:30 | 436.364 | 392.7276 | 24047.8307 | 5.9175 | 0.072323
18:45 | 443.4529 | 399.1076 | 24446.9384 | 5.9175 | 0.073498
19:00 | 450.5419 | 405.4877 | 24852.4261 | 5.9175 | 0.074673
19:15 | 450.5419 | 405.4877 | 25257.9138 | 5.9175 | 0.074673
19:30 | 450.5419 | 405.4877 | 25663.4015 | 5.9175 | 0.074673
19:45 | 450.5419 | 405.4877 | 26068.8892 | 5.9175 | 0.074673
20:00 | 450.5419 | 405.4877 | 26474.3769 | 5.9175 | 0.074673
20:15 | 445.0283 | 400.5254 | 26874.9023 | 5.9175 | 0.073759
20:30 | 439.5146 | 395.5632 | 27270.4655 | 5.9175 | 0.072846
20:45 | 434.001 | 390.6009 | 27661.0664 | 5.9175 | 0.071932
21:00 | 428.4874 | 385.6386 | 28046.705 | 5.9175 | 0.071018
21:15 | 429.275 | 386.3475 | 28433.0526 | 5.9175 | 0.071148
21:30 | 430.0627 | 387.0564 | 28820.109 | 5.9175 | 0.071279
21:45 | 430.8504 | 387.7653 | 29207.8743 | 5.9175 | 0.07141
22:00 | 431.638 | 388.4742 | 29596.3486 | 5.9175 | 0.07154
22:15 | 424.5491 | 382.0942 | 29978.4427 | 5.9175 | 0.070365
22:30 | 417.4601 | 375.7141 | 30354.1569 | 5.9655 | 0.069752
22:45 | 410.3712 | 369.3341 | 30723.4909 | 5.9655 | 0.068567
23:00 | 403.2822 | 362.954 | 31086.445 | 5.9655 | 0.067383
23:15 | 395.4056 | 355.8651 | 31442.31 | 5.9655 | 0.066067
23:30 | 387.529 | 348.7761 | 31791.0862 | 5.9655 | 0.064751
23:45 | 379.6524 | 341.6872 | 32132.7734 | 6.0211 | 0.064026
|  |  | Q (m3) |  | UQ (±%)
|  | Total | 32132.7734 |  | 6.429

## Calculations (hidden)
h | A | a0 | Cv0(i) | Cv0(ii) | Cv0(iii) | Cv0(iv) | Q0 | (Re/10^5)1 | (del*/L)1a | (del*/L)1b | (del*/L)1 | be1 | he1 | a1 | Cv1(i) | Cv1(ii) | Cv1(iii) | Cv1(iv) | CD1 | Q1 | (Re/10^5)2 | (del*/L)2a | (del*/L)2b | (del*/L)2 | be2 | he2 | a2 | Cv2(I) | Cv2(ii) | Cv2(iii) | Cv2(iv) | CD2 | Q2 | (Re/10^5)3 | (del*/L)3a | (del*/L)3b | (del*/L)3 | be3 | he3 | a3 | Cv3(i) | Cv3(ii) | Cv3(iii) | Cv3(iv) | CD3 | Q3 |  | Q | CD | Cv | del*/L | Re/10^5
0.001 | 0.023947 | 0.00010946 | 0.99858 | 1.0002 | 1.0002 | 1.0002 | 3.5099e-05 | 0.70881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A
0.002 | 0.024988 | 0.00040211 | 0.99904 | 1.0006 | 1.0006 | 1.0006 | 9.9319e-05 | 1.0025 | 0.0054 | 0.0054 | 0.0054 | 0.64012 | -0.0034 | 0.0011239 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | 2 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
0.003 | 0.026029 | 0.00083381 | 0.99974 | 1.0013 | 1.0013 | 1.0013 | 0.00018258 | 1.2281 | 0.0051 | 0.0051 | 0.0051 | 0.64072 | -0.0021 | 0.00039586 | 1.0006 | 1.0006 | 1.0006 | 1.0006 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | 3 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
0.004 | 0.02707 | 0.0013705 | 1.0006 | 1.0021 | 1.0021 | 1.0021 | 0.00028133 | 1.4185 | 0.0047 | 0.0047 | 0.0047 | 0.64152 | -0.0007 | 4.0768e-05 | 1.0001 | 1.0001 | 1.0001 | 1.0001 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | 4 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
0.005 | 0.028112 | 0.0019857 | 1.0016 | 1.003 | 1.003 | 1.003 | 0.00039353 | 1.5864 | 0.0047 | 0.0047 | 0.0047 | 0.64152 | 0.0003 | 6.9436e-06 | 1 | 1 | 1 | 1 | 0.014485 | 5.6832e-06 | 0.38633 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5 | #N/A | #N/A | #N/A | #N/A | #N/A
0.006 | 0.029153 | 0.0026588 | 1.0027 | 1.004 | 1.004 | 1.004 | 0.00051784 | 1.7384 | 0.0044 | 0.0044 | 0.0044 | 0.64212 | 0.0016 | 0.000184 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | 0.13584 | 7.0083e-05 | 0.89255 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6 | #N/A | #N/A | #N/A | #N/A | #N/A
0.007 | 0.030194 | 0.0033737 | 1.0038 | 1.0051 | 1.0051 | 1.0051 | 0.00065326 | 1.8784 | 0.0041 | 0.0041 | 0.0041 | 0.64272 | 0.0029 | 0.00056454 | 1.0008 | 1.0008 | 1.0008 | 1.0008 | 0.2633 | 0.00017127 | 1.2022 | 0.0051 | 0.0051 | 0.0051 | 0.64072 | 0.0019 | 0.00024082 | 1.0004 | 1.0004 | 1.0004 | 1.0004 | 0.1392 | 9.0501e-05 | 0.97195 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | 0.97195
0.008 | 0.031235 | 0.0041176 | 1.005 | 1.0063 | 1.0063 | 1.0063 | 0.00079903 | 2.0089 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0042 | 0.0011086 | 1.0017 | 1.0017 | 1.0017 | 1.0017 | 0.37596 | 0.00029903 | 1.4477 | 0.0047 | 0.0047 | 0.0047 | 0.64152 | 0.0033 | 0.00068055 | 1.001 | 1.001 | 1.001 | 1.001 | 0.26111 | 0.00020755 | 1.2817 | 0.0051 | 0.0051 | 0.0051 | 0.64072 | 0.0029 | 0.00052425 | 1.0008 | 1.0008 | 1.0008 | 1.0008 | 0.21483 | 0.00017073 | 8 | 0.17073 | 0.21483 | 1.0008 | 0.0051 | 1.2817
0.009 | 0.032276 | 0.0048805 | 1.0063 | 1.0074 | 1.0074 | 1.0074 | 0.00095456 | 2.1316 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0052 | 0.0015914 | 1.0024 | 1.0024 | 1.0024 | 1.0024 | 0.43405 | 0.00041226 | 1.6112 | 0.0044 | 0.0044 | 0.0044 | 0.64212 | 0.0046 | 0.0012407 | 1.0019 | 1.0019 | 1.0019 | 1.0019 | 0.36046 | 0.00034218 | 1.5142 | 0.0047 | 0.0047 | 0.0047 | 0.64152 | 0.0043 | 0.0010821 | 1.0016 | 1.0016 | 1.0016 | 1.0016 | 0.32548 | 0.0003089 | 9 | 0.3089 | 0.32548 | 1.0016 | 0.0047 | 1.5142
0.01 | 0.033317 | 0.0056547 | 1.0076 | 1.0086 | 1.0086 | 1.0086 | 0.0011193 | 2.2477 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0062 | 0.0021232 | 1.0032 | 1.0032 | 1.0032 | 1.0032 | 0.48249 | 0.00053716 | 1.7598 | 0.0044 | 0.0044 | 0.0044 | 0.64212 | 0.0056 | 0.0017257 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 0.4134 | 0.00045996 | 1.6711 | 0.0044 | 0.0044 | 0.0044 | 0.64212 | 0.0056 | 0.0017257 | 1.0026 | 1.0026 | 1.0026 | 1.0026 | 0.4134 | 0.00045996 | 10 | 0.45996 | 0.4134 | 1.0026 | 0.0044 | 1.6711
0.011 | 0.034359 | 0.0064337 | 1.0088 | 1.0098 | 1.0098 | 1.0098 | 0.0012929 | 2.3584 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0074 | 0.0028476 | 1.0043 | 1.0043 | 1.0043 | 1.0043 | 0.54567 | 0.00070163 | 1.9237 | 0.0041 | 0.0041 | 0.0041 | 0.64272 | 0.0069 | 0.0024681 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 0.49054 | 0.00063039 | 1.8562 | 0.0041 | 0.0041 | 0.0041 | 0.64272 | 0.0069 | 0.0024681 | 1.0037 | 1.0037 | 1.0037 | 1.0037 | 0.49054 | 0.00063039 | 11 | 0.63039 | 0.49054 | 1.0037 | 0.0041 | 1.8562
0.012 | 0.0354 | 0.0072129 | 1.0101 | 1.0111 | 1.0111 | 1.0111 | 0.0014749 | 2.4643 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0084 | 0.0034566 | 1.0052 | 1.0052 | 1.0052 | 1.0052 | 0.57918 | 0.00084934 | 2.0502 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0082 | 0.0032898 | 1.005 | 1.005 | 1.005 | 1.005 | 0.55828 | 0.00081847 | 2.025 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0082 | 0.0032898 | 1.005 | 1.005 | 1.005 | 1.005 | 0.55828 | 0.00081847 | 12 | 0.81847 | 0.55828 | 1.005 | 0.0038 | 2.025
0.013 | 0.036441 | 0.0079884 | 1.0114 | 1.0123 | 1.0123 | 1.0123 | 0.0016651 | 2.5659 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0094 | 0.0040847 | 1.0062 | 1.0062 | 1.0062 | 1.0062 | 0.60806 | 0.0010064 | 2.1695 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0092 | 0.0039079 | 1.0059 | 1.0059 | 1.0059 | 1.0059 | 0.58839 | 0.00097358 | 2.1456 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0092 | 0.0039079 | 1.0059 | 1.0059 | 1.0059 | 1.0059 | 0.58839 | 0.00097358 | 13 | 0.97358 | 0.58839 | 1.0059 | 0.0038 | 2.1456
0.014 | 0.037482 | 0.008757 | 1.0127 | 1.0135 | 1.0135 | 1.0135 | 0.0018631 | 2.6638 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0107 | 0.0050121 | 1.0076 | 1.0076 | 1.0076 | 1.0076 | 0.66139 | 0.0012251 | 2.3164 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0104 | 0.0047261 | 1.0072 | 1.0072 | 1.0072 | 1.0072 | 0.63318 | 0.0011723 | 2.2827 | 0.0038 | 0.0038 | 0.0038 | 0.64332 | 0.0102 | 0.0045405 | 1.0069 | 1.0069 | 1.0069 | 1.0069 | 0.61462 | 0.0011377 | 14 | 1.1377 | 0.61462 | 1.0069 | 0.0038 | 2.2827
0.015 | 0.038523 | 0.0095167 | 1.0139 | 1.0147 | 1.0147 | 1.0147 | 0.0020687 | 2.7584 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0117 | 0.0056731 | 1.0087 | 1.0087 | 1.0087 | 1.0087 | 0.68189 | 0.0014022 | 2.4231 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0114 | 0.0053759 | 1.0082 | 1.0082 | 1.0082 | 1.0082 | 0.65522 | 0.0013468 | 2.3907 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0114 | 0.0053759 | 1.0082 | 1.0082 | 1.0082 | 1.0082 | 0.65522 | 0.0013468 | 15 | 1.3468 | 0.65522 | 1.0082 | 0.0036 | 2.3907
0.016 | 0.039564 | 0.010265 | 1.0152 | 1.0159 | 1.0159 | 1.0159 | 0.0022817 | 2.85 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0127 | 0.0063372 | 1.0097 | 1.0097 | 1.0097 | 1.0097 | 0.7 | 0.0015874 | 2.5254 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0124 | 0.0060301 | 1.0092 | 1.0092 | 1.0092 | 1.0092 | 0.67472 | 0.0015294 | 2.4942 | 0.0036 | 0.0036 | 0.0036 | 0.64372 | 0.0124 | 0.0060301 | 1.0092 | 1.0092 | 1.0092 | 1.0092 | 0.67472 | 0.0015294 | 16 | 1.5294 | 0.67472 | 1.0092 | 0.0036 | 2.4942
0.017 | 0.040606 | 0.011002 | 1.0164 | 1.0171 | 1.0171 | 1.0171 | 0.0025018 | 2.9389 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0137 | 0.0070011 | 1.0107 | 1.0107 | 1.0107 | 1.0107 | 0.71611 | 0.0017804 | 2.6238 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0137 | 0.0070011 | 1.0107 | 1.0107 | 1.0107 | 1.0107 | 0.71611 | 0.0017804 | 2.6238 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0137 | 0.0070011 | 1.0107 | 1.0107 | 1.0107 | 1.0107 | 0.71611 | 0.0017804 | 17 | 1.7804 | 0.71611 | 1.0107 | 0.0033 | 2.6238
0.018 | 0.041647 | 0.011726 | 1.0177 | 1.0182 | 1.0182 | 1.0182 | 0.0027289 | 3.0252 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0149 | 0.0078822 | 1.0121 | 1.0121 | 1.0121 | 1.0121 | 0.74596 | 0.0020234 | 2.7381 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0147 | 0.0076625 | 1.0118 | 1.0118 | 1.0118 | 1.0118 | 0.73054 | 0.0019809 | 2.7188 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0147 | 0.0076625 | 1.0118 | 1.0118 | 1.0118 | 1.0118 | 0.73054 | 0.0019809 | 18 | 1.9809 | 0.73054 | 1.0118 | 0.0033 | 2.7188
0.019 | 0.042688 | 0.012435 | 1.0189 | 1.0194 | 1.0194 | 1.0194 | 0.0029627 | 3.1093 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0159 | 0.0085432 | 1.0132 | 1.0132 | 1.0132 | 1.0132 | 0.75824 | 0.0022327 | 2.8295 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0157 | 0.0083193 | 1.0128 | 1.0128 | 1.0128 | 1.0128 | 0.74352 | 0.0021886 | 2.8107 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0157 | 0.0083193 | 1.0128 | 1.0128 | 1.0128 | 1.0128 | 0.74352 | 0.0021886 | 19 | 2.1886 | 0.74352 | 1.0128 | 0.0033 | 2.8107
0.02 | 0.043729 | 0.01313 | 1.02 | 1.0205 | 1.0205 | 1.0205 | 0.0032032 | 3.1912 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0169 | 0.0091975 | 1.0142 | 1.0142 | 1.0142 | 1.0142 | 0.76936 | 0.0024492 | 2.9181 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0167 | 0.0089699 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 0.75527 | 0.0024035 | 2.8998 | 0.0033 | 0.0033 | 0.0033 | 0.64432 | 0.0167 | 0.0089699 | 1.0138 | 1.0138 | 1.0138 | 1.0138 | 0.75527 | 0.0024035 | 20 | 2.4035 | 0.75527 | 1.0138 | 0.0033 | 2.8998
0.021 | 0.04477 | 0.01381 | 1.0212 | 1.0216 | 1.0216 | 1.0216 | 0.0034502 | 3.2712 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0179 | 0.0098438 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 0.77946 | 0.0026724 | 3.0042 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0179 | 0.0098438 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 0.77946 | 0.0026724 | 3.0042 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0179 | 0.0098438 | 1.0152 | 1.0152 | 1.0152 | 1.0152 | 0.77946 | 0.0026724 | 21 | 2.6724 | 0.77946 | 1.0152 | 0.0031 | 3.0042
0.022 | 0.045811 | 0.014476 | 1.0223 | 1.0227 | 1.0227 | 1.0227 | 0.0037035 | 3.3494 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0189 | 0.010481 | 1.0163 | 1.0162 | 1.0162 | 1.0162 | 0.78868 | 0.0029024 | 3.088 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0189 | 0.010481 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 0.78868 | 0.0029024 | 3.088 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0189 | 0.010481 | 1.0162 | 1.0162 | 1.0162 | 1.0162 | 0.78868 | 0.0029024 | 22 | 2.9024 | 0.78868 | 1.0162 | 0.0031 | 3.088
0.023 | 0.046853 | 0.015126 | 1.0235 | 1.0238 | 1.0238 | 1.0238 | 0.003963 | 3.4259 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0199 | 0.011109 | 1.0173 | 1.0172 | 1.0172 | 1.0172 | 0.79713 | 0.0031389 | 3.1697 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0199 | 0.011109 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 0.79713 | 0.0031389 | 3.1697 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0199 | 0.011109 | 1.0172 | 1.0172 | 1.0172 | 1.0172 | 0.79713 | 0.0031389 | 23 | 3.1389 | 0.79713 | 1.0172 | 0.0031 | 3.1697
0.024 | 0.047894 | 0.015762 | 1.0245 | 1.0248 | 1.0248 | 1.0248 | 0.0042286 | 3.5007 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.021267 | 0.012169 | 1.019 | 1.019 | 1.019 | 1.019 | 0.82712 | 0.0034775 | 3.2798 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0209 | 0.011727 | 1.0182 | 1.0182 | 1.0182 | 1.0182 | 0.80491 | 0.0033817 | 3.2494 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0209 | 0.011727 | 1.0182 | 1.0182 | 1.0182 | 1.0182 | 0.80491 | 0.0033817 | 24 | 3.3817 | 0.80491 | 1.0182 | 0.0031 | 3.2494
0.025 | 0.048935 | 0.016383 | 1.0256 | 1.0259 | 1.0259 | 1.0259 | 0.0045001 | 3.5741 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.022267 | 0.012779 | 1.02 | 1.0199 | 1.0199 | 1.0199 | 0.83351 | 0.0037292 | 3.3571 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0219 | 0.012333 | 1.0192 | 1.0192 | 1.0192 | 1.0192 | 0.81208 | 0.0036308 | 3.3273 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0219 | 0.012333 | 1.0192 | 1.0192 | 1.0192 | 1.0192 | 0.81208 | 0.0036308 | 25 | 3.6308 | 0.81208 | 1.0192 | 0.0031 | 3.3273
0.026 | 0.049976 | 0.016989 | 1.0267 | 1.0269 | 1.0269 | 1.0269 | 0.0047775 | 3.6461 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.023267 | 0.013377 | 1.021 | 1.0209 | 1.0209 | 1.0209 | 0.83942 | 0.003987 | 3.4328 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0229 | 0.01293 | 1.0202 | 1.0202 | 1.0202 | 1.0202 | 0.81872 | 0.003886 | 3.4035 | 0.0031 | 0.0031 | 0.0031 | 0.64472 | 0.0229 | 0.01293 | 1.0202 | 1.0202 | 1.0202 | 1.0202 | 0.81872 | 0.003886 | 26 | 3.886 | 0.81872 | 1.0202 | 0.0031 | 3.4035
0.027 | 0.051017 | 0.017581 | 1.0277 | 1.0279 | 1.0279 | 1.0279 | 0.0050606 | 3.7167 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.024267 | 0.013964 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 0.8449 | 0.0042508 | 3.5069 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.024267 | 0.013964 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 0.8449 | 0.0042508 | 3.5069 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.024267 | 0.013964 | 1.0219 | 1.0219 | 1.0219 | 1.0219 | 0.8449 | 0.0042508 | 27 | 4.2508 | 0.8449 | 1.0219 | 0.0027333 | 3.5069
0.028 | 0.052058 | 0.018159 | 1.0287 | 1.0288 | 1.0288 | 1.0288 | 0.0053494 | 3.7861 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.025267 | 0.014539 | 1.0229 | 1.0228 | 1.0228 | 1.0228 | 0.85001 | 0.0045204 | 3.5795 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.025267 | 0.014539 | 1.0228 | 1.0228 | 1.0228 | 1.0228 | 0.85001 | 0.0045204 | 3.5795 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.025267 | 0.014539 | 1.0228 | 1.0228 | 1.0228 | 1.0228 | 0.85001 | 0.0045204 | 28 | 4.5204 | 0.85001 | 1.0228 | 0.0027333 | 3.5795
0.029 | 0.0531 | 0.018722 | 1.0297 | 1.0298 | 1.0298 | 1.0298 | 0.0056437 | 3.8543 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.026267 | 0.015103 | 1.0238 | 1.0237 | 1.0237 | 1.0237 | 0.85477 | 0.0047958 | 3.6507 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.026267 | 0.015103 | 1.0237 | 1.0237 | 1.0237 | 1.0237 | 0.85477 | 0.0047958 | 3.6507 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.026267 | 0.015103 | 1.0237 | 1.0237 | 1.0237 | 1.0237 | 0.85477 | 0.0047958 | 29 | 4.7958 | 0.85477 | 1.0237 | 0.0027333 | 3.6507
0.03 | 0.054141 | 0.019273 | 1.0307 | 1.0307 | 1.0307 | 1.0307 | 0.0059435 | 3.9214 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.027267 | 0.015654 | 1.0247 | 1.0247 | 1.0247 | 1.0247 | 0.85922 | 0.0050767 | 3.7207 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.027267 | 0.015654 | 1.0247 | 1.0247 | 1.0247 | 1.0247 | 0.85922 | 0.0050767 | 3.7207 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.027267 | 0.015654 | 1.0247 | 1.0247 | 1.0247 | 1.0247 | 0.85922 | 0.0050767 | 30 | 5.0767 | 0.85922 | 1.0247 | 0.0027333 | 3.7207
0.031 | 0.055182 | 0.01981 | 1.0316 | 1.0316 | 1.0316 | 1.0316 | 0.0062487 | 3.9874 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.028267 | 0.016195 | 1.0256 | 1.0255 | 1.0255 | 1.0255 | 0.86339 | 0.0053633 | 3.7894 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.028267 | 0.016195 | 1.0255 | 1.0255 | 1.0255 | 1.0255 | 0.86339 | 0.0053633 | 3.7894 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.028267 | 0.016195 | 1.0255 | 1.0255 | 1.0255 | 1.0255 | 0.86339 | 0.0053633 | 31 | 5.3633 | 0.86339 | 1.0255 | 0.0027333 | 3.7894
0.032 | 0.056223 | 0.020334 | 1.0325 | 1.0325 | 1.0325 | 1.0325 | 0.0065591 | 4.0524 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.029367 | 0.016849 | 1.0267 | 1.0266 | 1.0266 | 1.0266 | 0.87202 | 0.0056871 | 3.8642 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.029267 | 0.016724 | 1.0264 | 1.0264 | 1.0264 | 1.0264 | 0.86731 | 0.0056552 | 3.857 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.029267 | 0.016724 | 1.0264 | 1.0264 | 1.0264 | 1.0264 | 0.86731 | 0.0056552 | 32 | 5.6552 | 0.86731 | 1.0264 | 0.0027333 | 3.857
0.033 | 0.057264 | 0.020845 | 1.0334 | 1.0334 | 1.0334 | 1.0334 | 0.0068748 | 4.1164 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.030367 | 0.017367 | 1.0276 | 1.0275 | 1.0275 | 1.0275 | 0.87558 | 0.0059851 | 3.9305 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.030267 | 0.017242 | 1.0273 | 1.0273 | 1.0273 | 1.0273 | 0.87099 | 0.0059525 | 3.9234 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.030267 | 0.017242 | 1.0273 | 1.0273 | 1.0273 | 1.0273 | 0.87099 | 0.0059525 | 33 | 5.9525 | 0.87099 | 1.0273 | 0.0027333 | 3.9234
0.034 | 0.058305 | 0.021345 | 1.0343 | 1.0342 | 1.0342 | 1.0342 | 0.0071956 | 4.1794 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.031367 | 0.017874 | 1.0284 | 1.0284 | 1.0284 | 1.0284 | 0.87893 | 0.0062884 | 3.9958 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.031267 | 0.017749 | 1.0281 | 1.0281 | 1.0281 | 1.0281 | 0.87446 | 0.0062551 | 3.9888 | 0.0028 | 0.0027 | 0.0027333 | 0.64545 | 0.031267 | 0.017749 | 1.0281 | 1.0281 | 1.0281 | 1.0281 | 0.87446 | 0.0062551 | 34 | 6.2551 | 0.87446 | 1.0281 | 0.0027333 | 3.9888
0.035 | 0.059347 | 0.021832 | 1.0352 | 1.0351 | 1.0351 | 1.0351 | 0.0075214 | 4.2416 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.032367 | 0.018369 | 1.0292 | 1.0292 | 1.0292 | 1.0292 | 0.8821 | 0.0065968 | 4.0601 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.032367 | 0.018369 | 1.0292 | 1.0292 | 1.0292 | 1.0292 | 0.8821 | 0.0065968 | 4.0601 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.032367 | 0.018369 | 1.0292 | 1.0292 | 1.0292 | 1.0292 | 0.8821 | 0.0065968 | 35 | 6.5968 | 0.8821 | 1.0292 | 0.0026333 | 4.0601
0.036 | 0.060388 | 0.022308 | 1.036 | 1.0359 | 1.0359 | 1.0359 | 0.0078523 | 4.3029 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.033367 | 0.018855 | 1.0301 | 1.03 | 1.03 | 1.03 | 0.88509 | 0.0069104 | 4.1235 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.033367 | 0.018855 | 1.03 | 1.03 | 1.03 | 1.03 | 0.88509 | 0.0069104 | 4.1235 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.033367 | 0.018855 | 1.03 | 1.03 | 1.03 | 1.03 | 0.88509 | 0.0069104 | 36 | 6.9104 | 0.88509 | 1.03 | 0.0026333 | 4.1235
0.037 | 0.061429 | 0.022772 | 1.0369 | 1.0367 | 1.0367 | 1.0367 | 0.0081881 | 4.3634 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.034367 | 0.01933 | 1.0309 | 1.0308 | 1.0308 | 1.0308 | 0.88792 | 0.007229 | 4.1859 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.034367 | 0.01933 | 1.0308 | 1.0308 | 1.0308 | 1.0308 | 0.88792 | 0.007229 | 4.1859 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.034367 | 0.01933 | 1.0308 | 1.0308 | 1.0308 | 1.0308 | 0.88792 | 0.007229 | 37 | 7.229 | 0.88792 | 1.0308 | 0.0026333 | 4.1859
0.038 | 0.06247 | 0.023226 | 1.0377 | 1.0375 | 1.0375 | 1.0375 | 0.0085288 | 4.4231 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.035367 | 0.019794 | 1.0317 | 1.0316 | 1.0316 | 1.0316 | 0.89061 | 0.0075526 | 4.2474 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.035367 | 0.019794 | 1.0316 | 1.0316 | 1.0316 | 1.0316 | 0.89061 | 0.0075526 | 4.2474 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.035367 | 0.019794 | 1.0316 | 1.0316 | 1.0316 | 1.0316 | 0.89061 | 0.0075526 | 38 | 7.5526 | 0.89061 | 1.0316 | 0.0026333 | 4.2474
0.039 | 0.063511 | 0.023669 | 1.0385 | 1.0383 | 1.0383 | 1.0383 | 0.0088742 | 4.482 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.036367 | 0.020249 | 1.0324 | 1.0324 | 1.0324 | 1.0324 | 0.89316 | 0.0078811 | 4.3081 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.036367 | 0.020249 | 1.0324 | 1.0324 | 1.0324 | 1.0324 | 0.89316 | 0.0078811 | 4.3081 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.036367 | 0.020249 | 1.0324 | 1.0324 | 1.0324 | 1.0324 | 0.89316 | 0.0078811 | 39 | 7.8811 | 0.89316 | 1.0324 | 0.0026333 | 4.3081
0.04 | 0.064552 | 0.024101 | 1.0392 | 1.039 | 1.039 | 1.039 | 0.0092244 | 4.5402 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0373 | 0.020611 | 1.0331 | 1.033 | 1.033 | 1.033 | 0.89301 | 0.0081896 | 4.3637 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.037367 | 0.020694 | 1.0331 | 1.0331 | 1.0331 | 1.0331 | 0.89559 | 0.0082144 | 4.3681 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.037367 | 0.020694 | 1.0331 | 1.0331 | 1.0331 | 1.0331 | 0.89559 | 0.0082144 | 40 | 8.2144 | 0.89559 | 1.0331 | 0.0026333 | 4.3681
0.041 | 0.065594 | 0.024524 | 1.04 | 1.0398 | 1.0398 | 1.0398 | 0.0095793 | 4.5977 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0383 | 0.021047 | 1.0338 | 1.0337 | 1.0337 | 1.0337 | 0.89537 | 0.0085273 | 4.4228 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.038367 | 0.021129 | 1.0339 | 1.0339 | 1.0339 | 1.0339 | 0.8979 | 0.0085525 | 4.4272 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.038367 | 0.021129 | 1.0339 | 1.0339 | 1.0339 | 1.0339 | 0.8979 | 0.0085525 | 41 | 8.5525 | 0.8979 | 1.0339 | 0.0026333 | 4.4272
0.042 | 0.066635 | 0.024937 | 1.0407 | 1.0405 | 1.0405 | 1.0405 | 0.0099389 | 4.6545 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0393 | 0.021473 | 1.0345 | 1.0345 | 1.0345 | 1.0345 | 0.89763 | 0.0088697 | 4.4812 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.039367 | 0.021555 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 0.9001 | 0.0088954 | 4.4856 | 0.0027 | 0.0026 | 0.0026333 | 0.64565 | 0.039367 | 0.021555 | 1.0346 | 1.0346 | 1.0346 | 1.0346 | 0.9001 | 0.0088954 | 42 | 8.8954 | 0.9001 | 1.0346 | 0.0026333 | 4.4856
0.043 | 0.067676 | 0.025341 | 1.0415 | 1.0412 | 1.0412 | 1.0412 | 0.010303 | 4.7107 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0403 | 0.02189 | 1.0353 | 1.0352 | 1.0352 | 1.0352 | 0.89978 | 0.0092168 | 4.539 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0403 | 0.02189 | 1.0352 | 1.0352 | 1.0352 | 1.0352 | 0.89978 | 0.0092168 | 4.539 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0403 | 0.02189 | 1.0352 | 1.0352 | 1.0352 | 1.0352 | 0.89978 | 0.0092168 | 43 | 9.2168 | 0.89978 | 1.0352 | 0.0027 | 4.539
0.044 | 0.068717 | 0.025735 | 1.0422 | 1.0419 | 1.0419 | 1.0419 | 0.010672 | 4.7662 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0413 | 0.022299 | 1.036 | 1.0359 | 1.0359 | 1.0359 | 0.90184 | 0.0095685 | 4.596 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0413 | 0.022299 | 1.0359 | 1.0359 | 1.0359 | 1.0359 | 0.90184 | 0.0095685 | 4.596 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0413 | 0.022299 | 1.0359 | 1.0359 | 1.0359 | 1.0359 | 0.90184 | 0.0095685 | 44 | 9.5685 | 0.90184 | 1.0359 | 0.0027 | 4.596
0.045 | 0.069758 | 0.026121 | 1.0429 | 1.0426 | 1.0426 | 1.0426 | 0.011045 | 4.8211 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0423 | 0.022699 | 1.0367 | 1.0366 | 1.0366 | 1.0366 | 0.9038 | 0.0099248 | 4.6523 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0423 | 0.022699 | 1.0366 | 1.0366 | 1.0366 | 1.0366 | 0.9038 | 0.0099248 | 4.6523 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0423 | 0.022699 | 1.0366 | 1.0366 | 1.0366 | 1.0366 | 0.9038 | 0.0099248 | 45 | 9.9248 | 0.9038 | 1.0366 | 0.0027 | 4.6523
0.046 | 0.070799 | 0.026497 | 1.0436 | 1.0433 | 1.0433 | 1.0433 | 0.011422 | 4.8754 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0433 | 0.02309 | 1.0373 | 1.0373 | 1.0373 | 1.0373 | 0.90568 | 0.010286 | 4.708 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0433 | 0.02309 | 1.0373 | 1.0373 | 1.0373 | 1.0373 | 0.90568 | 0.010286 | 4.708 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0433 | 0.02309 | 1.0373 | 1.0373 | 1.0373 | 1.0373 | 0.90568 | 0.010286 | 46 | 10.2855 | 0.90568 | 1.0373 | 0.0027 | 4.708
0.047 | 0.071841 | 0.026866 | 1.0443 | 1.0439 | 1.0439 | 1.0439 | 0.011804 | 4.9292 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0443 | 0.023474 | 1.038 | 1.0379 | 1.0379 | 1.0379 | 0.90749 | 0.010651 | 4.7631 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0443 | 0.023474 | 1.0379 | 1.0379 | 1.0379 | 1.0379 | 0.90749 | 0.010651 | 4.7631 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0443 | 0.023474 | 1.0379 | 1.0379 | 1.0379 | 1.0379 | 0.90749 | 0.010651 | 47 | 10.6507 | 0.90749 | 1.0379 | 0.0027 | 4.7631
0.048 | 0.072882 | 0.027227 | 1.0449 | 1.0446 | 1.0446 | 1.0446 | 0.01219 | 4.9824 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0453 | 0.023849 | 1.0387 | 1.0386 | 1.0386 | 1.0386 | 0.90922 | 0.01102 | 4.8176 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0453 | 0.023849 | 1.0386 | 1.0386 | 1.0386 | 1.0386 | 0.90922 | 0.01102 | 4.8176 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0453 | 0.023849 | 1.0386 | 1.0386 | 1.0386 | 1.0386 | 0.90922 | 0.01102 | 48 | 11.0203 | 0.90922 | 1.0386 | 0.0027 | 4.8176
0.049 | 0.073923 | 0.027579 | 1.0456 | 1.0452 | 1.0452 | 1.0452 | 0.012581 | 5.035 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.046033 | 0.023899 | 1.0388 | 1.0387 | 1.0387 | 1.0387 | 0.90227 | 0.011281 | 4.8552 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0463 | 0.024217 | 1.0392 | 1.0392 | 1.0392 | 1.0392 | 0.91088 | 0.011394 | 4.8714 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0463 | 0.024217 | 1.0392 | 1.0392 | 1.0392 | 1.0392 | 0.91088 | 0.011394 | 49 | 11.3943 | 0.91088 | 1.0392 | 0.0027 | 4.8714
0.05 | 0.074964 | 0.027924 | 1.0462 | 1.0458 | 1.0458 | 1.0458 | 0.012976 | 5.0871 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.047033 | 0.02426 | 1.0394 | 1.0393 | 1.0393 | 1.0393 | 0.90402 | 0.011657 | 4.9086 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0473 | 0.024577 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 0.91247 | 0.011773 | 4.9248 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0473 | 0.024577 | 1.0399 | 1.0399 | 1.0399 | 1.0399 | 0.91247 | 0.011773 | 50 | 11.7726 | 0.91247 | 1.0399 | 0.0027 | 4.9248
0.051 | 0.076005 | 0.028262 | 1.0468 | 1.0464 | 1.0464 | 1.0464 | 0.013375 | 5.1387 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.048033 | 0.024615 | 1.04 | 1.0399 | 1.0399 | 1.0399 | 0.90569 | 0.012038 | 4.9615 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0483 | 0.02493 | 1.0405 | 1.0405 | 1.0405 | 1.0405 | 0.914 | 0.012155 | 4.9775 | 0.0029 | 0.0026 | 0.0027 | 0.64552 | 0.0483 | 0.02493 | 1.0405 | 1.0405 | 1.0405 | 1.0405 | 0.914 | 0.012155 | 51 | 12.1551 | 0.914 | 1.0405 | 0.0027 | 4.9775
0.052 | 0.077046 | 0.028592 | 1.0474 | 1.047 | 1.047 | 1.047 | 0.013778 | 5.1899 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.049033 | 0.024962 | 1.0406 | 1.0405 | 1.0405 | 1.0405 | 0.90731 | 0.012423 | 5.0139 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.049033 | 0.024962 | 1.0405 | 1.0405 | 1.0405 | 1.0405 | 0.90731 | 0.012423 | 5.0139 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.049033 | 0.024962 | 1.0405 | 1.0405 | 1.0405 | 1.0405 | 0.90731 | 0.012423 | 52 | 12.4234 | 0.90731 | 1.0405 | 0.0029667 | 5.0139
0.053 | 0.078088 | 0.028916 | 1.048 | 1.0476 | 1.0476 | 1.0476 | 0.014185 | 5.2405 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.050033 | 0.025302 | 1.0412 | 1.0411 | 1.0411 | 1.0411 | 0.90886 | 0.012813 | 5.0657 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.050033 | 0.025302 | 1.0411 | 1.0411 | 1.0411 | 1.0411 | 0.90886 | 0.012813 | 5.0657 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.050033 | 0.025302 | 1.0411 | 1.0411 | 1.0411 | 1.0411 | 0.90886 | 0.012813 | 53 | 12.8128 | 0.90886 | 1.0411 | 0.0029667 | 5.0657
0.054 | 0.079129 | 0.029233 | 1.0486 | 1.0482 | 1.0482 | 1.0482 | 0.014596 | 5.2907 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.051033 | 0.025635 | 1.0418 | 1.0417 | 1.0417 | 1.0417 | 0.91036 | 0.013206 | 5.1171 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.051033 | 0.025635 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 0.91036 | 0.013206 | 5.1171 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.051033 | 0.025635 | 1.0417 | 1.0417 | 1.0417 | 1.0417 | 0.91036 | 0.013206 | 54 | 13.2063 | 0.91036 | 1.0417 | 0.0029667 | 5.1171
0.055 | 0.08017 | 0.029543 | 1.0492 | 1.0487 | 1.0487 | 1.0487 | 0.015012 | 5.3404 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.052033 | 0.025962 | 1.0424 | 1.0423 | 1.0423 | 1.0423 | 0.9118 | 0.013604 | 5.1679 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.052033 | 0.025962 | 1.0423 | 1.0423 | 1.0423 | 1.0423 | 0.9118 | 0.013604 | 5.1679 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.052033 | 0.025962 | 1.0423 | 1.0423 | 1.0423 | 1.0423 | 0.9118 | 0.013604 | 55 | 13.6039 | 0.9118 | 1.0423 | 0.0029667 | 5.1679
0.056 | 0.081211 | 0.029846 | 1.0497 | 1.0493 | 1.0493 | 1.0493 | 0.015431 | 5.3897 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.053033 | 0.026282 | 1.043 | 1.0429 | 1.0429 | 1.0429 | 0.9132 | 0.014006 | 5.2183 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.053033 | 0.026282 | 1.0429 | 1.0429 | 1.0429 | 1.0429 | 0.9132 | 0.014006 | 5.2183 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.053033 | 0.026282 | 1.0429 | 1.0429 | 1.0429 | 1.0429 | 0.9132 | 0.014006 | 56 | 14.0056 | 0.9132 | 1.0429 | 0.0029667 | 5.2183
0.057 | 0.082252 | 0.030144 | 1.0503 | 1.0498 | 1.0498 | 1.0498 | 0.015855 | 5.4385 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.054033 | 0.026596 | 1.0435 | 1.0434 | 1.0434 | 1.0434 | 0.91454 | 0.014411 | 5.2682 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.054033 | 0.026596 | 1.0434 | 1.0434 | 1.0434 | 1.0434 | 0.91454 | 0.014411 | 5.2682 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.054033 | 0.026596 | 1.0434 | 1.0434 | 1.0434 | 1.0434 | 0.91454 | 0.014411 | 57 | 14.4113 | 0.91454 | 1.0434 | 0.0029667 | 5.2682
0.058 | 0.083293 | 0.030436 | 1.0508 | 1.0504 | 1.0504 | 1.0504 | 0.016282 | 5.4869 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.055033 | 0.026904 | 1.0441 | 1.044 | 1.044 | 1.044 | 0.91584 | 0.014821 | 5.3177 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.055033 | 0.026904 | 1.044 | 1.044 | 1.044 | 1.044 | 0.91584 | 0.014821 | 5.3177 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.055033 | 0.026904 | 1.044 | 1.044 | 1.044 | 1.044 | 0.91584 | 0.014821 | 58 | 14.821 | 0.91584 | 1.044 | 0.0029667 | 5.3177
0.059 | 0.084335 | 0.030721 | 1.0514 | 1.0509 | 1.0509 | 1.0509 | 0.016713 | 5.535 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0556 | 0.026716 | 1.0437 | 1.0436 | 1.0436 | 1.0436 | 0.90526 | 0.015025 | 5.342 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.056033 | 0.027207 | 1.0445 | 1.0445 | 1.0445 | 1.0445 | 0.9171 | 0.015235 | 5.3667 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.056033 | 0.027207 | 1.0445 | 1.0445 | 1.0445 | 1.0445 | 0.9171 | 0.015235 | 59 | 15.2347 | 0.9171 | 1.0445 | 0.0029667 | 5.3667
0.06 | 0.085376 | 0.031001 | 1.0519 | 1.0514 | 1.0514 | 1.0514 | 0.017148 | 5.5826 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0566 | 0.027014 | 1.0443 | 1.0442 | 1.0442 | 1.0442 | 0.90664 | 0.01544 | 5.3908 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.057033 | 0.027503 | 1.045 | 1.0451 | 1.0451 | 1.0451 | 0.91831 | 0.015652 | 5.4153 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.057033 | 0.027503 | 1.0451 | 1.0451 | 1.0451 | 1.0451 | 0.91831 | 0.015652 | 60 | 15.6523 | 0.91831 | 1.0451 | 0.0029667 | 5.4153
0.061 | 0.086417 | 0.031276 | 1.0524 | 1.0519 | 1.0519 | 1.0519 | 0.017587 | 5.6298 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0576 | 0.027307 | 1.0448 | 1.0447 | 1.0447 | 1.0447 | 0.90798 | 0.015859 | 5.4391 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.058033 | 0.027794 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 0.91948 | 0.016074 | 5.4635 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.058033 | 0.027794 | 1.0456 | 1.0456 | 1.0456 | 1.0456 | 0.91948 | 0.016074 | 61 | 16.0738 | 0.91948 | 1.0456 | 0.0029667 | 5.4635
0.062 | 0.087458 | 0.031545 | 1.0529 | 1.0524 | 1.0524 | 1.0524 | 0.01803 | 5.6767 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0586 | 0.027594 | 1.0453 | 1.0452 | 1.0452 | 1.0452 | 0.90928 | 0.016282 | 5.487 | 0.0033 | 0.0028 | 0.0029667 | 0.64498 | 0.059033 | 0.028079 | 1.0461 | 1.0461 | 1.0461 | 1.0461 | 0.92062 | 0.016499 | 5.5112 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0586 | 0.027594 | 1.0452 | 1.0452 | 1.0452 | 1.0452 | 0.90928 | 0.016282 | 62 | 16.2823 | 0.90928 | 1.0452 | 0.0034 | 5.5112
0.063 | 0.088499 | 0.031809 | 1.0534 | 1.0529 | 1.0529 | 1.0529 | 0.018476 | 5.7231 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0596 | 0.027877 | 1.0458 | 1.0457 | 1.0457 | 1.0457 | 0.91054 | 0.016709 | 5.5345 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0596 | 0.027877 | 1.0457 | 1.0457 | 1.0457 | 1.0457 | 0.91054 | 0.016709 | 5.5345 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0596 | 0.027877 | 1.0457 | 1.0457 | 1.0457 | 1.0457 | 0.91054 | 0.016709 | 63 | 16.7089 | 0.91054 | 1.0457 | 0.0034 | 5.5345
0.064 | 0.08954 | 0.032068 | 1.0539 | 1.0534 | 1.0534 | 1.0534 | 0.018927 | 5.7693 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0606 | 0.028154 | 1.0463 | 1.0462 | 1.0462 | 1.0462 | 0.91175 | 0.017139 | 5.5816 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0606 | 0.028154 | 1.0462 | 1.0462 | 1.0462 | 1.0462 | 0.91175 | 0.017139 | 5.5816 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0606 | 0.028154 | 1.0462 | 1.0462 | 1.0462 | 1.0462 | 0.91175 | 0.017139 | 64 | 17.1394 | 0.91175 | 1.0462 | 0.0034 | 5.5816
0.065 | 0.090582 | 0.032322 | 1.0544 | 1.0538 | 1.0538 | 1.0538 | 0.019381 | 5.815 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0616 | 0.028425 | 1.0468 | 1.0467 | 1.0467 | 1.0467 | 0.91294 | 0.017574 | 5.6284 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0616 | 0.028425 | 1.0467 | 1.0467 | 1.0467 | 1.0467 | 0.91294 | 0.017574 | 5.6284 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0616 | 0.028425 | 1.0467 | 1.0467 | 1.0467 | 1.0467 | 0.91294 | 0.017574 | 65 | 17.5736 | 0.91294 | 1.0467 | 0.0034 | 5.6284
0.066 | 0.091623 | 0.032571 | 1.0548 | 1.0543 | 1.0543 | 1.0543 | 0.019838 | 5.8604 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0626 | 0.028692 | 1.0473 | 1.0472 | 1.0472 | 1.0472 | 0.91408 | 0.018012 | 5.6747 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0626 | 0.028692 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 0.91408 | 0.018012 | 5.6747 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0626 | 0.028692 | 1.0472 | 1.0472 | 1.0472 | 1.0472 | 0.91408 | 0.018012 | 66 | 18.0115 | 0.91408 | 1.0472 | 0.0034 | 5.6747
0.067 | 0.092664 | 0.032815 | 1.0553 | 1.0548 | 1.0548 | 1.0548 | 0.0203 | 5.9055 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0636 | 0.028955 | 1.0478 | 1.0477 | 1.0477 | 1.0477 | 0.91519 | 0.018453 | 5.7207 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0636 | 0.028955 | 1.0477 | 1.0477 | 1.0477 | 1.0477 | 0.91519 | 0.018453 | 5.7207 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0636 | 0.028955 | 1.0477 | 1.0477 | 1.0477 | 1.0477 | 0.91519 | 0.018453 | 67 | 18.4532 | 0.91519 | 1.0477 | 0.0034 | 5.7207
0.068 | 0.093705 | 0.033055 | 1.0557 | 1.0552 | 1.0552 | 1.0552 | 0.020765 | 5.9503 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0646 | 0.029212 | 1.0482 | 1.0481 | 1.0481 | 1.0481 | 0.91627 | 0.018899 | 5.7664 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0646 | 0.029212 | 1.0481 | 1.0481 | 1.0481 | 1.0481 | 0.91627 | 0.018899 | 5.7664 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0646 | 0.029212 | 1.0481 | 1.0481 | 1.0481 | 1.0481 | 0.91627 | 0.018899 | 68 | 18.8985 | 0.91627 | 1.0481 | 0.0034 | 5.7664
0.069 | 0.094746 | 0.033291 | 1.0562 | 1.0557 | 1.0556 | 1.0556 | 0.021233 | 5.9947 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0656 | 0.029465 | 1.0487 | 1.0486 | 1.0486 | 1.0486 | 0.91732 | 0.019348 | 5.8117 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0656 | 0.029465 | 1.0486 | 1.0486 | 1.0486 | 1.0486 | 0.91732 | 0.019348 | 5.8117 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0656 | 0.029465 | 1.0486 | 1.0486 | 1.0486 | 1.0486 | 0.91732 | 0.019348 | 69 | 19.3475 | 0.91732 | 1.0486 | 0.0034 | 5.8117
0.07 | 0.095787 | 0.033522 | 1.0566 | 1.0561 | 1.0561 | 1.0561 | 0.021705 | 6.0388 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.066033 | 0.029108 | 1.0481 | 1.0479 | 1.0479 | 1.0479 | 0.90505 | 0.019493 | 5.8262 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0666 | 0.029714 | 1.049 | 1.049 | 1.049 | 1.049 | 0.91834 | 0.0198 | 5.8567 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0666 | 0.029714 | 1.049 | 1.049 | 1.049 | 1.049 | 0.91834 | 0.0198 | 70 | 19.8001 | 0.91834 | 1.049 | 0.0034 | 5.8567
0.071 | 0.096829 | 0.033749 | 1.0571 | 1.0565 | 1.0565 | 1.0565 | 0.022181 | 6.0826 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.067033 | 0.029354 | 1.0485 | 1.0484 | 1.0484 | 1.0484 | 0.9062 | 0.019946 | 5.871 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0676 | 0.029958 | 1.0495 | 1.0495 | 1.0495 | 1.0495 | 0.91933 | 0.020256 | 5.9013 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0676 | 0.029958 | 1.0495 | 1.0495 | 1.0495 | 1.0495 | 0.91933 | 0.020256 | 71 | 20.2563 | 0.91933 | 1.0495 | 0.0034 | 5.9013
0.072 | 0.09787 | 0.033972 | 1.0575 | 1.0569 | 1.0569 | 1.0569 | 0.02266 | 6.1261 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.068033 | 0.029597 | 1.049 | 1.0488 | 1.0488 | 1.0488 | 0.90732 | 0.020403 | 5.9155 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0686 | 0.030198 | 1.0499 | 1.0499 | 1.0499 | 1.0499 | 0.92029 | 0.020716 | 5.9456 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0686 | 0.030198 | 1.0499 | 1.0499 | 1.0499 | 1.0499 | 0.92029 | 0.020716 | 72 | 20.7161 | 0.92029 | 1.0499 | 0.0034 | 5.9456
0.073 | 0.098911 | 0.03419 | 1.0579 | 1.0573 | 1.0573 | 1.0573 | 0.023143 | 6.1693 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.069033 | 0.029835 | 1.0494 | 1.0493 | 1.0493 | 1.0493 | 0.9084 | 0.020863 | 5.9596 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0696 | 0.030434 | 1.0503 | 1.0504 | 1.0504 | 1.0504 | 0.92123 | 0.021179 | 5.9896 | 0.0038 | 0.0032 | 0.0034 | 0.64412 | 0.0696 | 0.030434 | 1.0504 | 1.0504 | 1.0504 | 1.0504 | 0.92123 | 0.021179 | 73 | 21.1794 | 0.92123 | 1.0504 | 0.0034 | 5.9896
0.074 | 0.099952 | 0.034405 | 1.0583 | 1.0577 | 1.0577 | 1.0577 | 0.023629 | 6.2122 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.070033 | 0.030069 | 1.0498 | 1.0497 | 1.0497 | 1.0497 | 0.90946 | 0.021326 | 6.0035 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.070033 | 0.030069 | 1.0497 | 1.0497 | 1.0497 | 1.0497 | 0.90946 | 0.021326 | 6.0035 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.070033 | 0.030069 | 1.0497 | 1.0497 | 1.0497 | 1.0497 | 0.90946 | 0.021326 | 74 | 21.3264 | 0.90946 | 1.0497 | 0.0039667 | 6.0035
0.075 | 0.10099 | 0.034617 | 1.0587 | 1.0581 | 1.0581 | 1.0581 | 0.024119 | 6.2548 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.071033 | 0.0303 | 1.0502 | 1.0501 | 1.0501 | 1.0501 | 0.91049 | 0.021794 | 6.047 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.071033 | 0.0303 | 1.0501 | 1.0501 | 1.0501 | 1.0501 | 0.91049 | 0.021794 | 6.047 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.071033 | 0.0303 | 1.0501 | 1.0501 | 1.0501 | 1.0501 | 0.91049 | 0.021794 | 75 | 21.7935 | 0.91049 | 1.0501 | 0.0039667 | 6.047
0.076 | 0.10203 | 0.034824 | 1.0591 | 1.0585 | 1.0585 | 1.0585 | 0.024612 | 6.2971 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.072033 | 0.030526 | 1.0507 | 1.0505 | 1.0505 | 1.0505 | 0.91149 | 0.022264 | 6.0902 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.072033 | 0.030526 | 1.0505 | 1.0505 | 1.0505 | 1.0505 | 0.91149 | 0.022264 | 6.0902 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.072033 | 0.030526 | 1.0505 | 1.0505 | 1.0505 | 1.0505 | 0.91149 | 0.022264 | 76 | 22.2641 | 0.91149 | 1.0505 | 0.0039667 | 6.0902
0.077 | 0.10308 | 0.035028 | 1.0595 | 1.0589 | 1.0589 | 1.0589 | 0.025108 | 6.3392 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.073033 | 0.030749 | 1.0511 | 1.0509 | 1.0509 | 1.0509 | 0.91247 | 0.022738 | 6.1331 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.073033 | 0.030749 | 1.0509 | 1.0509 | 1.0509 | 1.0509 | 0.91247 | 0.022738 | 6.1331 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.073033 | 0.030749 | 1.0509 | 1.0509 | 1.0509 | 1.0509 | 0.91247 | 0.022738 | 77 | 22.7382 | 0.91247 | 1.0509 | 0.0039667 | 6.1331
0.078 | 0.10412 | 0.035229 | 1.0599 | 1.0593 | 1.0593 | 1.0593 | 0.025608 | 6.381 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.074033 | 0.030968 | 1.0515 | 1.0513 | 1.0513 | 1.0513 | 0.91343 | 0.023216 | 6.1757 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.074033 | 0.030968 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 0.91343 | 0.023216 | 6.1757 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.074033 | 0.030968 | 1.0513 | 1.0513 | 1.0513 | 1.0513 | 0.91343 | 0.023216 | 78 | 23.2157 | 0.91343 | 1.0513 | 0.0039667 | 6.1757
0.079 | 0.10516 | 0.035426 | 1.0602 | 1.0597 | 1.0597 | 1.0597 | 0.026111 | 6.4225 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.075033 | 0.031183 | 1.0519 | 1.0517 | 1.0517 | 1.0517 | 0.91436 | 0.023697 | 6.2181 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.075033 | 0.031183 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 0.91436 | 0.023697 | 6.2181 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.075033 | 0.031183 | 1.0517 | 1.0517 | 1.0517 | 1.0517 | 0.91436 | 0.023697 | 79 | 23.6965 | 0.91436 | 1.0517 | 0.0039667 | 6.2181
0.08 | 0.1062 | 0.035619 | 1.0606 | 1.06 | 1.06 | 1.06 | 0.026618 | 6.4638 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.076033 | 0.031395 | 1.0523 | 1.0521 | 1.0521 | 1.0521 | 0.91526 | 0.024181 | 6.2602 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.076033 | 0.031395 | 1.0521 | 1.0521 | 1.0521 | 1.0521 | 0.91526 | 0.024181 | 6.2602 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.076033 | 0.031395 | 1.0521 | 1.0521 | 1.0521 | 1.0521 | 0.91526 | 0.024181 | 80 | 24.1808 | 0.91526 | 1.0521 | 0.0039667 | 6.2602
0.081 | 0.10724 | 0.03581 | 1.061 | 1.0604 | 1.0604 | 1.0604 | 0.027128 | 6.5048 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0771 | 0.031672 | 1.0528 | 1.0526 | 1.0526 | 1.0526 | 0.91753 | 0.024709 | 6.3054 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.077033 | 0.031604 | 1.0525 | 1.0525 | 1.0525 | 1.0525 | 0.91615 | 0.024668 | 6.302 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.077033 | 0.031604 | 1.0525 | 1.0525 | 1.0525 | 1.0525 | 0.91615 | 0.024668 | 81 | 24.6684 | 0.91615 | 1.0525 | 0.0039667 | 6.302
0.082 | 0.10828 | 0.035997 | 1.0613 | 1.0608 | 1.0607 | 1.0607 | 0.027641 | 6.5456 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0781 | 0.031877 | 1.0531 | 1.053 | 1.053 | 1.053 | 0.91838 | 0.0252 | 6.3469 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.078033 | 0.031809 | 1.0529 | 1.0529 | 1.0529 | 1.0529 | 0.91701 | 0.025159 | 6.3435 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.078033 | 0.031809 | 1.0529 | 1.0529 | 1.0529 | 1.0529 | 0.91701 | 0.025159 | 82 | 25.1594 | 0.91701 | 1.0529 | 0.0039667 | 6.3435
0.083 | 0.10932 | 0.036181 | 1.0617 | 1.0611 | 1.0611 | 1.0611 | 0.028158 | 6.5861 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0791 | 0.032078 | 1.0535 | 1.0534 | 1.0534 | 1.0534 | 0.9192 | 0.025694 | 6.3882 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.079033 | 0.032011 | 1.0533 | 1.0533 | 1.0533 | 1.0533 | 0.91785 | 0.025654 | 6.3848 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.079033 | 0.032011 | 1.0533 | 1.0533 | 1.0533 | 1.0533 | 0.91785 | 0.025654 | 83 | 25.6537 | 0.91785 | 1.0533 | 0.0039667 | 6.3848
0.084 | 0.11036 | 0.036362 | 1.062 | 1.0615 | 1.0614 | 1.0614 | 0.028677 | 6.6264 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0801 | 0.032277 | 1.0539 | 1.0538 | 1.0538 | 1.0538 | 0.92001 | 0.026192 | 6.4292 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.080033 | 0.03221 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 0.91867 | 0.026151 | 6.4258 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.080033 | 0.03221 | 1.0536 | 1.0536 | 1.0536 | 1.0536 | 0.91867 | 0.026151 | 84 | 26.1512 | 0.91867 | 1.0536 | 0.0039667 | 6.4258
0.085 | 0.1114 | 0.036541 | 1.0624 | 1.0618 | 1.0618 | 1.0618 | 0.0292 | 6.6664 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0811 | 0.032472 | 1.0543 | 1.0541 | 1.0541 | 1.0541 | 0.9208 | 0.026694 | 6.4699 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.081033 | 0.032405 | 1.054 | 1.054 | 1.054 | 1.054 | 0.91948 | 0.026652 | 6.4665 | 0.0041 | 0.0039 | 0.0039667 | 0.64298 | 0.081033 | 0.032405 | 1.054 | 1.054 | 1.054 | 1.054 | 0.91948 | 0.026652 | 85 | 26.652 | 0.91948 | 1.054 | 0.0039667 | 6.4665
0.086 | 0.11245 | 0.036716 | 1.0627 | 1.0621 | 1.0621 | 1.0621 | 0.029727 | 6.7062 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0821 | 0.032664 | 1.0546 | 1.0545 | 1.0545 | 1.0545 | 0.92158 | 0.027198 | 6.5104 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0821 | 0.032664 | 1.0545 | 1.0545 | 1.0545 | 1.0545 | 0.92158 | 0.027198 | 6.5104 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0821 | 0.032664 | 1.0545 | 1.0545 | 1.0545 | 1.0545 | 0.92158 | 0.027198 | 86 | 27.1981 | 0.92158 | 1.0545 | 0.0039 | 6.5104
0.087 | 0.11349 | 0.036889 | 1.063 | 1.0625 | 1.0625 | 1.0625 | 0.030256 | 6.7458 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0831 | 0.032854 | 1.055 | 1.0548 | 1.0548 | 1.0548 | 0.92233 | 0.027706 | 6.5507 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0831 | 0.032854 | 1.0548 | 1.0548 | 1.0548 | 1.0548 | 0.92233 | 0.027706 | 6.5507 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0831 | 0.032854 | 1.0548 | 1.0548 | 1.0548 | 1.0548 | 0.92233 | 0.027706 | 87 | 27.7058 | 0.92233 | 1.0548 | 0.0039 | 6.5507
0.088 | 0.11453 | 0.037058 | 1.0634 | 1.0628 | 1.0628 | 1.0628 | 0.030789 | 6.7851 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0841 | 0.03304 | 1.0553 | 1.0552 | 1.0552 | 1.0552 | 0.92307 | 0.028217 | 6.5907 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0841 | 0.03304 | 1.0552 | 1.0552 | 1.0552 | 1.0552 | 0.92307 | 0.028217 | 6.5907 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0841 | 0.03304 | 1.0552 | 1.0552 | 1.0552 | 1.0552 | 0.92307 | 0.028217 | 88 | 28.2167 | 0.92307 | 1.0552 | 0.0039 | 6.5907
0.089 | 0.11557 | 0.037226 | 1.0637 | 1.0631 | 1.0631 | 1.0631 | 0.031324 | 6.8243 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0851 | 0.033224 | 1.0557 | 1.0555 | 1.0555 | 1.0555 | 0.92379 | 0.028731 | 6.6305 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0851 | 0.033224 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 0.92379 | 0.028731 | 6.6305 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0851 | 0.033224 | 1.0555 | 1.0555 | 1.0555 | 1.0555 | 0.92379 | 0.028731 | 89 | 28.7307 | 0.92379 | 1.0555 | 0.0039 | 6.6305
0.09 | 0.11661 | 0.03739 | 1.064 | 1.0634 | 1.0634 | 1.0634 | 0.031863 | 6.8632 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0861 | 0.033405 | 1.056 | 1.0559 | 1.0559 | 1.0559 | 0.9245 | 0.029248 | 6.67 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0861 | 0.033405 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0.9245 | 0.029248 | 6.67 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0861 | 0.033405 | 1.0559 | 1.0559 | 1.0559 | 1.0559 | 0.9245 | 0.029248 | 90 | 29.248 | 0.9245 | 1.0559 | 0.0039 | 6.67
0.091 | 0.11765 | 0.037552 | 1.0643 | 1.0637 | 1.0637 | 1.0637 | 0.032405 | 6.9019 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0871 | 0.033583 | 1.0563 | 1.0562 | 1.0562 | 1.0562 | 0.92519 | 0.029768 | 6.7094 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0871 | 0.033583 | 1.0562 | 1.0562 | 1.0562 | 1.0562 | 0.92519 | 0.029768 | 6.7094 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0871 | 0.033583 | 1.0562 | 1.0562 | 1.0562 | 1.0562 | 0.92519 | 0.029768 | 91 | 29.7684 | 0.92519 | 1.0562 | 0.0039 | 6.7094
0.092 | 0.11869 | 0.037711 | 1.0646 | 1.064 | 1.064 | 1.064 | 0.03295 | 6.9404 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0881 | 0.033758 | 1.0567 | 1.0565 | 1.0565 | 1.0565 | 0.92586 | 0.030292 | 6.7485 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0881 | 0.033758 | 1.0565 | 1.0565 | 1.0565 | 1.0565 | 0.92586 | 0.030292 | 6.7485 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0881 | 0.033758 | 1.0565 | 1.0565 | 1.0565 | 1.0565 | 0.92586 | 0.030292 | 92 | 30.292 | 0.92586 | 1.0565 | 0.0039 | 6.7485
0.093 | 0.11973 | 0.037868 | 1.0649 | 1.0644 | 1.0643 | 1.0643 | 0.033499 | 6.9786 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0891 | 0.033931 | 1.057 | 1.0568 | 1.0568 | 1.0568 | 0.92652 | 0.030819 | 6.7873 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0891 | 0.033931 | 1.0568 | 1.0568 | 1.0568 | 1.0568 | 0.92652 | 0.030819 | 6.7873 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0891 | 0.033931 | 1.0568 | 1.0568 | 1.0568 | 1.0568 | 0.92652 | 0.030819 | 93 | 30.8186 | 0.92652 | 1.0568 | 0.0039 | 6.7873
0.094 | 0.12078 | 0.038023 | 1.0652 | 1.0647 | 1.0646 | 1.0646 | 0.03405 | 7.0167 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0899 | 0.033908 | 1.0569 | 1.0568 | 1.0568 | 1.0568 | 0.92351 | 0.031214 | 6.8162 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0901 | 0.034101 | 1.0572 | 1.0572 | 1.0572 | 1.0572 | 0.92717 | 0.031348 | 6.826 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0901 | 0.034101 | 1.0572 | 1.0572 | 1.0572 | 1.0572 | 0.92717 | 0.031348 | 94 | 31.3484 | 0.92717 | 1.0572 | 0.0039 | 6.826
0.095 | 0.12182 | 0.038175 | 1.0655 | 1.0649 | 1.0649 | 1.0649 | 0.034604 | 7.0546 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0909 | 0.034076 | 1.0573 | 1.0571 | 1.0571 | 1.0571 | 0.92418 | 0.031746 | 6.8547 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0911 | 0.034269 | 1.0575 | 1.0575 | 1.0575 | 1.0575 | 0.9278 | 0.031881 | 6.8645 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0911 | 0.034269 | 1.0575 | 1.0575 | 1.0575 | 1.0575 | 0.9278 | 0.031881 | 95 | 31.8812 | 0.9278 | 1.0575 | 0.0039 | 6.8645
0.096 | 0.12286 | 0.038325 | 1.0658 | 1.0652 | 1.0652 | 1.0652 | 0.035162 | 7.0923 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0919 | 0.034242 | 1.0576 | 1.0574 | 1.0574 | 1.0574 | 0.92483 | 0.03228 | 6.893 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0921 | 0.034434 | 1.0578 | 1.0578 | 1.0578 | 1.0578 | 0.92843 | 0.032417 | 6.9027 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0921 | 0.034434 | 1.0578 | 1.0578 | 1.0578 | 1.0578 | 0.92843 | 0.032417 | 96 | 32.4172 | 0.92843 | 1.0578 | 0.0039 | 6.9027
0.097 | 0.1239 | 0.038473 | 1.0661 | 1.0655 | 1.0655 | 1.0655 | 0.035722 | 7.1298 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0929 | 0.034406 | 1.0579 | 1.0577 | 1.0577 | 1.0577 | 0.92547 | 0.032818 | 6.9311 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0931 | 0.034597 | 1.0581 | 1.0581 | 1.0581 | 1.0581 | 0.92903 | 0.032956 | 6.9408 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0931 | 0.034597 | 1.0581 | 1.0581 | 1.0581 | 1.0581 | 0.92903 | 0.032956 | 97 | 32.9561 | 0.92903 | 1.0581 | 0.0039 | 6.9408
0.098 | 0.12494 | 0.038619 | 1.0664 | 1.0658 | 1.0658 | 1.0658 | 0.036286 | 7.167 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0939 | 0.034567 | 1.0582 | 1.058 | 1.058 | 1.058 | 0.92609 | 0.033359 | 6.969 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0941 | 0.034758 | 1.0584 | 1.0584 | 1.0584 | 1.0584 | 0.92963 | 0.033498 | 6.9786 | 0.0045 | 0.0036 | 0.0039 | 0.64312 | 0.0941 | 0.034758 | 1.0584 | 1.0584 | 1.0584 | 1.0584 | 0.92963 | 0.033498 | 98 | 33.4981 | 0.92963 | 1.0584 | 0.0039 | 6.9786
0.099 | 0.12598 | 0.038762 | 1.0667 | 1.0661 | 1.0661 | 1.0661 | 0.036852 | 7.2041 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0949 | 0.034726 | 1.0585 | 1.0583 | 1.0583 | 1.0583 | 0.9267 | 0.033903 | 7.0066 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0949 | 0.034726 | 1.0583 | 1.0583 | 1.0583 | 1.0583 | 0.9267 | 0.033903 | 7.0066 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0949 | 0.034726 | 1.0583 | 1.0583 | 1.0583 | 1.0583 | 0.9267 | 0.033903 | 99 | 33.9032 | 0.9267 | 1.0583 | 0.0041 | 7.0066
0.1 | 0.12702 | 0.038903 | 1.067 | 1.0664 | 1.0663 | 1.0663 | 0.037421 | 7.2411 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0959 | 0.034883 | 1.0588 | 1.0586 | 1.0586 | 1.0586 | 0.9273 | 0.03445 | 7.0441 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0959 | 0.034883 | 1.0586 | 1.0586 | 1.0586 | 1.0586 | 0.9273 | 0.03445 | 7.0441 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0959 | 0.034883 | 1.0586 | 1.0586 | 1.0586 | 1.0586 | 0.9273 | 0.03445 | 100 | 34.4501 | 0.9273 | 1.0586 | 0.0041 | 7.0441
0.101 | 0.12806 | 0.039043 | 1.0672 | 1.0666 | 1.0666 | 1.0666 | 0.037994 | 7.2778 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0969 | 0.035037 | 1.0591 | 1.0589 | 1.0589 | 1.0589 | 0.92789 | 0.035 | 7.0814 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0969 | 0.035037 | 1.0589 | 1.0589 | 1.0589 | 1.0589 | 0.92789 | 0.035 | 7.0814 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0969 | 0.035037 | 1.0589 | 1.0589 | 1.0589 | 1.0589 | 0.92789 | 0.035 | 101 | 35 | 0.92789 | 1.0589 | 0.0041 | 7.0814
0.102 | 0.1291 | 0.03918 | 1.0675 | 1.0669 | 1.0669 | 1.0669 | 0.038569 | 7.3143 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0979 | 0.03519 | 1.0594 | 1.0592 | 1.0592 | 1.0592 | 0.92847 | 0.035553 | 7.1185 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0979 | 0.03519 | 1.0592 | 1.0592 | 1.0592 | 1.0592 | 0.92847 | 0.035553 | 7.1185 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0979 | 0.03519 | 1.0592 | 1.0592 | 1.0592 | 1.0592 | 0.92847 | 0.035553 | 102 | 35.5529 | 0.92847 | 1.0592 | 0.0041 | 7.1185
0.103 | 0.13015 | 0.039315 | 1.0678 | 1.0672 | 1.0671 | 1.0671 | 0.039147 | 7.3507 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0989 | 0.03534 | 1.0596 | 1.0595 | 1.0595 | 1.0595 | 0.92904 | 0.036109 | 7.1554 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0989 | 0.03534 | 1.0595 | 1.0595 | 1.0595 | 1.0595 | 0.92904 | 0.036109 | 7.1554 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0989 | 0.03534 | 1.0595 | 1.0595 | 1.0595 | 1.0595 | 0.92904 | 0.036109 | 103 | 36.1087 | 0.92904 | 1.0595 | 0.0041 | 7.1554
0.104 | 0.13119 | 0.039449 | 1.068 | 1.0674 | 1.0674 | 1.0674 | 0.039729 | 7.3869 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0999 | 0.035488 | 1.0599 | 1.0598 | 1.0598 | 1.0598 | 0.92959 | 0.036667 | 7.1921 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0999 | 0.035488 | 1.0598 | 1.0598 | 1.0598 | 1.0598 | 0.92959 | 0.036667 | 7.1921 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.0999 | 0.035488 | 1.0598 | 1.0598 | 1.0598 | 1.0598 | 0.92959 | 0.036667 | 104 | 36.6675 | 0.92959 | 1.0598 | 0.0041 | 7.1921
0.105 | 0.13223 | 0.03958 | 1.0683 | 1.0677 | 1.0677 | 1.0677 | 0.040313 | 7.4229 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1009 | 0.035634 | 1.0602 | 1.0601 | 1.0601 | 1.0601 | 0.93014 | 0.037229 | 7.2286 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1009 | 0.035634 | 1.0601 | 1.0601 | 1.0601 | 1.0601 | 0.93014 | 0.037229 | 7.2286 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1009 | 0.035634 | 1.0601 | 1.0601 | 1.0601 | 1.0601 | 0.93014 | 0.037229 | 105 | 37.2292 | 0.93014 | 1.0601 | 0.0041 | 7.2286
0.106 | 0.13327 | 0.03971 | 1.0685 | 1.0679 | 1.0679 | 1.0679 | 0.0409 | 7.4588 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1019 | 0.035779 | 1.0605 | 1.0603 | 1.0603 | 1.0603 | 0.93067 | 0.037794 | 7.265 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1019 | 0.035779 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 0.93067 | 0.037794 | 7.265 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1019 | 0.035779 | 1.0603 | 1.0603 | 1.0603 | 1.0603 | 0.93067 | 0.037794 | 106 | 37.7938 | 0.93067 | 1.0603 | 0.0041 | 7.265
0.107 | 0.13431 | 0.039838 | 1.0688 | 1.0682 | 1.0682 | 1.0682 | 0.04149 | 7.4945 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1029 | 0.035921 | 1.0608 | 1.0606 | 1.0606 | 1.0606 | 0.9312 | 0.038361 | 7.3012 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1029 | 0.035921 | 1.0606 | 1.0606 | 1.0606 | 1.0606 | 0.9312 | 0.038361 | 7.3012 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1029 | 0.035921 | 1.0606 | 1.0606 | 1.0606 | 1.0606 | 0.9312 | 0.038361 | 107 | 38.3612 | 0.9312 | 1.0606 | 0.0041 | 7.3012
0.108 | 0.13535 | 0.039964 | 1.069 | 1.0684 | 1.0684 | 1.0684 | 0.042082 | 7.53 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1038 | 0.035969 | 1.0609 | 1.0607 | 1.0607 | 1.0607 | 0.93008 | 0.038857 | 7.3325 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1039 | 0.036061 | 1.0609 | 1.0609 | 1.0609 | 1.0609 | 0.93171 | 0.038932 | 7.3372 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1039 | 0.036061 | 1.0609 | 1.0609 | 1.0609 | 1.0609 | 0.93171 | 0.038932 | 108 | 38.9316 | 0.93171 | 1.0609 | 0.0041 | 7.3372
0.109 | 0.13639 | 0.040088 | 1.0693 | 1.0687 | 1.0687 | 1.0687 | 0.042678 | 7.5654 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1048 | 0.036108 | 1.0611 | 1.061 | 1.061 | 1.061 | 0.9306 | 0.03943 | 7.3683 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1049 | 0.0362 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 0.93222 | 0.039505 | 7.373 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1049 | 0.0362 | 1.0611 | 1.0611 | 1.0611 | 1.0611 | 0.93222 | 0.039505 | 109 | 39.5048 | 0.93222 | 1.0611 | 0.0041 | 7.373
0.11 | 0.13743 | 0.040211 | 1.0695 | 1.0689 | 1.0689 | 1.0689 | 0.043276 | 7.6006 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1058 | 0.036245 | 1.0614 | 1.0612 | 1.0612 | 1.0612 | 0.9311 | 0.040005 | 7.404 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1059 | 0.036336 | 1.0614 | 1.0614 | 1.0614 | 1.0614 | 0.93272 | 0.040081 | 7.4087 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1059 | 0.036336 | 1.0614 | 1.0614 | 1.0614 | 1.0614 | 0.93272 | 0.040081 | 110 | 40.0809 | 0.93272 | 1.0614 | 0.0041 | 7.4087
0.111 | 0.13848 | 0.040332 | 1.0697 | 1.0692 | 1.0691 | 1.0691 | 0.043878 | 7.6356 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1068 | 0.03638 | 1.0616 | 1.0615 | 1.0615 | 1.0615 | 0.9316 | 0.040584 | 7.4395 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1069 | 0.036471 | 1.0616 | 1.0617 | 1.0617 | 1.0617 | 0.9332 | 0.04066 | 7.4442 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1069 | 0.036471 | 1.0617 | 1.0617 | 1.0617 | 1.0617 | 0.9332 | 0.04066 | 111 | 40.6598 | 0.9332 | 1.0617 | 0.0041 | 7.4442
0.112 | 0.13952 | 0.040451 | 1.07 | 1.0694 | 1.0694 | 1.0694 | 0.044482 | 7.6705 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1078 | 0.036513 | 1.0619 | 1.0617 | 1.0617 | 1.0617 | 0.93209 | 0.041165 | 7.4749 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1079 | 0.036604 | 1.0619 | 1.0619 | 1.0619 | 1.0619 | 0.93368 | 0.041242 | 7.4795 | 0.0047 | 0.0038 | 0.0041 | 0.64272 | 0.1079 | 0.036604 | 1.0619 | 1.0619 | 1.0619 | 1.0619 | 0.93368 | 0.041242 | 112 | 41.2416 | 0.93368 | 1.0619 | 0.0041 | 7.4795
0.113 | 0.14056 | 0.040569 | 1.0702 | 1.0696 | 1.0696 | 1.0696 | 0.045088 | 7.7052 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1088 | 0.036645 | 1.0621 | 1.062 | 1.062 | 1.062 | 0.93258 | 0.041749 | 7.5101 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1088 | 0.036645 | 1.062 | 1.062 | 1.062 | 1.062 | 0.93258 | 0.041749 | 7.5101 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1088 | 0.036645 | 1.062 | 1.062 | 1.062 | 1.062 | 0.93258 | 0.041749 | 113 | 41.7488 | 0.93258 | 1.062 | 0.0042 | 7.5101
0.114 | 0.1416 | 0.040685 | 1.0704 | 1.0699 | 1.0698 | 1.0698 | 0.045698 | 7.7398 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1098 | 0.036775 | 1.0624 | 1.0622 | 1.0622 | 1.0622 | 0.93305 | 0.042336 | 7.5451 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1098 | 0.036775 | 1.0622 | 1.0622 | 1.0622 | 1.0622 | 0.93305 | 0.042336 | 7.5451 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1098 | 0.036775 | 1.0622 | 1.0622 | 1.0622 | 1.0622 | 0.93305 | 0.042336 | 114 | 42.3356 | 0.93305 | 1.0622 | 0.0042 | 7.5451
0.115 | 0.14264 | 0.0408 | 1.0707 | 1.0701 | 1.0701 | 1.0701 | 0.046311 | 7.7742 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1108 | 0.036903 | 1.0626 | 1.0625 | 1.0625 | 1.0625 | 0.93352 | 0.042925 | 7.5799 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1108 | 0.036903 | 1.0625 | 1.0625 | 1.0625 | 1.0625 | 0.93352 | 0.042925 | 7.5799 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1108 | 0.036903 | 1.0625 | 1.0625 | 1.0625 | 1.0625 | 0.93352 | 0.042925 | 115 | 42.9252 | 0.93352 | 1.0625 | 0.0042 | 7.5799
0.116 | 0.14368 | 0.040913 | 1.0709 | 1.0703 | 1.0703 | 1.0703 | 0.046926 | 7.8085 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1118 | 0.03703 | 1.0629 | 1.0627 | 1.0627 | 1.0627 | 0.93397 | 0.043518 | 7.6147 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1118 | 0.03703 | 1.0627 | 1.0627 | 1.0627 | 1.0627 | 0.93397 | 0.043518 | 7.6147 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1118 | 0.03703 | 1.0627 | 1.0627 | 1.0627 | 1.0627 | 0.93397 | 0.043518 | 116 | 43.5175 | 0.93397 | 1.0627 | 0.0042 | 7.6147
0.117 | 0.14472 | 0.041025 | 1.0711 | 1.0705 | 1.0705 | 1.0705 | 0.047544 | 7.8426 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1128 | 0.037155 | 1.0631 | 1.063 | 1.063 | 1.063 | 0.93442 | 0.044113 | 7.6492 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1128 | 0.037155 | 1.063 | 1.063 | 1.063 | 1.063 | 0.93442 | 0.044113 | 7.6492 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1128 | 0.037155 | 1.063 | 1.063 | 1.063 | 1.063 | 0.93442 | 0.044113 | 117 | 44.1127 | 0.93442 | 1.063 | 0.0042 | 7.6492
0.118 | 0.14576 | 0.041135 | 1.0713 | 1.0707 | 1.0707 | 1.0707 | 0.048164 | 7.8766 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1138 | 0.037278 | 1.0634 | 1.0632 | 1.0632 | 1.0632 | 0.93487 | 0.044711 | 7.6836 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1138 | 0.037278 | 1.0632 | 1.0632 | 1.0632 | 1.0632 | 0.93487 | 0.044711 | 7.6836 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1138 | 0.037278 | 1.0632 | 1.0632 | 1.0632 | 1.0632 | 0.93487 | 0.044711 | 118 | 44.7106 | 0.93487 | 1.0632 | 0.0042 | 7.6836
0.119 | 0.1468 | 0.041244 | 1.0715 | 1.071 | 1.0709 | 1.0709 | 0.048788 | 7.9104 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1148 | 0.0374 | 1.0636 | 1.0634 | 1.0634 | 1.0634 | 0.9353 | 0.045311 | 7.7179 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1148 | 0.0374 | 1.0634 | 1.0634 | 1.0634 | 1.0634 | 0.9353 | 0.045311 | 7.7179 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1148 | 0.0374 | 1.0634 | 1.0634 | 1.0634 | 1.0634 | 0.9353 | 0.045311 | 119 | 45.3112 | 0.9353 | 1.0634 | 0.0042 | 7.7179
0.12 | 0.14785 | 0.041352 | 1.0718 | 1.0712 | 1.0712 | 1.0712 | 0.049414 | 7.9441 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1158 | 0.03752 | 1.0638 | 1.0637 | 1.0637 | 1.0637 | 0.93573 | 0.045915 | 7.752 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1158 | 0.03752 | 1.0637 | 1.0637 | 1.0637 | 1.0637 | 0.93573 | 0.045915 | 7.752 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1158 | 0.03752 | 1.0637 | 1.0637 | 1.0637 | 1.0637 | 0.93573 | 0.045915 | 120 | 45.9145 | 0.93573 | 1.0637 | 0.0042 | 7.752
0.121 | 0.14889 | 0.041458 | 1.072 | 1.0714 | 1.0714 | 1.0714 | 0.050043 | 7.9777 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1168 | 0.037639 | 1.0641 | 1.0639 | 1.0639 | 1.0639 | 0.93615 | 0.046521 | 7.7859 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1168 | 0.037639 | 1.0639 | 1.0639 | 1.0639 | 1.0639 | 0.93615 | 0.046521 | 7.7859 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1168 | 0.037639 | 1.0639 | 1.0639 | 1.0639 | 1.0639 | 0.93615 | 0.046521 | 121 | 46.5206 | 0.93615 | 1.0639 | 0.0042 | 7.7859
0.122 | 0.14993 | 0.041562 | 1.0722 | 1.0716 | 1.0716 | 1.0716 | 0.050674 | 8.0111 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1177 | 0.037669 | 1.0641 | 1.064 | 1.064 | 1.064 | 0.93508 | 0.047047 | 7.8152 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1178 | 0.037756 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 0.93656 | 0.047129 | 7.8197 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1178 | 0.037756 | 1.0641 | 1.0641 | 1.0641 | 1.0641 | 0.93656 | 0.047129 | 122 | 47.1293 | 0.93656 | 1.0641 | 0.0042 | 7.8197
0.123 | 0.15097 | 0.041666 | 1.0724 | 1.0718 | 1.0718 | 1.0718 | 0.051308 | 8.0444 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1187 | 0.037785 | 1.0643 | 1.0642 | 1.0642 | 1.0642 | 0.9355 | 0.047658 | 7.8489 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1188 | 0.037872 | 1.0643 | 1.0643 | 1.0643 | 1.0643 | 0.93697 | 0.047741 | 7.8534 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1188 | 0.037872 | 1.0643 | 1.0643 | 1.0643 | 1.0643 | 0.93697 | 0.047741 | 123 | 47.7407 | 0.93697 | 1.0643 | 0.0042 | 7.8534
0.124 | 0.15201 | 0.041768 | 1.0726 | 1.072 | 1.072 | 1.072 | 0.051945 | 8.0775 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1197 | 0.0379 | 1.0646 | 1.0644 | 1.0644 | 1.0644 | 0.93591 | 0.048272 | 7.8824 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1198 | 0.037987 | 1.0646 | 1.0646 | 1.0646 | 1.0646 | 0.93737 | 0.048355 | 7.8869 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1198 | 0.037987 | 1.0646 | 1.0646 | 1.0646 | 1.0646 | 0.93737 | 0.048355 | 124 | 48.3548 | 0.93737 | 1.0646 | 0.0042 | 7.8869
0.125 | 0.15305 | 0.041869 | 1.0728 | 1.0722 | 1.0722 | 1.0722 | 0.052584 | 8.1105 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1207 | 0.038013 | 1.0648 | 1.0646 | 1.0646 | 1.0646 | 0.93631 | 0.048888 | 7.9158 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1208 | 0.0381 | 1.0648 | 1.0648 | 1.0648 | 1.0648 | 0.93777 | 0.048972 | 7.9203 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1208 | 0.0381 | 1.0648 | 1.0648 | 1.0648 | 1.0648 | 0.93777 | 0.048972 | 125 | 48.9716 | 0.93777 | 1.0648 | 0.0042 | 7.9203
0.126 | 0.15409 | 0.041969 | 1.073 | 1.0724 | 1.0724 | 1.0724 | 0.053227 | 8.1434 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1217 | 0.038125 | 1.065 | 1.0648 | 1.0648 | 1.0648 | 0.93671 | 0.049507 | 7.9491 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1218 | 0.038212 | 1.065 | 1.065 | 1.065 | 1.065 | 0.93815 | 0.049591 | 7.9536 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1218 | 0.038212 | 1.065 | 1.065 | 1.065 | 1.065 | 0.93815 | 0.049591 | 126 | 49.591 | 0.93815 | 1.065 | 0.0042 | 7.9536
0.127 | 0.15513 | 0.042067 | 1.0732 | 1.0726 | 1.0726 | 1.0726 | 0.053871 | 8.1761 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1227 | 0.038236 | 1.0652 | 1.0651 | 1.065 | 1.065 | 0.9371 | 0.050128 | 7.9822 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1228 | 0.038322 | 1.0652 | 1.0652 | 1.0652 | 1.0652 | 0.93854 | 0.050213 | 7.9867 | 0.0048 | 0.0039 | 0.0042 | 0.64252 | 0.1228 | 0.038322 | 1.0652 | 1.0652 | 1.0652 | 1.0652 | 0.93854 | 0.050213 | 127 | 50.2131 | 0.93854 | 1.0652 | 0.0042 | 7.9867
0.128 | 0.15618 | 0.042164 | 1.0734 | 1.0728 | 1.0728 | 1.0728 | 0.054519 | 8.2088 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1237 | 0.038345 | 1.0654 | 1.0653 | 1.0653 | 1.0653 | 0.93748 | 0.050752 | 8.0152 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1237 | 0.038345 | 1.0653 | 1.0653 | 1.0653 | 1.0653 | 0.93748 | 0.050752 | 8.0152 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1237 | 0.038345 | 1.0653 | 1.0653 | 1.0653 | 1.0653 | 0.93748 | 0.050752 | 128 | 50.7525 | 0.93748 | 1.0653 | 0.0043 | 8.0152
0.129 | 0.15722 | 0.04226 | 1.0735 | 1.073 | 1.073 | 1.073 | 0.055169 | 8.2413 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1247 | 0.038453 | 1.0656 | 1.0655 | 1.0655 | 1.0655 | 0.93786 | 0.051379 | 8.0481 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1247 | 0.038453 | 1.0655 | 1.0655 | 1.0655 | 1.0655 | 0.93786 | 0.051379 | 8.0481 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1247 | 0.038453 | 1.0655 | 1.0655 | 1.0655 | 1.0655 | 0.93786 | 0.051379 | 129 | 51.3792 | 0.93786 | 1.0655 | 0.0043 | 8.0481
0.13 | 0.15826 | 0.042355 | 1.0737 | 1.0732 | 1.0732 | 1.0732 | 0.055821 | 8.2736 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1257 | 0.03856 | 1.0658 | 1.0657 | 1.0657 | 1.0657 | 0.93824 | 0.052009 | 8.0808 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1257 | 0.03856 | 1.0657 | 1.0657 | 1.0657 | 1.0657 | 0.93824 | 0.052009 | 8.0808 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1257 | 0.03856 | 1.0657 | 1.0657 | 1.0657 | 1.0657 | 0.93824 | 0.052009 | 130 | 52.0086 | 0.93824 | 1.0657 | 0.0043 | 8.0808
0.131 | 0.1593 | 0.042449 | 1.0739 | 1.0734 | 1.0733 | 1.0733 | 0.056477 | 8.3059 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1267 | 0.038666 | 1.066 | 1.0659 | 1.0659 | 1.0659 | 0.9386 | 0.052641 | 8.1134 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1267 | 0.038666 | 1.0659 | 1.0659 | 1.0659 | 1.0659 | 0.9386 | 0.052641 | 8.1134 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1267 | 0.038666 | 1.0659 | 1.0659 | 1.0659 | 1.0659 | 0.9386 | 0.052641 | 131 | 52.6406 | 0.9386 | 1.0659 | 0.0043 | 8.1134
0.132 | 0.16034 | 0.042542 | 1.0741 | 1.0735 | 1.0735 | 1.0735 | 0.057134 | 8.338 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1277 | 0.03877 | 1.0663 | 1.0661 | 1.0661 | 1.0661 | 0.93896 | 0.053275 | 8.1459 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1277 | 0.03877 | 1.0661 | 1.0661 | 1.0661 | 1.0661 | 0.93896 | 0.053275 | 8.1459 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1277 | 0.03877 | 1.0661 | 1.0661 | 1.0661 | 1.0661 | 0.93896 | 0.053275 | 132 | 53.2752 | 0.93896 | 1.0661 | 0.0043 | 8.1459
0.133 | 0.16138 | 0.042633 | 1.0743 | 1.0737 | 1.0737 | 1.0737 | 0.057795 | 8.37 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1287 | 0.038873 | 1.0665 | 1.0663 | 1.0663 | 1.0663 | 0.93932 | 0.053912 | 8.1782 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1287 | 0.038873 | 1.0663 | 1.0663 | 1.0663 | 1.0663 | 0.93932 | 0.053912 | 8.1782 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1287 | 0.038873 | 1.0663 | 1.0663 | 1.0663 | 1.0663 | 0.93932 | 0.053912 | 133 | 53.9123 | 0.93932 | 1.0663 | 0.0043 | 8.1782
0.134 | 0.16242 | 0.042724 | 1.0745 | 1.0739 | 1.0739 | 1.0739 | 0.058458 | 8.4019 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1297 | 0.038975 | 1.0667 | 1.0665 | 1.0665 | 1.0665 | 0.93967 | 0.054552 | 8.2104 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1297 | 0.038975 | 1.0665 | 1.0665 | 1.0665 | 1.0665 | 0.93967 | 0.054552 | 8.2104 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1297 | 0.038975 | 1.0665 | 1.0665 | 1.0665 | 1.0665 | 0.93967 | 0.054552 | 134 | 54.5521 | 0.93967 | 1.0665 | 0.0043 | 8.2104
0.135 | 0.16346 | 0.042813 | 1.0746 | 1.0741 | 1.0741 | 1.0741 | 0.059123 | 8.4336 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1307 | 0.039076 | 1.0668 | 1.0667 | 1.0667 | 1.0667 | 0.94002 | 0.055194 | 8.2425 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1307 | 0.039076 | 1.0667 | 1.0667 | 1.0667 | 1.0667 | 0.94002 | 0.055194 | 8.2425 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1307 | 0.039076 | 1.0667 | 1.0667 | 1.0667 | 1.0667 | 0.94002 | 0.055194 | 135 | 55.1943 | 0.94002 | 1.0667 | 0.0043 | 8.2425
0.136 | 0.1645 | 0.042901 | 1.0748 | 1.0743 | 1.0742 | 1.0742 | 0.059791 | 8.4653 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1317 | 0.039175 | 1.067 | 1.0669 | 1.0669 | 1.0669 | 0.94036 | 0.055839 | 8.2745 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1317 | 0.039175 | 1.0669 | 1.0669 | 1.0669 | 1.0669 | 0.94036 | 0.055839 | 8.2745 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1317 | 0.039175 | 1.0669 | 1.0669 | 1.0669 | 1.0669 | 0.94036 | 0.055839 | 136 | 55.8392 | 0.94036 | 1.0669 | 0.0043 | 8.2745
0.137 | 0.16555 | 0.042989 | 1.075 | 1.0744 | 1.0744 | 1.0744 | 0.060462 | 8.4968 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1327 | 0.039274 | 1.0672 | 1.0671 | 1.0671 | 1.0671 | 0.9407 | 0.056487 | 8.3064 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1327 | 0.039274 | 1.0671 | 1.0671 | 1.0671 | 1.0671 | 0.9407 | 0.056487 | 8.3064 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1327 | 0.039274 | 1.0671 | 1.0671 | 1.0671 | 1.0671 | 0.9407 | 0.056487 | 137 | 56.4865 | 0.9407 | 1.0671 | 0.0043 | 8.3064
0.138 | 0.16659 | 0.043075 | 1.0752 | 1.0746 | 1.0746 | 1.0746 | 0.061135 | 8.5282 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1335 | 0.039204 | 1.0671 | 1.0669 | 1.0669 | 1.0669 | 0.93833 | 0.056955 | 8.3293 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1337 | 0.039371 | 1.0672 | 1.0673 | 1.0673 | 1.0673 | 0.94103 | 0.057136 | 8.3381 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1337 | 0.039371 | 1.0673 | 1.0673 | 1.0673 | 1.0673 | 0.94103 | 0.057136 | 138 | 57.1364 | 0.94103 | 1.0673 | 0.0043 | 8.3381
0.139 | 0.16763 | 0.04316 | 1.0753 | 1.0748 | 1.0748 | 1.0748 | 0.06181 | 8.5595 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1345 | 0.039301 | 1.0673 | 1.0671 | 1.0671 | 1.0671 | 0.93867 | 0.057607 | 8.3609 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1347 | 0.039467 | 1.0674 | 1.0674 | 1.0674 | 1.0674 | 0.94135 | 0.057789 | 8.3697 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1347 | 0.039467 | 1.0674 | 1.0674 | 1.0674 | 1.0674 | 0.94135 | 0.057789 | 139 | 57.7888 | 0.94135 | 1.0674 | 0.0043 | 8.3697
0.14 | 0.16867 | 0.043245 | 1.0755 | 1.075 | 1.0749 | 1.0749 | 0.062488 | 8.5907 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1355 | 0.039397 | 1.0675 | 1.0673 | 1.0673 | 1.0673 | 0.93901 | 0.058261 | 8.3924 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1357 | 0.039563 | 1.0676 | 1.0676 | 1.0676 | 1.0676 | 0.94168 | 0.058444 | 8.4012 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1357 | 0.039563 | 1.0676 | 1.0676 | 1.0676 | 1.0676 | 0.94168 | 0.058444 | 140 | 58.4437 | 0.94168 | 1.0676 | 0.0043 | 8.4012
0.141 | 0.16971 | 0.043328 | 1.0757 | 1.0751 | 1.0751 | 1.0751 | 0.063169 | 8.6218 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1365 | 0.039491 | 1.0677 | 1.0675 | 1.0675 | 1.0675 | 0.93934 | 0.058917 | 8.4238 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1367 | 0.039657 | 1.0678 | 1.0678 | 1.0678 | 1.0678 | 0.94199 | 0.059101 | 8.4326 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1367 | 0.039657 | 1.0678 | 1.0678 | 1.0678 | 1.0678 | 0.94199 | 0.059101 | 141 | 59.1011 | 0.94199 | 1.0678 | 0.0043 | 8.4326
0.142 | 0.17075 | 0.043411 | 1.0758 | 1.0753 | 1.0753 | 1.0753 | 0.063852 | 8.6527 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1375 | 0.039585 | 1.0678 | 1.0677 | 1.0677 | 1.0677 | 0.93967 | 0.059576 | 8.4551 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1377 | 0.03975 | 1.068 | 1.068 | 1.068 | 1.068 | 0.94231 | 0.059761 | 8.4639 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1377 | 0.03975 | 1.068 | 1.068 | 1.068 | 1.068 | 0.94231 | 0.059761 | 142 | 59.761 | 0.94231 | 1.068 | 0.0043 | 8.4639
0.143 | 0.17179 | 0.043492 | 1.076 | 1.0755 | 1.0754 | 1.0754 | 0.064538 | 8.6836 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1385 | 0.039678 | 1.068 | 1.0679 | 1.0679 | 1.0679 | 0.93999 | 0.060237 | 8.4863 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1387 | 0.039842 | 1.0682 | 1.0682 | 1.0682 | 1.0682 | 0.94262 | 0.060423 | 8.495 | 0.0049 | 0.004 | 0.0043 | 0.64232 | 0.1387 | 0.039842 | 1.0682 | 1.0682 | 1.0682 | 1.0682 | 0.94262 | 0.060423 | 143 | 60.4234 | 0.94262 | 1.0682 | 0.0043 | 8.495
0.144 | 0.17283 | 0.043573 | 1.0762 | 1.0756 | 1.0756 | 1.0756 | 0.065226 | 8.7143 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1395 | 0.039769 | 1.0682 | 1.068 | 1.068 | 1.068 | 0.94031 | 0.060901 | 8.5173 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1395 | 0.039769 | 1.068 | 1.068 | 1.068 | 1.068 | 0.94031 | 0.060901 | 8.5173 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1395 | 0.039769 | 1.068 | 1.068 | 1.068 | 1.068 | 0.94031 | 0.060901 | 144 | 60.9009 | 0.94031 | 1.068 | 0.0045 | 8.5173
0.145 | 0.17387 | 0.043653 | 1.0763 | 1.0758 | 1.0758 | 1.0758 | 0.065916 | 8.745 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1405 | 0.03986 | 1.0684 | 1.0682 | 1.0682 | 1.0682 | 0.94062 | 0.061567 | 8.5483 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1405 | 0.03986 | 1.0682 | 1.0682 | 1.0682 | 1.0682 | 0.94062 | 0.061567 | 8.5483 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1405 | 0.03986 | 1.0682 | 1.0682 | 1.0682 | 1.0682 | 0.94062 | 0.061567 | 145 | 61.5671 | 0.94062 | 1.0682 | 0.0045 | 8.5483
0.146 | 0.17492 | 0.043731 | 1.0765 | 1.0759 | 1.0759 | 1.0759 | 0.066609 | 8.7755 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1415 | 0.039949 | 1.0686 | 1.0684 | 1.0684 | 1.0684 | 0.94093 | 0.062236 | 8.5791 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1415 | 0.039949 | 1.0684 | 1.0684 | 1.0684 | 1.0684 | 0.94093 | 0.062236 | 8.5791 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1415 | 0.039949 | 1.0684 | 1.0684 | 1.0684 | 1.0684 | 0.94093 | 0.062236 | 146 | 62.2358 | 0.94093 | 1.0684 | 0.0045 | 8.5791
0.147 | 0.17596 | 0.043809 | 1.0766 | 1.0761 | 1.0761 | 1.0761 | 0.067304 | 8.806 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1425 | 0.040038 | 1.0687 | 1.0686 | 1.0686 | 1.0686 | 0.94124 | 0.062907 | 8.6098 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1425 | 0.040038 | 1.0686 | 1.0686 | 1.0686 | 1.0686 | 0.94124 | 0.062907 | 8.6098 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1425 | 0.040038 | 1.0686 | 1.0686 | 1.0686 | 1.0686 | 0.94124 | 0.062907 | 147 | 62.907 | 0.94124 | 1.0686 | 0.0045 | 8.6098
0.148 | 0.177 | 0.043887 | 1.0768 | 1.0762 | 1.0762 | 1.0762 | 0.068002 | 8.8363 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1435 | 0.040125 | 1.0689 | 1.0687 | 1.0687 | 1.0687 | 0.94154 | 0.063581 | 8.6405 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1435 | 0.040125 | 1.0687 | 1.0687 | 1.0687 | 1.0687 | 0.94154 | 0.063581 | 8.6405 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1435 | 0.040125 | 1.0687 | 1.0687 | 1.0687 | 1.0687 | 0.94154 | 0.063581 | 148 | 63.5805 | 0.94154 | 1.0687 | 0.0045 | 8.6405
0.149 | 0.17804 | 0.043963 | 1.0769 | 1.0764 | 1.0764 | 1.0764 | 0.068702 | 8.8665 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1445 | 0.040212 | 1.0691 | 1.0689 | 1.0689 | 1.0689 | 0.94184 | 0.064257 | 8.671 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1445 | 0.040212 | 1.0689 | 1.0689 | 1.0689 | 1.0689 | 0.94184 | 0.064257 | 8.671 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1445 | 0.040212 | 1.0689 | 1.0689 | 1.0689 | 1.0689 | 0.94184 | 0.064257 | 149 | 64.2565 | 0.94184 | 1.0689 | 0.0045 | 8.671
0.15 | 0.17908 | 0.044038 | 1.0771 | 1.0766 | 1.0765 | 1.0765 | 0.069405 | 8.8966 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1455 | 0.040298 | 1.0692 | 1.0691 | 1.0691 | 1.0691 | 0.94213 | 0.064935 | 8.7014 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1455 | 0.040298 | 1.0691 | 1.0691 | 1.0691 | 1.0691 | 0.94213 | 0.064935 | 8.7014 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1455 | 0.040298 | 1.0691 | 1.0691 | 1.0691 | 1.0691 | 0.94213 | 0.064935 | 150 | 64.935 | 0.94213 | 1.0691 | 0.0045 | 8.7014
0.151 | 0.18012 | 0.044113 | 1.0772 | 1.0767 | 1.0767 | 1.0767 | 0.07011 | 8.9267 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1465 | 0.040383 | 1.0694 | 1.0692 | 1.0692 | 1.0692 | 0.94242 | 0.065616 | 8.7317 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1465 | 0.040383 | 1.0692 | 1.0692 | 1.0692 | 1.0692 | 0.94242 | 0.065616 | 8.7317 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1465 | 0.040383 | 1.0692 | 1.0692 | 1.0692 | 1.0692 | 0.94242 | 0.065616 | 151 | 65.6158 | 0.94242 | 1.0692 | 0.0045 | 8.7317
0.152 | 0.18116 | 0.044187 | 1.0774 | 1.0769 | 1.0768 | 1.0768 | 0.070817 | 8.9566 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1475 | 0.040467 | 1.0696 | 1.0694 | 1.0694 | 1.0694 | 0.94271 | 0.066299 | 8.7619 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1475 | 0.040467 | 1.0694 | 1.0694 | 1.0694 | 1.0694 | 0.94271 | 0.066299 | 8.7619 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1475 | 0.040467 | 1.0694 | 1.0694 | 1.0694 | 1.0694 | 0.94271 | 0.066299 | 152 | 66.299 | 0.94271 | 1.0694 | 0.0045 | 8.7619
0.153 | 0.1822 | 0.04426 | 1.0775 | 1.077 | 1.077 | 1.077 | 0.071527 | 8.9864 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1485 | 0.04055 | 1.0697 | 1.0696 | 1.0696 | 1.0696 | 0.94299 | 0.066985 | 8.792 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1485 | 0.04055 | 1.0696 | 1.0696 | 1.0696 | 1.0696 | 0.94299 | 0.066985 | 8.792 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1485 | 0.04055 | 1.0696 | 1.0696 | 1.0696 | 1.0696 | 0.94299 | 0.066985 | 153 | 66.9847 | 0.94299 | 1.0696 | 0.0045 | 8.792
0.154 | 0.18325 | 0.044333 | 1.0777 | 1.0772 | 1.0771 | 1.0771 | 0.07224 | 9.0161 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1494 | 0.040553 | 1.0698 | 1.0696 | 1.0696 | 1.0696 | 0.94203 | 0.067574 | 8.8177 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1495 | 0.040632 | 1.0697 | 1.0697 | 1.0697 | 1.0697 | 0.94327 | 0.067673 | 8.822 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1495 | 0.040632 | 1.0697 | 1.0697 | 1.0697 | 1.0697 | 0.94327 | 0.067673 | 154 | 67.6727 | 0.94327 | 1.0697 | 0.0045 | 8.822
0.155 | 0.18429 | 0.044404 | 1.0778 | 1.0773 | 1.0773 | 1.0773 | 0.072954 | 9.0458 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1504 | 0.040634 | 1.0699 | 1.0697 | 1.0697 | 1.0697 | 0.94231 | 0.068264 | 8.8476 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1505 | 0.040714 | 1.0699 | 1.0699 | 1.0699 | 1.0699 | 0.94354 | 0.068363 | 8.8519 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1505 | 0.040714 | 1.0699 | 1.0699 | 1.0699 | 1.0699 | 0.94354 | 0.068363 | 155 | 68.3631 | 0.94354 | 1.0699 | 0.0045 | 8.8519
0.156 | 0.18533 | 0.044475 | 1.078 | 1.0774 | 1.0774 | 1.0774 | 0.073671 | 9.0753 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1514 | 0.040715 | 1.0701 | 1.0699 | 1.0699 | 1.0699 | 0.94258 | 0.068956 | 8.8774 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1515 | 0.040794 | 1.07 | 1.0701 | 1.0701 | 1.0701 | 0.94381 | 0.069056 | 8.8817 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1515 | 0.040794 | 1.0701 | 1.0701 | 1.0701 | 1.0701 | 0.94381 | 0.069056 | 156 | 69.0558 | 0.94381 | 1.0701 | 0.0045 | 8.8817
0.157 | 0.18637 | 0.044545 | 1.0781 | 1.0776 | 1.0776 | 1.0776 | 0.074391 | 9.1048 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1524 | 0.040795 | 1.0702 | 1.0701 | 1.0701 | 1.0701 | 0.94286 | 0.06965 | 8.9071 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1525 | 0.040874 | 1.0702 | 1.0702 | 1.0702 | 1.0702 | 0.94408 | 0.069751 | 8.9114 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1525 | 0.040874 | 1.0702 | 1.0702 | 1.0702 | 1.0702 | 0.94408 | 0.069751 | 157 | 69.751 | 0.94408 | 1.0702 | 0.0045 | 8.9114
0.158 | 0.18741 | 0.044614 | 1.0783 | 1.0777 | 1.0777 | 1.0777 | 0.075112 | 9.1341 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1534 | 0.040874 | 1.0704 | 1.0702 | 1.0702 | 1.0702 | 0.94313 | 0.070347 | 8.9367 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1535 | 0.040953 | 1.0704 | 1.0704 | 1.0704 | 1.0704 | 0.94434 | 0.070448 | 8.941 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1535 | 0.040953 | 1.0704 | 1.0704 | 1.0704 | 1.0704 | 0.94434 | 0.070448 | 158 | 70.4484 | 0.94434 | 1.0704 | 0.0045 | 8.941
0.159 | 0.18845 | 0.044683 | 1.0784 | 1.0779 | 1.0779 | 1.0779 | 0.075836 | 9.1634 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1544 | 0.040952 | 1.0705 | 1.0704 | 1.0704 | 1.0704 | 0.94339 | 0.071047 | 8.9662 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1545 | 0.041031 | 1.0705 | 1.0705 | 1.0705 | 1.0705 | 0.94461 | 0.071148 | 8.9705 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1545 | 0.041031 | 1.0705 | 1.0705 | 1.0705 | 1.0705 | 0.94461 | 0.071148 | 159 | 71.1482 | 0.94461 | 1.0705 | 0.0045 | 8.9705
0.16 | 0.18949 | 0.044751 | 1.0785 | 1.078 | 1.078 | 1.078 | 0.076563 | 9.1925 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1554 | 0.04103 | 1.0707 | 1.0705 | 1.0705 | 1.0705 | 0.94366 | 0.071748 | 8.9957 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1555 | 0.041108 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 0.94486 | 0.07185 | 8.9999 | 0.0051 | 0.0042 | 0.0045 | 0.64192 | 0.1555 | 0.041108 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 0.94486 | 0.07185 | 160 | 71.8504 | 0.94486 | 1.0707 | 0.0045 | 8.9999
0.161 | 0.19053 | 0.044818 | 1.0787 | 1.0781 | 1.0781 | 1.0781 | 0.077291 | 9.2216 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1564 | 0.041107 | 1.0708 | 1.0707 | 1.0707 | 1.0707 | 0.94392 | 0.072452 | 9.025 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1564 | 0.041107 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 0.94392 | 0.072452 | 9.025 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1564 | 0.041107 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 0.94392 | 0.072452 | 161 | 72.4523 | 0.94392 | 1.0707 | 0.0046 | 9.025
0.162 | 0.19157 | 0.044885 | 1.0788 | 1.0783 | 1.0783 | 1.0783 | 0.078022 | 9.2506 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1574 | 0.041183 | 1.071 | 1.0708 | 1.0708 | 1.0708 | 0.94418 | 0.073159 | 9.0542 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1574 | 0.041183 | 1.0708 | 1.0708 | 1.0708 | 1.0708 | 0.94418 | 0.073159 | 9.0542 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1574 | 0.041183 | 1.0708 | 1.0708 | 1.0708 | 1.0708 | 0.94418 | 0.073159 | 162 | 73.1586 | 0.94418 | 1.0708 | 0.0046 | 9.0542
0.163 | 0.19262 | 0.044951 | 1.0789 | 1.0784 | 1.0784 | 1.0784 | 0.078756 | 9.2795 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1584 | 0.041258 | 1.0711 | 1.071 | 1.071 | 1.071 | 0.94443 | 0.073867 | 9.0833 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1584 | 0.041258 | 1.071 | 1.071 | 1.071 | 1.071 | 0.94443 | 0.073867 | 9.0833 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1584 | 0.041258 | 1.071 | 1.071 | 1.071 | 1.071 | 0.94443 | 0.073867 | 163 | 73.8671 | 0.94443 | 1.071 | 0.0046 | 9.0833
0.164 | 0.19366 | 0.045016 | 1.0791 | 1.0785 | 1.0785 | 1.0785 | 0.079491 | 9.3083 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1594 | 0.041333 | 1.0713 | 1.0711 | 1.0711 | 1.0711 | 0.94468 | 0.074578 | 9.1124 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1594 | 0.041333 | 1.0711 | 1.0711 | 1.0711 | 1.0711 | 0.94468 | 0.074578 | 9.1124 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1594 | 0.041333 | 1.0711 | 1.0711 | 1.0711 | 1.0711 | 0.94468 | 0.074578 | 164 | 74.578 | 0.94468 | 1.0711 | 0.0046 | 9.1124
0.165 | 0.1947 | 0.045081 | 1.0792 | 1.0787 | 1.0787 | 1.0787 | 0.080229 | 9.337 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1604 | 0.041406 | 1.0714 | 1.0713 | 1.0713 | 1.0713 | 0.94493 | 0.075291 | 9.1414 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1604 | 0.041406 | 1.0713 | 1.0713 | 1.0713 | 1.0713 | 0.94493 | 0.075291 | 9.1414 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1604 | 0.041406 | 1.0713 | 1.0713 | 1.0713 | 1.0713 | 0.94493 | 0.075291 | 165 | 75.2912 | 0.94493 | 1.0713 | 0.0046 | 9.1414
0.166 | 0.19574 | 0.045145 | 1.0793 | 1.0788 | 1.0788 | 1.0788 | 0.08097 | 9.3656 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1614 | 0.04148 | 1.0716 | 1.0714 | 1.0714 | 1.0714 | 0.94517 | 0.076007 | 9.1702 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1614 | 0.04148 | 1.0714 | 1.0714 | 1.0714 | 1.0714 | 0.94517 | 0.076007 | 9.1702 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1614 | 0.04148 | 1.0714 | 1.0714 | 1.0714 | 1.0714 | 0.94517 | 0.076007 | 166 | 76.0067 | 0.94517 | 1.0714 | 0.0046 | 9.1702
0.167 | 0.19678 | 0.045208 | 1.0794 | 1.0789 | 1.0789 | 1.0789 | 0.081712 | 9.3942 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1624 | 0.041552 | 1.0717 | 1.0716 | 1.0716 | 1.0716 | 0.94541 | 0.076724 | 9.199 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1624 | 0.041552 | 1.0716 | 1.0716 | 1.0716 | 1.0716 | 0.94541 | 0.076724 | 9.199 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1624 | 0.041552 | 1.0716 | 1.0716 | 1.0716 | 1.0716 | 0.94541 | 0.076724 | 167 | 76.7245 | 0.94541 | 1.0716 | 0.0046 | 9.199
0.168 | 0.19782 | 0.045271 | 1.0796 | 1.0791 | 1.079 | 1.079 | 0.082457 | 9.4226 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1634 | 0.041624 | 1.0719 | 1.0717 | 1.0717 | 1.0717 | 0.94565 | 0.077445 | 9.2277 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1634 | 0.041624 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 0.94565 | 0.077445 | 9.2277 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1634 | 0.041624 | 1.0717 | 1.0717 | 1.0717 | 1.0717 | 0.94565 | 0.077445 | 168 | 77.4445 | 0.94565 | 1.0717 | 0.0046 | 9.2277
0.169 | 0.19886 | 0.045333 | 1.0797 | 1.0792 | 1.0792 | 1.0792 | 0.083204 | 9.451 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1644 | 0.041695 | 1.072 | 1.0718 | 1.0718 | 1.0718 | 0.94589 | 0.078167 | 9.2563 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1644 | 0.041695 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 0.94589 | 0.078167 | 9.2563 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1644 | 0.041695 | 1.0718 | 1.0718 | 1.0718 | 1.0718 | 0.94589 | 0.078167 | 169 | 78.1668 | 0.94589 | 1.0718 | 0.0046 | 9.2563
0.17 | 0.1999 | 0.045394 | 1.0798 | 1.0793 | 1.0793 | 1.0793 | 0.083954 | 9.4793 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1654 | 0.041765 | 1.0722 | 1.072 | 1.072 | 1.072 | 0.94612 | 0.078891 | 9.2848 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1654 | 0.041765 | 1.072 | 1.072 | 1.072 | 1.072 | 0.94612 | 0.078891 | 9.2848 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1654 | 0.041765 | 1.072 | 1.072 | 1.072 | 1.072 | 0.94612 | 0.078891 | 170 | 78.8914 | 0.94612 | 1.072 | 0.0046 | 9.2848
0.171 | 0.20095 | 0.045455 | 1.0799 | 1.0794 | 1.0794 | 1.0794 | 0.084705 | 9.5075 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1664 | 0.041834 | 1.0723 | 1.0721 | 1.0721 | 1.0721 | 0.94635 | 0.079618 | 9.3132 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1664 | 0.041834 | 1.0721 | 1.0721 | 1.0721 | 1.0721 | 0.94635 | 0.079618 | 9.3132 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1664 | 0.041834 | 1.0721 | 1.0721 | 1.0721 | 1.0721 | 0.94635 | 0.079618 | 171 | 79.6182 | 0.94635 | 1.0721 | 0.0046 | 9.3132
0.172 | 0.20199 | 0.045516 | 1.0801 | 1.0796 | 1.0796 | 1.0796 | 0.085459 | 9.5356 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1674 | 0.041903 | 1.0724 | 1.0723 | 1.0723 | 1.0723 | 0.94658 | 0.080347 | 9.3416 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1674 | 0.041903 | 1.0723 | 1.0723 | 1.0723 | 1.0723 | 0.94658 | 0.080347 | 9.3416 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1674 | 0.041903 | 1.0723 | 1.0723 | 1.0723 | 1.0723 | 0.94658 | 0.080347 | 172 | 80.3473 | 0.94658 | 1.0723 | 0.0046 | 9.3416
0.173 | 0.20303 | 0.045575 | 1.0802 | 1.0797 | 1.0797 | 1.0797 | 0.086215 | 9.5636 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1684 | 0.041972 | 1.0726 | 1.0724 | 1.0724 | 1.0724 | 0.94681 | 0.081079 | 9.3698 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1684 | 0.041972 | 1.0724 | 1.0724 | 1.0724 | 1.0724 | 0.94681 | 0.081079 | 9.3698 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1684 | 0.041972 | 1.0724 | 1.0724 | 1.0724 | 1.0724 | 0.94681 | 0.081079 | 173 | 81.0787 | 0.94681 | 1.0724 | 0.0046 | 9.3698
0.174 | 0.20407 | 0.045634 | 1.0803 | 1.0798 | 1.0798 | 1.0798 | 0.086974 | 9.5916 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1694 | 0.042039 | 1.0727 | 1.0725 | 1.0725 | 1.0725 | 0.94703 | 0.081812 | 9.398 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1694 | 0.042039 | 1.0725 | 1.0725 | 1.0725 | 1.0725 | 0.94703 | 0.081812 | 9.398 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1694 | 0.042039 | 1.0725 | 1.0725 | 1.0725 | 1.0725 | 0.94703 | 0.081812 | 174 | 81.8122 | 0.94703 | 1.0725 | 0.0046 | 9.398
0.175 | 0.20511 | 0.045693 | 1.0804 | 1.0799 | 1.0799 | 1.0799 | 0.087734 | 9.6195 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1704 | 0.042106 | 1.0728 | 1.0727 | 1.0727 | 1.0727 | 0.94725 | 0.082548 | 9.4261 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1704 | 0.042106 | 1.0727 | 1.0727 | 1.0727 | 1.0727 | 0.94725 | 0.082548 | 9.4261 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1704 | 0.042106 | 1.0727 | 1.0727 | 1.0727 | 1.0727 | 0.94725 | 0.082548 | 175 | 82.548 | 0.94725 | 1.0727 | 0.0046 | 9.4261
0.176 | 0.20615 | 0.045751 | 1.0805 | 1.08 | 1.08 | 1.08 | 0.088497 | 9.6473 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1714 | 0.042173 | 1.073 | 1.0728 | 1.0728 | 1.0728 | 0.94747 | 0.083286 | 9.4541 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1714 | 0.042173 | 1.0728 | 1.0728 | 1.0728 | 1.0728 | 0.94747 | 0.083286 | 9.4541 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1714 | 0.042173 | 1.0728 | 1.0728 | 1.0728 | 1.0728 | 0.94747 | 0.083286 | 176 | 83.286 | 0.94747 | 1.0728 | 0.0046 | 9.4541
0.177 | 0.20719 | 0.045809 | 1.0807 | 1.0802 | 1.0802 | 1.0802 | 0.089262 | 9.675 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1724 | 0.042239 | 1.0731 | 1.0729 | 1.0729 | 1.0729 | 0.94768 | 0.084026 | 9.482 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1724 | 0.042239 | 1.0729 | 1.0729 | 1.0729 | 1.0729 | 0.94768 | 0.084026 | 9.482 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1724 | 0.042239 | 1.0729 | 1.0729 | 1.0729 | 1.0729 | 0.94768 | 0.084026 | 177 | 84.0262 | 0.94768 | 1.0729 | 0.0046 | 9.482
0.178 | 0.20823 | 0.045866 | 1.0808 | 1.0803 | 1.0803 | 1.0803 | 0.090029 | 9.7027 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1734 | 0.042304 | 1.0732 | 1.0731 | 1.0731 | 1.0731 | 0.9479 | 0.084769 | 9.5099 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1734 | 0.042304 | 1.0731 | 1.0731 | 1.0731 | 1.0731 | 0.9479 | 0.084769 | 9.5099 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1734 | 0.042304 | 1.0731 | 1.0731 | 1.0731 | 1.0731 | 0.9479 | 0.084769 | 178 | 84.7687 | 0.9479 | 1.0731 | 0.0046 | 9.5099
0.179 | 0.20927 | 0.045922 | 1.0809 | 1.0804 | 1.0804 | 1.0804 | 0.090799 | 9.7302 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1744 | 0.042369 | 1.0734 | 1.0732 | 1.0732 | 1.0732 | 0.94811 | 0.085513 | 9.5376 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1744 | 0.042369 | 1.0732 | 1.0732 | 1.0732 | 1.0732 | 0.94811 | 0.085513 | 9.5376 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1744 | 0.042369 | 1.0732 | 1.0732 | 1.0732 | 1.0732 | 0.94811 | 0.085513 | 179 | 85.5133 | 0.94811 | 1.0732 | 0.0046 | 9.5376
0.18 | 0.21032 | 0.045978 | 1.081 | 1.0805 | 1.0805 | 1.0805 | 0.091571 | 9.7577 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1754 | 0.042433 | 1.0735 | 1.0733 | 1.0733 | 1.0733 | 0.94832 | 0.08626 | 9.5653 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1754 | 0.042433 | 1.0733 | 1.0733 | 1.0733 | 1.0733 | 0.94832 | 0.08626 | 9.5653 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1754 | 0.042433 | 1.0733 | 1.0733 | 1.0733 | 1.0733 | 0.94832 | 0.08626 | 180 | 86.2601 | 0.94832 | 1.0733 | 0.0046 | 9.5653
0.181 | 0.21136 | 0.046033 | 1.0811 | 1.0806 | 1.0806 | 1.0806 | 0.092345 | 9.7851 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1764 | 0.042496 | 1.0736 | 1.0734 | 1.0734 | 1.0734 | 0.94852 | 0.087009 | 9.5929 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1764 | 0.042496 | 1.0734 | 1.0734 | 1.0734 | 1.0734 | 0.94852 | 0.087009 | 9.5929 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1764 | 0.042496 | 1.0734 | 1.0734 | 1.0734 | 1.0734 | 0.94852 | 0.087009 | 181 | 87.0092 | 0.94852 | 1.0734 | 0.0046 | 9.5929
0.182 | 0.2124 | 0.046088 | 1.0812 | 1.0807 | 1.0807 | 1.0807 | 0.093121 | 9.8124 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1774 | 0.042559 | 1.0737 | 1.0736 | 1.0736 | 1.0736 | 0.94873 | 0.08776 | 9.6204 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1774 | 0.042559 | 1.0736 | 1.0736 | 1.0736 | 1.0736 | 0.94873 | 0.08776 | 9.6204 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1774 | 0.042559 | 1.0736 | 1.0736 | 1.0736 | 1.0736 | 0.94873 | 0.08776 | 182 | 87.7604 | 0.94873 | 1.0736 | 0.0046 | 9.6204
0.183 | 0.21344 | 0.046142 | 1.0813 | 1.0809 | 1.0808 | 1.0808 | 0.093899 | 9.8397 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1784 | 0.042621 | 1.0739 | 1.0737 | 1.0737 | 1.0737 | 0.94893 | 0.088514 | 9.6479 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1784 | 0.042621 | 1.0737 | 1.0737 | 1.0737 | 1.0737 | 0.94893 | 0.088514 | 9.6479 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1784 | 0.042621 | 1.0737 | 1.0737 | 1.0737 | 1.0737 | 0.94893 | 0.088514 | 183 | 88.5137 | 0.94893 | 1.0737 | 0.0046 | 9.6479
0.184 | 0.21448 | 0.046196 | 1.0814 | 1.081 | 1.0809 | 1.0809 | 0.094679 | 9.8669 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1794 | 0.042683 | 1.074 | 1.0738 | 1.0738 | 1.0738 | 0.94913 | 0.089269 | 9.6753 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1794 | 0.042683 | 1.0738 | 1.0738 | 1.0738 | 1.0738 | 0.94913 | 0.089269 | 9.6753 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1794 | 0.042683 | 1.0738 | 1.0738 | 1.0738 | 1.0738 | 0.94913 | 0.089269 | 184 | 89.2693 | 0.94913 | 1.0738 | 0.0046 | 9.6753
0.185 | 0.21552 | 0.04625 | 1.0816 | 1.0811 | 1.0811 | 1.0811 | 0.095462 | 9.894 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1804 | 0.042744 | 1.0741 | 1.0739 | 1.0739 | 1.0739 | 0.94933 | 0.090027 | 9.7026 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1804 | 0.042744 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 0.94933 | 0.090027 | 9.7026 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1804 | 0.042744 | 1.0739 | 1.0739 | 1.0739 | 1.0739 | 0.94933 | 0.090027 | 185 | 90.027 | 0.94933 | 1.0739 | 0.0046 | 9.7026
0.186 | 0.21656 | 0.046303 | 1.0817 | 1.0812 | 1.0812 | 1.0812 | 0.096247 | 9.921 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1814 | 0.042805 | 1.0742 | 1.0741 | 1.0741 | 1.0741 | 0.94952 | 0.090787 | 9.7298 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1814 | 0.042805 | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 0.94952 | 0.090787 | 9.7298 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1814 | 0.042805 | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 0.94952 | 0.090787 | 186 | 90.7869 | 0.94952 | 1.0741 | 0.0046 | 9.7298
0.187 | 0.2176 | 0.046355 | 1.0818 | 1.0813 | 1.0813 | 1.0813 | 0.097034 | 9.948 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1824 | 0.042865 | 1.0744 | 1.0742 | 1.0742 | 1.0742 | 0.94971 | 0.091549 | 9.7569 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1824 | 0.042865 | 1.0742 | 1.0742 | 1.0742 | 1.0742 | 0.94971 | 0.091549 | 9.7569 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1824 | 0.042865 | 1.0742 | 1.0742 | 1.0742 | 1.0742 | 0.94971 | 0.091549 | 187 | 91.5489 | 0.94971 | 1.0742 | 0.0046 | 9.7569
0.188 | 0.21865 | 0.046407 | 1.0819 | 1.0814 | 1.0814 | 1.0814 | 0.097823 | 9.9749 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1834 | 0.042924 | 1.0745 | 1.0743 | 1.0743 | 1.0743 | 0.9499 | 0.092313 | 9.784 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1834 | 0.042924 | 1.0743 | 1.0743 | 1.0743 | 1.0743 | 0.9499 | 0.092313 | 9.784 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1834 | 0.042924 | 1.0743 | 1.0743 | 1.0743 | 1.0743 | 0.9499 | 0.092313 | 188 | 92.3131 | 0.9499 | 1.0743 | 0.0046 | 9.784
0.189 | 0.21969 | 0.046459 | 1.082 | 1.0815 | 1.0815 | 1.0815 | 0.098614 | 10.0017 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.18427 | 0.042885 | 1.0744 | 1.0742 | 1.0742 | 1.0742 | 0.94867 | 0.092923 | 9.8055 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1844 | 0.042983 | 1.0744 | 1.0744 | 1.0744 | 1.0744 | 0.95009 | 0.093079 | 9.811 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1844 | 0.042983 | 1.0744 | 1.0744 | 1.0744 | 1.0744 | 0.95009 | 0.093079 | 189 | 93.0794 | 0.95009 | 1.0744 | 0.0046 | 9.811
0.19 | 0.22073 | 0.04651 | 1.0821 | 1.0816 | 1.0816 | 1.0816 | 0.099407 | 10.0285 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.18527 | 0.042944 | 1.0745 | 1.0743 | 1.0743 | 1.0743 | 0.94886 | 0.093691 | 9.8324 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1854 | 0.043042 | 1.0745 | 1.0745 | 1.0745 | 1.0745 | 0.95028 | 0.093848 | 9.8379 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1854 | 0.043042 | 1.0745 | 1.0745 | 1.0745 | 1.0745 | 0.95028 | 0.093848 | 190 | 93.8479 | 0.95028 | 1.0745 | 0.0046 | 9.8379
0.191 | 0.22177 | 0.04656 | 1.0822 | 1.0817 | 1.0817 | 1.0817 | 0.1002 | 10.0552 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.18627 | 0.043002 | 1.0746 | 1.0745 | 1.0745 | 1.0745 | 0.94905 | 0.09446 | 9.8593 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1864 | 0.0431 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 0.95047 | 0.094618 | 9.8648 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1864 | 0.0431 | 1.0746 | 1.0746 | 1.0746 | 1.0746 | 0.95047 | 0.094618 | 191 | 94.6184 | 0.95047 | 1.0746 | 0.0046 | 9.8648
0.192 | 0.22281 | 0.04661 | 1.0823 | 1.0818 | 1.0818 | 1.0818 | 0.101 | 10.0818 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.18727 | 0.04306 | 1.0748 | 1.0746 | 1.0746 | 1.0746 | 0.94924 | 0.095232 | 9.8861 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1874 | 0.043157 | 1.0748 | 1.0748 | 1.0748 | 1.0748 | 0.95065 | 0.095391 | 9.8916 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1874 | 0.043157 | 1.0748 | 1.0748 | 1.0748 | 1.0748 | 0.95065 | 0.095391 | 192 | 95.3911 | 0.95065 | 1.0748 | 0.0046 | 9.8916
0.193 | 0.22385 | 0.04666 | 1.0824 | 1.0819 | 1.0819 | 1.0819 | 0.1018 | 10.1083 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.18827 | 0.043117 | 1.0749 | 1.0747 | 1.0747 | 1.0747 | 0.94943 | 0.096007 | 9.9128 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1884 | 0.043214 | 1.0749 | 1.0749 | 1.0749 | 1.0749 | 0.95083 | 0.096166 | 9.9183 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1884 | 0.043214 | 1.0749 | 1.0749 | 1.0749 | 1.0749 | 0.95083 | 0.096166 | 193 | 96.1659 | 0.95083 | 1.0749 | 0.0046 | 9.9183
0.194 | 0.22489 | 0.046709 | 1.0825 | 1.082 | 1.082 | 1.082 | 0.1026 | 10.1348 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.18927 | 0.043174 | 1.075 | 1.0748 | 1.0748 | 1.0748 | 0.94961 | 0.096783 | 9.9394 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1894 | 0.043271 | 1.075 | 1.075 | 1.075 | 1.075 | 0.95101 | 0.096943 | 9.9449 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1894 | 0.043271 | 1.075 | 1.075 | 1.075 | 1.075 | 0.95101 | 0.096943 | 194 | 96.9429 | 0.95101 | 1.075 | 0.0046 | 9.9449
0.195 | 0.22593 | 0.046758 | 1.0826 | 1.0821 | 1.0821 | 1.0821 | 0.10341 | 10.1612 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19027 | 0.04323 | 1.0751 | 1.0749 | 1.0749 | 1.0749 | 0.94979 | 0.097561 | 9.966 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1904 | 0.043327 | 1.0751 | 1.0751 | 1.0751 | 1.0751 | 0.95119 | 0.097722 | 9.9715 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1904 | 0.043327 | 1.0751 | 1.0751 | 1.0751 | 1.0751 | 0.95119 | 0.097722 | 195 | 97.7219 | 0.95119 | 1.0751 | 0.0046 | 9.9715
0.196 | 0.22697 | 0.046806 | 1.0827 | 1.0822 | 1.0822 | 1.0822 | 0.10421 | 10.1875 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19127 | 0.043286 | 1.0752 | 1.075 | 1.075 | 1.075 | 0.94998 | 0.098341 | 9.9925 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1914 | 0.043382 | 1.0752 | 1.0752 | 1.0752 | 1.0752 | 0.95136 | 0.098503 | 9.998 | 0.0052 | 0.0043 | 0.0046 | 0.64172 | 0.1914 | 0.043382 | 1.0752 | 1.0752 | 1.0752 | 1.0752 | 0.95136 | 0.098503 | 196 | 98.503 | 0.95136 | 1.0752 | 0.0046 | 9.998
0.197 | 0.22802 | 0.046854 | 1.0828 | 1.0823 | 1.0823 | 1.0823 | 0.10502 | 10.2138 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19227 | 0.043341 | 1.0753 | 1.0751 | 1.0751 | 1.0751 | 0.95015 | 0.099124 | 10.0189 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19227 | 0.043341 | 1.0751 | 1.0751 | 1.0751 | 1.0751 | 0.95015 | 0.099124 | 10.0189 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19227 | 0.043341 | 1.0751 | 1.0751 | 1.0751 | 1.0751 | 0.95015 | 0.099124 | 197 | 99.124 | 0.95015 | 1.0751 | 0.0047333 | 10.0189
0.198 | 0.22906 | 0.046902 | 1.0829 | 1.0824 | 1.0824 | 1.0824 | 0.10583 | 10.24 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19327 | 0.043396 | 1.0754 | 1.0752 | 1.0752 | 1.0752 | 0.95033 | 0.099909 | 10.0453 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19327 | 0.043396 | 1.0752 | 1.0752 | 1.0752 | 1.0752 | 0.95033 | 0.099909 | 10.0453 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19327 | 0.043396 | 1.0752 | 1.0752 | 1.0752 | 1.0752 | 0.95033 | 0.099909 | 198 | 99.9086 | 0.95033 | 1.0752 | 0.0047333 | 10.0453
0.199 | 0.2301 | 0.046949 | 1.083 | 1.0825 | 1.0825 | 1.0825 | 0.10664 | 10.2661 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19427 | 0.04345 | 1.0755 | 1.0754 | 1.0754 | 1.0754 | 0.95051 | 0.1007 | 10.0716 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19427 | 0.04345 | 1.0754 | 1.0754 | 1.0754 | 1.0754 | 0.95051 | 0.1007 | 10.0716 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19427 | 0.04345 | 1.0754 | 1.0754 | 1.0754 | 1.0754 | 0.95051 | 0.1007 | 199 | 100.6952 | 0.95051 | 1.0754 | 0.0047333 | 10.0716
0.2 | 0.23114 | 0.046996 | 1.0831 | 1.0826 | 1.0826 | 1.0826 | 0.10746 | 10.2922 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19527 | 0.043504 | 1.0756 | 1.0755 | 1.0755 | 1.0755 | 0.95068 | 0.10148 | 10.0978 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19527 | 0.043504 | 1.0755 | 1.0755 | 1.0755 | 1.0755 | 0.95068 | 0.10148 | 10.0978 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19527 | 0.043504 | 1.0755 | 1.0755 | 1.0755 | 1.0755 | 0.95068 | 0.10148 | 200 | 101.484 | 0.95068 | 1.0755 | 0.0047333 | 10.0978
0.201 | 0.23218 | 0.047042 | 1.0832 | 1.0827 | 1.0827 | 1.0827 | 0.10827 | 10.3182 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19627 | 0.043558 | 1.0758 | 1.0756 | 1.0756 | 1.0756 | 0.95085 | 0.10227 | 10.124 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19627 | 0.043558 | 1.0756 | 1.0756 | 1.0756 | 1.0756 | 0.95085 | 0.10227 | 10.124 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19627 | 0.043558 | 1.0756 | 1.0756 | 1.0756 | 1.0756 | 0.95085 | 0.10227 | 201 | 102.2748 | 0.95085 | 1.0756 | 0.0047333 | 10.124
0.202 | 0.23322 | 0.047088 | 1.0833 | 1.0828 | 1.0828 | 1.0828 | 0.10909 | 10.3441 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19727 | 0.043611 | 1.0759 | 1.0757 | 1.0757 | 1.0757 | 0.95102 | 0.10307 | 10.1501 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19727 | 0.043611 | 1.0757 | 1.0757 | 1.0757 | 1.0757 | 0.95102 | 0.10307 | 10.1501 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19727 | 0.043611 | 1.0757 | 1.0757 | 1.0757 | 1.0757 | 0.95102 | 0.10307 | 202 | 103.0677 | 0.95102 | 1.0757 | 0.0047333 | 10.1501
0.203 | 0.23426 | 0.047134 | 1.0834 | 1.0829 | 1.0829 | 1.0829 | 0.10991 | 10.37 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19827 | 0.043663 | 1.076 | 1.0758 | 1.0758 | 1.0758 | 0.95119 | 0.10386 | 10.1761 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19827 | 0.043663 | 1.0758 | 1.0758 | 1.0758 | 1.0758 | 0.95119 | 0.10386 | 10.1761 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19827 | 0.043663 | 1.0758 | 1.0758 | 1.0758 | 1.0758 | 0.95119 | 0.10386 | 203 | 103.8627 | 0.95119 | 1.0758 | 0.0047333 | 10.1761
0.204 | 0.2353 | 0.047179 | 1.0834 | 1.083 | 1.083 | 1.083 | 0.11074 | 10.3958 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19927 | 0.043715 | 1.0761 | 1.0759 | 1.0759 | 1.0759 | 0.95136 | 0.10466 | 10.2021 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19927 | 0.043715 | 1.0759 | 1.0759 | 1.0759 | 1.0759 | 0.95136 | 0.10466 | 10.2021 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.19927 | 0.043715 | 1.0759 | 1.0759 | 1.0759 | 1.0759 | 0.95136 | 0.10466 | 204 | 104.6597 | 0.95136 | 1.0759 | 0.0047333 | 10.2021
0.205 | 0.23634 | 0.047224 | 1.0835 | 1.0831 | 1.0831 | 1.0831 | 0.11156 | 10.4216 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20027 | 0.043767 | 1.0762 | 1.076 | 1.076 | 1.076 | 0.95152 | 0.10546 | 10.228 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20027 | 0.043767 | 1.076 | 1.076 | 1.076 | 1.076 | 0.95152 | 0.10546 | 10.228 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20027 | 0.043767 | 1.076 | 1.076 | 1.076 | 1.076 | 0.95152 | 0.10546 | 205 | 105.4587 | 0.95152 | 1.076 | 0.0047333 | 10.228
0.206 | 0.23739 | 0.047268 | 1.0836 | 1.0832 | 1.0832 | 1.0832 | 0.11239 | 10.4472 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20127 | 0.043818 | 1.0763 | 1.0761 | 1.0761 | 1.0761 | 0.95169 | 0.10626 | 10.2538 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20127 | 0.043818 | 1.0761 | 1.0761 | 1.0761 | 1.0761 | 0.95169 | 0.10626 | 10.2538 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20127 | 0.043818 | 1.0761 | 1.0761 | 1.0761 | 1.0761 | 0.95169 | 0.10626 | 206 | 106.2598 | 0.95169 | 1.0761 | 0.0047333 | 10.2538
0.207 | 0.23843 | 0.047313 | 1.0837 | 1.0833 | 1.0833 | 1.0833 | 0.11322 | 10.4729 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20227 | 0.043869 | 1.0764 | 1.0762 | 1.0762 | 1.0762 | 0.95185 | 0.10706 | 10.2796 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20227 | 0.043869 | 1.0762 | 1.0762 | 1.0762 | 1.0762 | 0.95185 | 0.10706 | 10.2796 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20227 | 0.043869 | 1.0762 | 1.0762 | 1.0762 | 1.0762 | 0.95185 | 0.10706 | 207 | 107.063 | 0.95185 | 1.0762 | 0.0047333 | 10.2796
0.208 | 0.23947 | 0.047356 | 1.0838 | 1.0834 | 1.0833 | 1.0833 | 0.11405 | 10.4984 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20327 | 0.04392 | 1.0765 | 1.0763 | 1.0763 | 1.0763 | 0.95201 | 0.10787 | 10.3053 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20327 | 0.04392 | 1.0763 | 1.0763 | 1.0763 | 1.0763 | 0.95201 | 0.10787 | 10.3053 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20327 | 0.04392 | 1.0763 | 1.0763 | 1.0763 | 1.0763 | 0.95201 | 0.10787 | 208 | 107.8682 | 0.95201 | 1.0763 | 0.0047333 | 10.3053
0.209 | 0.24051 | 0.0474 | 1.0839 | 1.0835 | 1.0834 | 1.0834 | 0.11488 | 10.5239 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20427 | 0.04397 | 1.0766 | 1.0764 | 1.0764 | 1.0764 | 0.95217 | 0.10868 | 10.3309 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20427 | 0.04397 | 1.0764 | 1.0764 | 1.0764 | 1.0764 | 0.95217 | 0.10868 | 10.3309 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20427 | 0.04397 | 1.0764 | 1.0764 | 1.0764 | 1.0764 | 0.95217 | 0.10868 | 209 | 108.6754 | 0.95217 | 1.0764 | 0.0047333 | 10.3309
0.21 | 0.24155 | 0.047443 | 1.084 | 1.0835 | 1.0835 | 1.0835 | 0.11572 | 10.5494 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20527 | 0.044019 | 1.0767 | 1.0765 | 1.0765 | 1.0765 | 0.95233 | 0.10948 | 10.3565 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20527 | 0.044019 | 1.0765 | 1.0765 | 1.0765 | 1.0765 | 0.95233 | 0.10948 | 10.3565 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20527 | 0.044019 | 1.0765 | 1.0765 | 1.0765 | 1.0765 | 0.95233 | 0.10948 | 210 | 109.4846 | 0.95233 | 1.0765 | 0.0047333 | 10.3565
0.211 | 0.24259 | 0.047485 | 1.0841 | 1.0836 | 1.0836 | 1.0836 | 0.11655 | 10.5747 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20627 | 0.044068 | 1.0768 | 1.0766 | 1.0766 | 1.0766 | 0.95248 | 0.1103 | 10.382 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20627 | 0.044068 | 1.0766 | 1.0766 | 1.0766 | 1.0766 | 0.95248 | 0.1103 | 10.382 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20627 | 0.044068 | 1.0766 | 1.0766 | 1.0766 | 1.0766 | 0.95248 | 0.1103 | 211 | 110.2959 | 0.95248 | 1.0766 | 0.0047333 | 10.382
0.212 | 0.24363 | 0.047528 | 1.0842 | 1.0837 | 1.0837 | 1.0837 | 0.11739 | 10.6001 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20727 | 0.044117 | 1.0769 | 1.0767 | 1.0767 | 1.0767 | 0.95264 | 0.11111 | 10.4075 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20727 | 0.044117 | 1.0767 | 1.0767 | 1.0767 | 1.0767 | 0.95264 | 0.11111 | 10.4075 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20727 | 0.044117 | 1.0767 | 1.0767 | 1.0767 | 1.0767 | 0.95264 | 0.11111 | 212 | 111.1091 | 0.95264 | 1.0767 | 0.0047333 | 10.4075
0.213 | 0.24467 | 0.04757 | 1.0842 | 1.0838 | 1.0838 | 1.0838 | 0.11823 | 10.6253 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20827 | 0.044166 | 1.077 | 1.0768 | 1.0768 | 1.0768 | 0.95279 | 0.11192 | 10.4329 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20827 | 0.044166 | 1.0768 | 1.0768 | 1.0768 | 1.0768 | 0.95279 | 0.11192 | 10.4329 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20827 | 0.044166 | 1.0768 | 1.0768 | 1.0768 | 1.0768 | 0.95279 | 0.11192 | 213 | 111.9244 | 0.95279 | 1.0768 | 0.0047333 | 10.4329
0.214 | 0.24572 | 0.047611 | 1.0843 | 1.0839 | 1.0839 | 1.0839 | 0.11908 | 10.6505 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20927 | 0.044214 | 1.0771 | 1.0769 | 1.0769 | 1.0769 | 0.95294 | 0.11274 | 10.4582 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20927 | 0.044214 | 1.0769 | 1.0769 | 1.0769 | 1.0769 | 0.95294 | 0.11274 | 10.4582 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.20927 | 0.044214 | 1.0769 | 1.0769 | 1.0769 | 1.0769 | 0.95294 | 0.11274 | 214 | 112.7417 | 0.95294 | 1.0769 | 0.0047333 | 10.4582
0.215 | 0.24676 | 0.047653 | 1.0844 | 1.084 | 1.084 | 1.084 | 0.11992 | 10.6757 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21027 | 0.044261 | 1.0772 | 1.077 | 1.077 | 1.077 | 0.95309 | 0.11356 | 10.4835 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21027 | 0.044261 | 1.077 | 1.077 | 1.077 | 1.077 | 0.95309 | 0.11356 | 10.4835 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21027 | 0.044261 | 1.077 | 1.077 | 1.077 | 1.077 | 0.95309 | 0.11356 | 215 | 113.561 | 0.95309 | 1.077 | 0.0047333 | 10.4835
0.216 | 0.2478 | 0.047694 | 1.0845 | 1.0841 | 1.0841 | 1.0841 | 0.12077 | 10.7007 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21127 | 0.044309 | 1.0773 | 1.0771 | 1.0771 | 1.0771 | 0.95324 | 0.11438 | 10.5087 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21127 | 0.044309 | 1.0771 | 1.0771 | 1.0771 | 1.0771 | 0.95324 | 0.11438 | 10.5087 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21127 | 0.044309 | 1.0771 | 1.0771 | 1.0771 | 1.0771 | 0.95324 | 0.11438 | 216 | 114.3822 | 0.95324 | 1.0771 | 0.0047333 | 10.5087
0.217 | 0.24884 | 0.047734 | 1.0846 | 1.0841 | 1.0841 | 1.0841 | 0.12162 | 10.7258 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21227 | 0.044356 | 1.0774 | 1.0772 | 1.0772 | 1.0772 | 0.95339 | 0.11521 | 10.5338 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21227 | 0.044356 | 1.0772 | 1.0772 | 1.0772 | 1.0772 | 0.95339 | 0.11521 | 10.5338 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21227 | 0.044356 | 1.0772 | 1.0772 | 1.0772 | 1.0772 | 0.95339 | 0.11521 | 217 | 115.2055 | 0.95339 | 1.0772 | 0.0047333 | 10.5338
0.218 | 0.24988 | 0.047775 | 1.0847 | 1.0842 | 1.0842 | 1.0842 | 0.12247 | 10.7507 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21327 | 0.044402 | 1.0775 | 1.0773 | 1.0773 | 1.0773 | 0.95354 | 0.11603 | 10.5589 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21327 | 0.044402 | 1.0773 | 1.0773 | 1.0773 | 1.0773 | 0.95354 | 0.11603 | 10.5589 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21327 | 0.044402 | 1.0773 | 1.0773 | 1.0773 | 1.0773 | 0.95354 | 0.11603 | 218 | 116.0308 | 0.95354 | 1.0773 | 0.0047333 | 10.5589
0.219 | 0.25092 | 0.047815 | 1.0847 | 1.0843 | 1.0843 | 1.0843 | 0.12332 | 10.7756 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21427 | 0.044448 | 1.0776 | 1.0774 | 1.0774 | 1.0774 | 0.95368 | 0.11686 | 10.584 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21427 | 0.044448 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 0.95368 | 0.11686 | 10.584 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21427 | 0.044448 | 1.0774 | 1.0774 | 1.0774 | 1.0774 | 0.95368 | 0.11686 | 219 | 116.858 | 0.95368 | 1.0774 | 0.0047333 | 10.584
0.22 | 0.25196 | 0.047854 | 1.0848 | 1.0844 | 1.0844 | 1.0844 | 0.12418 | 10.8005 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21527 | 0.044494 | 1.0777 | 1.0775 | 1.0775 | 1.0775 | 0.95382 | 0.11769 | 10.6089 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21527 | 0.044494 | 1.0775 | 1.0775 | 1.0775 | 1.0775 | 0.95382 | 0.11769 | 10.6089 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21527 | 0.044494 | 1.0775 | 1.0775 | 1.0775 | 1.0775 | 0.95382 | 0.11769 | 220 | 117.6872 | 0.95382 | 1.0775 | 0.0047333 | 10.6089
0.221 | 0.253 | 0.047894 | 1.0849 | 1.0845 | 1.0845 | 1.0845 | 0.12503 | 10.8253 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21627 | 0.04454 | 1.0777 | 1.0776 | 1.0776 | 1.0776 | 0.95397 | 0.11852 | 10.6339 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21627 | 0.04454 | 1.0776 | 1.0776 | 1.0776 | 1.0776 | 0.95397 | 0.11852 | 10.6339 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21627 | 0.04454 | 1.0776 | 1.0776 | 1.0776 | 1.0776 | 0.95397 | 0.11852 | 221 | 118.5184 | 0.95397 | 1.0776 | 0.0047333 | 10.6339
0.222 | 0.25404 | 0.047933 | 1.085 | 1.0846 | 1.0846 | 1.0846 | 0.12589 | 10.85 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21727 | 0.044585 | 1.0778 | 1.0777 | 1.0777 | 1.0777 | 0.95411 | 0.11935 | 10.6587 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21727 | 0.044585 | 1.0777 | 1.0777 | 1.0777 | 1.0777 | 0.95411 | 0.11935 | 10.6587 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21727 | 0.044585 | 1.0777 | 1.0777 | 1.0777 | 1.0777 | 0.95411 | 0.11935 | 222 | 119.3515 | 0.95411 | 1.0777 | 0.0047333 | 10.6587
0.223 | 0.25509 | 0.047972 | 1.0851 | 1.0846 | 1.0846 | 1.0846 | 0.12675 | 10.8747 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21827 | 0.04463 | 1.0779 | 1.0777 | 1.0777 | 1.0777 | 0.95425 | 0.12019 | 10.6835 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21827 | 0.04463 | 1.0777 | 1.0777 | 1.0777 | 1.0777 | 0.95425 | 0.12019 | 10.6835 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21827 | 0.04463 | 1.0777 | 1.0777 | 1.0777 | 1.0777 | 0.95425 | 0.12019 | 223 | 120.1866 | 0.95425 | 1.0777 | 0.0047333 | 10.6835
0.224 | 0.25613 | 0.04801 | 1.0851 | 1.0847 | 1.0847 | 1.0847 | 0.12762 | 10.8993 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21927 | 0.044674 | 1.078 | 1.0778 | 1.0778 | 1.0778 | 0.95439 | 0.12102 | 10.7083 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21927 | 0.044674 | 1.0778 | 1.0778 | 1.0778 | 1.0778 | 0.95439 | 0.12102 | 10.7083 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.21927 | 0.044674 | 1.0778 | 1.0778 | 1.0778 | 1.0778 | 0.95439 | 0.12102 | 224 | 121.0237 | 0.95439 | 1.0778 | 0.0047333 | 10.7083
0.225 | 0.25717 | 0.048048 | 1.0852 | 1.0848 | 1.0848 | 1.0848 | 0.12848 | 10.9239 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22027 | 0.044718 | 1.0781 | 1.0779 | 1.0779 | 1.0779 | 0.95452 | 0.12186 | 10.733 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22027 | 0.044718 | 1.0779 | 1.0779 | 1.0779 | 1.0779 | 0.95452 | 0.12186 | 10.733 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22027 | 0.044718 | 1.0779 | 1.0779 | 1.0779 | 1.0779 | 0.95452 | 0.12186 | 225 | 121.8627 | 0.95452 | 1.0779 | 0.0047333 | 10.733
0.226 | 0.25821 | 0.048086 | 1.0853 | 1.0849 | 1.0849 | 1.0849 | 0.12935 | 10.9484 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22127 | 0.044762 | 1.0782 | 1.078 | 1.078 | 1.078 | 0.95466 | 0.1227 | 10.7576 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22127 | 0.044762 | 1.078 | 1.078 | 1.078 | 1.078 | 0.95466 | 0.1227 | 10.7576 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22127 | 0.044762 | 1.078 | 1.078 | 1.078 | 1.078 | 0.95466 | 0.1227 | 226 | 122.7037 | 0.95466 | 1.078 | 0.0047333 | 10.7576
0.227 | 0.25925 | 0.048124 | 1.0854 | 1.085 | 1.085 | 1.0849 | 0.13022 | 10.9728 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22227 | 0.044805 | 1.0783 | 1.0781 | 1.0781 | 1.0781 | 0.9548 | 0.12355 | 10.7822 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22227 | 0.044805 | 1.0781 | 1.0781 | 1.0781 | 1.0781 | 0.9548 | 0.12355 | 10.7822 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22227 | 0.044805 | 1.0781 | 1.0781 | 1.0781 | 1.0781 | 0.9548 | 0.12355 | 227 | 123.5466 | 0.9548 | 1.0781 | 0.0047333 | 10.7822
0.228 | 0.26029 | 0.048161 | 1.0855 | 1.085 | 1.085 | 1.085 | 0.13109 | 10.9973 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22327 | 0.044849 | 1.0784 | 1.0782 | 1.0782 | 1.0782 | 0.95493 | 0.12439 | 10.8067 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22327 | 0.044849 | 1.0782 | 1.0782 | 1.0782 | 1.0782 | 0.95493 | 0.12439 | 10.8067 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22327 | 0.044849 | 1.0782 | 1.0782 | 1.0782 | 1.0782 | 0.95493 | 0.12439 | 228 | 124.3914 | 0.95493 | 1.0782 | 0.0047333 | 10.8067
0.229 | 0.26133 | 0.048198 | 1.0855 | 1.0851 | 1.0851 | 1.0851 | 0.13196 | 11.0216 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22427 | 0.044891 | 1.0785 | 1.0783 | 1.0783 | 1.0783 | 0.95506 | 0.12524 | 10.8311 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22427 | 0.044891 | 1.0783 | 1.0783 | 1.0783 | 1.0783 | 0.95506 | 0.12524 | 10.8311 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22427 | 0.044891 | 1.0783 | 1.0783 | 1.0783 | 1.0783 | 0.95506 | 0.12524 | 229 | 125.2382 | 0.95506 | 1.0783 | 0.0047333 | 10.8311
0.23 | 0.26237 | 0.048235 | 1.0856 | 1.0852 | 1.0852 | 1.0852 | 0.13284 | 11.0459 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22527 | 0.044934 | 1.0785 | 1.0784 | 1.0784 | 1.0784 | 0.95519 | 0.12609 | 10.8556 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22527 | 0.044934 | 1.0784 | 1.0784 | 1.0784 | 1.0784 | 0.95519 | 0.12609 | 10.8556 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22527 | 0.044934 | 1.0784 | 1.0784 | 1.0784 | 1.0784 | 0.95519 | 0.12609 | 230 | 126.0869 | 0.95519 | 1.0784 | 0.0047333 | 10.8556
0.231 | 0.26342 | 0.048271 | 1.0857 | 1.0853 | 1.0853 | 1.0853 | 0.13371 | 11.0702 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22627 | 0.044976 | 1.0786 | 1.0785 | 1.0784 | 1.0784 | 0.95532 | 0.12694 | 10.8799 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22627 | 0.044976 | 1.0784 | 1.0784 | 1.0784 | 1.0784 | 0.95532 | 0.12694 | 10.8799 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22627 | 0.044976 | 1.0784 | 1.0784 | 1.0784 | 1.0784 | 0.95532 | 0.12694 | 231 | 126.9376 | 0.95532 | 1.0784 | 0.0047333 | 10.8799
0.232 | 0.26446 | 0.048308 | 1.0858 | 1.0853 | 1.0853 | 1.0853 | 0.13459 | 11.0943 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22727 | 0.045018 | 1.0787 | 1.0785 | 1.0785 | 1.0785 | 0.95545 | 0.12779 | 10.9042 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22727 | 0.045018 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 0.95545 | 0.12779 | 10.9042 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22727 | 0.045018 | 1.0785 | 1.0785 | 1.0785 | 1.0785 | 0.95545 | 0.12779 | 232 | 127.7901 | 0.95545 | 1.0785 | 0.0047333 | 10.9042
0.233 | 0.2655 | 0.048343 | 1.0858 | 1.0854 | 1.0854 | 1.0854 | 0.13547 | 11.1185 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22827 | 0.045059 | 1.0788 | 1.0786 | 1.0786 | 1.0786 | 0.95558 | 0.12864 | 10.9285 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22827 | 0.045059 | 1.0786 | 1.0786 | 1.0786 | 1.0786 | 0.95558 | 0.12864 | 10.9285 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22827 | 0.045059 | 1.0786 | 1.0786 | 1.0786 | 1.0786 | 0.95558 | 0.12864 | 233 | 128.6446 | 0.95558 | 1.0786 | 0.0047333 | 10.9285
0.234 | 0.26654 | 0.048379 | 1.0859 | 1.0855 | 1.0855 | 1.0855 | 0.13635 | 11.1426 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22927 | 0.045101 | 1.0789 | 1.0787 | 1.0787 | 1.0787 | 0.95571 | 0.1295 | 10.9527 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22927 | 0.045101 | 1.0787 | 1.0787 | 1.0787 | 1.0787 | 0.95571 | 0.1295 | 10.9527 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.22927 | 0.045101 | 1.0787 | 1.0787 | 1.0787 | 1.0787 | 0.95571 | 0.1295 | 234 | 129.501 | 0.95571 | 1.0787 | 0.0047333 | 10.9527
0.235 | 0.26758 | 0.048415 | 1.086 | 1.0856 | 1.0856 | 1.0856 | 0.13724 | 11.1666 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23027 | 0.045142 | 1.079 | 1.0788 | 1.0788 | 1.0788 | 0.95583 | 0.13036 | 10.9768 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23027 | 0.045142 | 1.0788 | 1.0788 | 1.0788 | 1.0788 | 0.95583 | 0.13036 | 10.9768 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23027 | 0.045142 | 1.0788 | 1.0788 | 1.0788 | 1.0788 | 0.95583 | 0.13036 | 235 | 130.3593 | 0.95583 | 1.0788 | 0.0047333 | 10.9768
0.236 | 0.26862 | 0.04845 | 1.086 | 1.0856 | 1.0856 | 1.0856 | 0.13813 | 11.1906 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23127 | 0.045182 | 1.0791 | 1.0789 | 1.0789 | 1.0789 | 0.95596 | 0.13122 | 11.0009 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23127 | 0.045182 | 1.0789 | 1.0789 | 1.0789 | 1.0789 | 0.95596 | 0.13122 | 11.0009 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23127 | 0.045182 | 1.0789 | 1.0789 | 1.0789 | 1.0789 | 0.95596 | 0.13122 | 236 | 131.2195 | 0.95596 | 1.0789 | 0.0047333 | 11.0009
0.237 | 0.26966 | 0.048485 | 1.0861 | 1.0857 | 1.0857 | 1.0857 | 0.13901 | 11.2145 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23227 | 0.045223 | 1.0791 | 1.079 | 1.079 | 1.079 | 0.95608 | 0.13208 | 11.0249 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23227 | 0.045223 | 1.079 | 1.079 | 1.079 | 1.079 | 0.95608 | 0.13208 | 11.0249 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23227 | 0.045223 | 1.079 | 1.079 | 1.079 | 1.079 | 0.95608 | 0.13208 | 237 | 132.0816 | 0.95608 | 1.079 | 0.0047333 | 11.0249
0.238 | 0.2707 | 0.048519 | 1.0862 | 1.0858 | 1.0858 | 1.0858 | 0.1399 | 11.2384 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23327 | 0.045263 | 1.0792 | 1.079 | 1.079 | 1.079 | 0.9562 | 0.13295 | 11.0489 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23327 | 0.045263 | 1.079 | 1.079 | 1.079 | 1.079 | 0.9562 | 0.13295 | 11.0489 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23327 | 0.045263 | 1.079 | 1.079 | 1.079 | 1.079 | 0.9562 | 0.13295 | 238 | 132.9456 | 0.9562 | 1.079 | 0.0047333 | 11.0489
0.239 | 0.27174 | 0.048554 | 1.0863 | 1.0859 | 1.0859 | 1.0859 | 0.1408 | 11.2623 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23427 | 0.045302 | 1.0793 | 1.0791 | 1.0791 | 1.0791 | 0.95633 | 0.13381 | 11.0729 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23427 | 0.045302 | 1.0791 | 1.0791 | 1.0791 | 1.0791 | 0.95633 | 0.13381 | 11.0729 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23427 | 0.045302 | 1.0791 | 1.0791 | 1.0791 | 1.0791 | 0.95633 | 0.13381 | 239 | 133.8115 | 0.95633 | 1.0791 | 0.0047333 | 11.0729
0.24 | 0.27279 | 0.048588 | 1.0863 | 1.0859 | 1.0859 | 1.0859 | 0.14169 | 11.286 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23527 | 0.045342 | 1.0794 | 1.0792 | 1.0792 | 1.0792 | 0.95645 | 0.13468 | 11.0968 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23527 | 0.045342 | 1.0792 | 1.0792 | 1.0792 | 1.0792 | 0.95645 | 0.13468 | 11.0968 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23527 | 0.045342 | 1.0792 | 1.0792 | 1.0792 | 1.0792 | 0.95645 | 0.13468 | 240 | 134.6793 | 0.95645 | 1.0792 | 0.0047333 | 11.0968
0.241 | 0.27383 | 0.048622 | 1.0864 | 1.086 | 1.086 | 1.086 | 0.14259 | 11.3098 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23627 | 0.045381 | 1.0795 | 1.0793 | 1.0793 | 1.0793 | 0.95657 | 0.13555 | 11.1206 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23627 | 0.045381 | 1.0793 | 1.0793 | 1.0793 | 1.0793 | 0.95657 | 0.13555 | 11.1206 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23627 | 0.045381 | 1.0793 | 1.0793 | 1.0793 | 1.0793 | 0.95657 | 0.13555 | 241 | 135.5489 | 0.95657 | 1.0793 | 0.0047333 | 11.1206
0.242 | 0.27487 | 0.048655 | 1.0865 | 1.0861 | 1.0861 | 1.0861 | 0.14348 | 11.3335 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23727 | 0.04542 | 1.0795 | 1.0794 | 1.0794 | 1.0794 | 0.95669 | 0.13642 | 11.1444 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23727 | 0.04542 | 1.0794 | 1.0794 | 1.0794 | 1.0794 | 0.95669 | 0.13642 | 11.1444 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23727 | 0.04542 | 1.0794 | 1.0794 | 1.0794 | 1.0794 | 0.95669 | 0.13642 | 242 | 136.4205 | 0.95669 | 1.0794 | 0.0047333 | 11.1444
0.243 | 0.27591 | 0.048689 | 1.0865 | 1.0861 | 1.0861 | 1.0861 | 0.14438 | 11.3571 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23827 | 0.045459 | 1.0796 | 1.0794 | 1.0794 | 1.0794 | 0.9568 | 0.13729 | 11.1681 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23827 | 0.045459 | 1.0794 | 1.0794 | 1.0794 | 1.0794 | 0.9568 | 0.13729 | 11.1681 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23827 | 0.045459 | 1.0794 | 1.0794 | 1.0794 | 1.0794 | 0.9568 | 0.13729 | 243 | 137.2939 | 0.9568 | 1.0794 | 0.0047333 | 11.1681
0.244 | 0.27695 | 0.048722 | 1.0866 | 1.0862 | 1.0862 | 1.0862 | 0.14528 | 11.3807 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23927 | 0.045497 | 1.0797 | 1.0795 | 1.0795 | 1.0795 | 0.95692 | 0.13817 | 11.1918 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23927 | 0.045497 | 1.0795 | 1.0795 | 1.0795 | 1.0795 | 0.95692 | 0.13817 | 11.1918 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.23927 | 0.045497 | 1.0795 | 1.0795 | 1.0795 | 1.0795 | 0.95692 | 0.13817 | 244 | 138.1692 | 0.95692 | 1.0795 | 0.0047333 | 11.1918
0.245 | 0.27799 | 0.048755 | 1.0867 | 1.0863 | 1.0863 | 1.0863 | 0.14619 | 11.4042 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24027 | 0.045535 | 1.0798 | 1.0796 | 1.0796 | 1.0796 | 0.95704 | 0.13905 | 11.2154 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24027 | 0.045535 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 0.95704 | 0.13905 | 11.2154 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24027 | 0.045535 | 1.0796 | 1.0796 | 1.0796 | 1.0796 | 0.95704 | 0.13905 | 245 | 139.0464 | 0.95704 | 1.0796 | 0.0047333 | 11.2154
0.246 | 0.27903 | 0.048787 | 1.0867 | 1.0864 | 1.0863 | 1.0863 | 0.14709 | 11.4277 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24127 | 0.045573 | 1.0799 | 1.0797 | 1.0797 | 1.0797 | 0.95715 | 0.13993 | 11.239 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24127 | 0.045573 | 1.0797 | 1.0797 | 1.0797 | 1.0797 | 0.95715 | 0.13993 | 11.239 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24127 | 0.045573 | 1.0797 | 1.0797 | 1.0797 | 1.0797 | 0.95715 | 0.13993 | 246 | 139.9254 | 0.95715 | 1.0797 | 0.0047333 | 11.239
0.247 | 0.28007 | 0.04882 | 1.0868 | 1.0864 | 1.0864 | 1.0864 | 0.148 | 11.4512 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24227 | 0.04561 | 1.0799 | 1.0797 | 1.0797 | 1.0797 | 0.95727 | 0.14081 | 11.2625 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24227 | 0.04561 | 1.0797 | 1.0797 | 1.0797 | 1.0797 | 0.95727 | 0.14081 | 11.2625 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24227 | 0.04561 | 1.0797 | 1.0797 | 1.0797 | 1.0797 | 0.95727 | 0.14081 | 247 | 140.8063 | 0.95727 | 1.0797 | 0.0047333 | 11.2625
0.248 | 0.28112 | 0.048852 | 1.0869 | 1.0865 | 1.0865 | 1.0865 | 0.14891 | 11.4746 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24327 | 0.045648 | 1.08 | 1.0798 | 1.0798 | 1.0798 | 0.95738 | 0.14169 | 11.286 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24327 | 0.045648 | 1.0798 | 1.0798 | 1.0798 | 1.0798 | 0.95738 | 0.14169 | 11.286 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24327 | 0.045648 | 1.0798 | 1.0798 | 1.0798 | 1.0798 | 0.95738 | 0.14169 | 248 | 141.689 | 0.95738 | 1.0798 | 0.0047333 | 11.286
0.249 | 0.28216 | 0.048884 | 1.0869 | 1.0866 | 1.0865 | 1.0865 | 0.14982 | 11.4979 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24427 | 0.045685 | 1.0801 | 1.0799 | 1.0799 | 1.0799 | 0.95749 | 0.14257 | 11.3095 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24427 | 0.045685 | 1.0799 | 1.0799 | 1.0799 | 1.0799 | 0.95749 | 0.14257 | 11.3095 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24427 | 0.045685 | 1.0799 | 1.0799 | 1.0799 | 1.0799 | 0.95749 | 0.14257 | 249 | 142.5736 | 0.95749 | 1.0799 | 0.0047333 | 11.3095
0.25 | 0.2832 | 0.048916 | 1.087 | 1.0866 | 1.0866 | 1.0866 | 0.15073 | 11.5212 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24527 | 0.045722 | 1.0802 | 1.08 | 1.08 | 1.08 | 0.9576 | 0.14346 | 11.3329 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24527 | 0.045722 | 1.08 | 1.08 | 1.08 | 1.08 | 0.9576 | 0.14346 | 11.3329 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24527 | 0.045722 | 1.08 | 1.08 | 1.08 | 1.08 | 0.9576 | 0.14346 | 250 | 143.46 | 0.9576 | 1.08 | 0.0047333 | 11.3329
0.251 | 0.28424 | 0.048947 | 1.0871 | 1.0867 | 1.0867 | 1.0867 | 0.15165 | 11.5445 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24627 | 0.045758 | 1.0802 | 1.0801 | 1.08 | 1.08 | 0.95771 | 0.14435 | 11.3562 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24627 | 0.045758 | 1.08 | 1.08 | 1.08 | 1.08 | 0.95771 | 0.14435 | 11.3562 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24627 | 0.045758 | 1.08 | 1.08 | 1.08 | 1.08 | 0.95771 | 0.14435 | 251 | 144.3483 | 0.95771 | 1.08 | 0.0047333 | 11.3562
0.252 | 0.28528 | 0.048979 | 1.0871 | 1.0868 | 1.0867 | 1.0867 | 0.15256 | 11.5677 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24727 | 0.045794 | 1.0803 | 1.0801 | 1.0801 | 1.0801 | 0.95782 | 0.14524 | 11.3795 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24727 | 0.045794 | 1.0801 | 1.0801 | 1.0801 | 1.0801 | 0.95782 | 0.14524 | 11.3795 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24727 | 0.045794 | 1.0801 | 1.0801 | 1.0801 | 1.0801 | 0.95782 | 0.14524 | 252 | 145.2384 | 0.95782 | 1.0801 | 0.0047333 | 11.3795
0.253 | 0.28632 | 0.04901 | 1.0872 | 1.0868 | 1.0868 | 1.0868 | 0.15348 | 11.5908 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24827 | 0.04583 | 1.0804 | 1.0802 | 1.0802 | 1.0802 | 0.95793 | 0.14613 | 11.4027 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24827 | 0.04583 | 1.0802 | 1.0802 | 1.0802 | 1.0802 | 0.95793 | 0.14613 | 11.4027 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24827 | 0.04583 | 1.0802 | 1.0802 | 1.0802 | 1.0802 | 0.95793 | 0.14613 | 253 | 146.1304 | 0.95793 | 1.0802 | 0.0047333 | 11.4027
0.254 | 0.28736 | 0.049041 | 1.0873 | 1.0869 | 1.0869 | 1.0869 | 0.1544 | 11.6139 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24927 | 0.045866 | 1.0805 | 1.0803 | 1.0803 | 1.0803 | 0.95804 | 0.14702 | 11.4259 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24927 | 0.045866 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 0.95804 | 0.14702 | 11.4259 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.24927 | 0.045866 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 0.95804 | 0.14702 | 254 | 147.0242 | 0.95804 | 1.0803 | 0.0047333 | 11.4259
0.255 | 0.2884 | 0.049071 | 1.0873 | 1.087 | 1.0869 | 1.0869 | 0.15532 | 11.637 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25027 | 0.045902 | 1.0805 | 1.0803 | 1.0803 | 1.0803 | 0.95815 | 0.14792 | 11.4491 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25027 | 0.045902 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 0.95815 | 0.14792 | 11.4491 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25027 | 0.045902 | 1.0803 | 1.0803 | 1.0803 | 1.0803 | 0.95815 | 0.14792 | 255 | 147.9198 | 0.95815 | 1.0803 | 0.0047333 | 11.4491
0.256 | 0.28944 | 0.049102 | 1.0874 | 1.087 | 1.087 | 1.087 | 0.15625 | 11.66 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25127 | 0.045937 | 1.0806 | 1.0804 | 1.0804 | 1.0804 | 0.95825 | 0.14882 | 11.4722 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25127 | 0.045937 | 1.0804 | 1.0804 | 1.0804 | 1.0804 | 0.95825 | 0.14882 | 11.4722 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25127 | 0.045937 | 1.0804 | 1.0804 | 1.0804 | 1.0804 | 0.95825 | 0.14882 | 256 | 148.8173 | 0.95825 | 1.0804 | 0.0047333 | 11.4722
0.257 | 0.29049 | 0.049132 | 1.0874 | 1.0871 | 1.0871 | 1.0871 | 0.15717 | 11.683 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25227 | 0.045972 | 1.0807 | 1.0805 | 1.0805 | 1.0805 | 0.95836 | 0.14972 | 11.4953 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25227 | 0.045972 | 1.0805 | 1.0805 | 1.0805 | 1.0805 | 0.95836 | 0.14972 | 11.4953 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25227 | 0.045972 | 1.0805 | 1.0805 | 1.0805 | 1.0805 | 0.95836 | 0.14972 | 257 | 149.7165 | 0.95836 | 1.0805 | 0.0047333 | 11.4953
0.258 | 0.29153 | 0.049162 | 1.0875 | 1.0871 | 1.0871 | 1.0871 | 0.1581 | 11.706 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25327 | 0.046007 | 1.0807 | 1.0806 | 1.0806 | 1.0806 | 0.95846 | 0.15062 | 11.5183 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25327 | 0.046007 | 1.0806 | 1.0806 | 1.0806 | 1.0806 | 0.95846 | 0.15062 | 11.5183 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25327 | 0.046007 | 1.0806 | 1.0806 | 1.0806 | 1.0806 | 0.95846 | 0.15062 | 258 | 150.6176 | 0.95846 | 1.0806 | 0.0047333 | 11.5183
0.259 | 0.29257 | 0.049192 | 1.0876 | 1.0872 | 1.0872 | 1.0872 | 0.15903 | 11.7288 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25427 | 0.046041 | 1.0808 | 1.0806 | 1.0806 | 1.0806 | 0.95857 | 0.15152 | 11.5412 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25427 | 0.046041 | 1.0806 | 1.0806 | 1.0806 | 1.0806 | 0.95857 | 0.15152 | 11.5412 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25427 | 0.046041 | 1.0806 | 1.0806 | 1.0806 | 1.0806 | 0.95857 | 0.15152 | 259 | 151.5205 | 0.95857 | 1.0806 | 0.0047333 | 11.5412
0.26 | 0.29361 | 0.049222 | 1.0876 | 1.0873 | 1.0873 | 1.0873 | 0.15996 | 11.7517 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25527 | 0.046076 | 1.0809 | 1.0807 | 1.0807 | 1.0807 | 0.95867 | 0.15243 | 11.5642 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25527 | 0.046076 | 1.0807 | 1.0807 | 1.0807 | 1.0807 | 0.95867 | 0.15243 | 11.5642 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25527 | 0.046076 | 1.0807 | 1.0807 | 1.0807 | 1.0807 | 0.95867 | 0.15243 | 260 | 152.4252 | 0.95867 | 1.0807 | 0.0047333 | 11.5642
0.261 | 0.29465 | 0.049251 | 1.0877 | 1.0873 | 1.0873 | 1.0873 | 0.16089 | 11.7745 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25627 | 0.04611 | 1.081 | 1.0808 | 1.0808 | 1.0808 | 0.95877 | 0.15333 | 11.5871 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25627 | 0.04611 | 1.0808 | 1.0808 | 1.0808 | 1.0808 | 0.95877 | 0.15333 | 11.5871 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25627 | 0.04611 | 1.0808 | 1.0808 | 1.0808 | 1.0808 | 0.95877 | 0.15333 | 261 | 153.3317 | 0.95877 | 1.0808 | 0.0047333 | 11.5871
0.262 | 0.29569 | 0.04928 | 1.0878 | 1.0874 | 1.0874 | 1.0874 | 0.16183 | 11.7973 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25727 | 0.046144 | 1.081 | 1.0808 | 1.0808 | 1.0808 | 0.95887 | 0.15424 | 11.6099 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25727 | 0.046144 | 1.0808 | 1.0808 | 1.0808 | 1.0808 | 0.95887 | 0.15424 | 11.6099 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25727 | 0.046144 | 1.0808 | 1.0808 | 1.0808 | 1.0808 | 0.95887 | 0.15424 | 262 | 154.2401 | 0.95887 | 1.0808 | 0.0047333 | 11.6099
0.263 | 0.29673 | 0.049309 | 1.0878 | 1.0875 | 1.0874 | 1.0874 | 0.16277 | 11.82 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25827 | 0.046177 | 1.0811 | 1.0809 | 1.0809 | 1.0809 | 0.95897 | 0.15515 | 11.6327 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25827 | 0.046177 | 1.0809 | 1.0809 | 1.0809 | 1.0809 | 0.95897 | 0.15515 | 11.6327 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25827 | 0.046177 | 1.0809 | 1.0809 | 1.0809 | 1.0809 | 0.95897 | 0.15515 | 263 | 155.1502 | 0.95897 | 1.0809 | 0.0047333 | 11.6327
0.264 | 0.29777 | 0.049338 | 1.0879 | 1.0875 | 1.0875 | 1.0875 | 0.1637 | 11.8426 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25927 | 0.046211 | 1.0812 | 1.081 | 1.081 | 1.081 | 0.95907 | 0.15606 | 11.6554 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25927 | 0.046211 | 1.081 | 1.081 | 1.081 | 1.081 | 0.95907 | 0.15606 | 11.6554 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.25927 | 0.046211 | 1.081 | 1.081 | 1.081 | 1.081 | 0.95907 | 0.15606 | 264 | 156.0621 | 0.95907 | 1.081 | 0.0047333 | 11.6554
0.265 | 0.29881 | 0.049367 | 1.0879 | 1.0876 | 1.0876 | 1.0876 | 0.16464 | 11.8653 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26027 | 0.046244 | 1.0812 | 1.0811 | 1.081 | 1.081 | 0.95917 | 0.15698 | 11.6781 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26027 | 0.046244 | 1.081 | 1.081 | 1.081 | 1.081 | 0.95917 | 0.15698 | 11.6781 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26027 | 0.046244 | 1.081 | 1.081 | 1.081 | 1.081 | 0.95917 | 0.15698 | 265 | 156.9758 | 0.95917 | 1.081 | 0.0047333 | 11.6781
0.266 | 0.29986 | 0.049395 | 1.088 | 1.0876 | 1.0876 | 1.0876 | 0.16559 | 11.8879 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26127 | 0.046277 | 1.0813 | 1.0811 | 1.0811 | 1.0811 | 0.95927 | 0.15789 | 11.7008 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26127 | 0.046277 | 1.0811 | 1.0811 | 1.0811 | 1.0811 | 0.95927 | 0.15789 | 11.7008 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26127 | 0.046277 | 1.0811 | 1.0811 | 1.0811 | 1.0811 | 0.95927 | 0.15789 | 266 | 157.8913 | 0.95927 | 1.0811 | 0.0047333 | 11.7008
0.267 | 0.3009 | 0.049423 | 1.088 | 1.0877 | 1.0877 | 1.0877 | 0.16653 | 11.9104 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26227 | 0.04631 | 1.0814 | 1.0812 | 1.0812 | 1.0812 | 0.95937 | 0.15881 | 11.7234 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26227 | 0.04631 | 1.0812 | 1.0812 | 1.0812 | 1.0812 | 0.95937 | 0.15881 | 11.7234 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26227 | 0.04631 | 1.0812 | 1.0812 | 1.0812 | 1.0812 | 0.95937 | 0.15881 | 267 | 158.8086 | 0.95937 | 1.0812 | 0.0047333 | 11.7234
0.268 | 0.30194 | 0.049452 | 1.0881 | 1.0878 | 1.0877 | 1.0877 | 0.16748 | 11.9329 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26327 | 0.046342 | 1.0814 | 1.0813 | 1.0812 | 1.0812 | 0.95946 | 0.15973 | 11.746 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26327 | 0.046342 | 1.0812 | 1.0812 | 1.0812 | 1.0812 | 0.95946 | 0.15973 | 11.746 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26327 | 0.046342 | 1.0812 | 1.0812 | 1.0812 | 1.0812 | 0.95946 | 0.15973 | 268 | 159.7277 | 0.95946 | 1.0812 | 0.0047333 | 11.746
0.269 | 0.30298 | 0.049479 | 1.0882 | 1.0878 | 1.0878 | 1.0878 | 0.16842 | 11.9554 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26427 | 0.046375 | 1.0815 | 1.0813 | 1.0813 | 1.0813 | 0.95956 | 0.16065 | 11.7685 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26427 | 0.046375 | 1.0813 | 1.0813 | 1.0813 | 1.0813 | 0.95956 | 0.16065 | 11.7685 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26427 | 0.046375 | 1.0813 | 1.0813 | 1.0813 | 1.0813 | 0.95956 | 0.16065 | 269 | 160.6485 | 0.95956 | 1.0813 | 0.0047333 | 11.7685
0.27 | 0.30402 | 0.049507 | 1.0882 | 1.0879 | 1.0879 | 1.0879 | 0.16937 | 11.9778 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26527 | 0.046407 | 1.0816 | 1.0814 | 1.0814 | 1.0814 | 0.95966 | 0.16157 | 11.791 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26527 | 0.046407 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 0.95966 | 0.16157 | 11.791 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26527 | 0.046407 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 0.95966 | 0.16157 | 270 | 161.5711 | 0.95966 | 1.0814 | 0.0047333 | 11.791
0.271 | 0.30506 | 0.049535 | 1.0883 | 1.0879 | 1.0879 | 1.0879 | 0.17032 | 12.0001 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.26617 | 0.046375 | 1.0815 | 1.0813 | 1.0813 | 1.0813 | 0.95891 | 0.16233 | 11.8095 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26627 | 0.046439 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 0.95975 | 0.1625 | 11.8134 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26627 | 0.046439 | 1.0814 | 1.0814 | 1.0814 | 1.0814 | 0.95975 | 0.1625 | 271 | 162.4955 | 0.95975 | 1.0814 | 0.0047333 | 11.8134
0.272 | 0.3061 | 0.049562 | 1.0883 | 1.088 | 1.088 | 1.088 | 0.17128 | 12.0225 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.26717 | 0.046407 | 1.0816 | 1.0814 | 1.0814 | 1.0814 | 0.95901 | 0.16326 | 11.8319 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26727 | 0.04647 | 1.0815 | 1.0815 | 1.0815 | 1.0815 | 0.95985 | 0.16342 | 11.8358 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26727 | 0.04647 | 1.0815 | 1.0815 | 1.0815 | 1.0815 | 0.95985 | 0.16342 | 272 | 163.4217 | 0.95985 | 1.0815 | 0.0047333 | 11.8358
0.273 | 0.30714 | 0.049589 | 1.0884 | 1.088 | 1.088 | 1.088 | 0.17223 | 12.0448 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.26817 | 0.046438 | 1.0816 | 1.0815 | 1.0814 | 1.0814 | 0.9591 | 0.16419 | 11.8543 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26827 | 0.046502 | 1.0816 | 1.0816 | 1.0816 | 1.0816 | 0.95994 | 0.16435 | 11.8582 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26827 | 0.046502 | 1.0816 | 1.0816 | 1.0816 | 1.0816 | 0.95994 | 0.16435 | 273 | 164.3496 | 0.95994 | 1.0816 | 0.0047333 | 11.8582
0.274 | 0.30819 | 0.049616 | 1.0884 | 1.0881 | 1.0881 | 1.0881 | 0.17319 | 12.067 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.26917 | 0.04647 | 1.0817 | 1.0815 | 1.0815 | 1.0815 | 0.9592 | 0.16512 | 11.8766 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26927 | 0.046533 | 1.0816 | 1.0816 | 1.0816 | 1.0816 | 0.96003 | 0.16528 | 11.8805 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.26927 | 0.046533 | 1.0816 | 1.0816 | 1.0816 | 1.0816 | 0.96003 | 0.16528 | 274 | 165.2793 | 0.96003 | 1.0816 | 0.0047333 | 11.8805
0.275 | 0.30923 | 0.049643 | 1.0885 | 1.0882 | 1.0881 | 1.0881 | 0.17414 | 12.0892 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27017 | 0.046501 | 1.0818 | 1.0816 | 1.0816 | 1.0816 | 0.95929 | 0.16605 | 11.8989 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27027 | 0.046564 | 1.0817 | 1.0817 | 1.0817 | 1.0817 | 0.96012 | 0.16621 | 11.9028 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27027 | 0.046564 | 1.0817 | 1.0817 | 1.0817 | 1.0817 | 0.96012 | 0.16621 | 275 | 166.2108 | 0.96012 | 1.0817 | 0.0047333 | 11.9028
0.276 | 0.31027 | 0.04967 | 1.0886 | 1.0882 | 1.0882 | 1.0882 | 0.1751 | 12.1114 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27117 | 0.046532 | 1.0818 | 1.0816 | 1.0816 | 1.0816 | 0.95938 | 0.16698 | 11.9211 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27127 | 0.046595 | 1.0818 | 1.0818 | 1.0818 | 1.0818 | 0.96021 | 0.16714 | 11.925 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27127 | 0.046595 | 1.0818 | 1.0818 | 1.0818 | 1.0818 | 0.96021 | 0.16714 | 276 | 167.144 | 0.96021 | 1.0818 | 0.0047333 | 11.925
0.277 | 0.31131 | 0.049696 | 1.0886 | 1.0883 | 1.0883 | 1.0883 | 0.17607 | 12.1335 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27217 | 0.046563 | 1.0819 | 1.0817 | 1.0817 | 1.0817 | 0.95948 | 0.16791 | 11.9433 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27227 | 0.046626 | 1.0818 | 1.0818 | 1.0818 | 1.0818 | 0.96031 | 0.16808 | 11.9472 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27227 | 0.046626 | 1.0818 | 1.0818 | 1.0818 | 1.0818 | 0.96031 | 0.16808 | 277 | 168.0789 | 0.96031 | 1.0818 | 0.0047333 | 11.9472
0.278 | 0.31235 | 0.049723 | 1.0887 | 1.0883 | 1.0883 | 1.0883 | 0.17703 | 12.1556 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27317 | 0.046593 | 1.082 | 1.0818 | 1.0818 | 1.0818 | 0.95957 | 0.16885 | 11.9655 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27327 | 0.046656 | 1.0819 | 1.0819 | 1.0819 | 1.0819 | 0.9604 | 0.16902 | 11.9694 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27327 | 0.046656 | 1.0819 | 1.0819 | 1.0819 | 1.0819 | 0.9604 | 0.16902 | 278 | 169.0156 | 0.9604 | 1.0819 | 0.0047333 | 11.9694
0.279 | 0.31339 | 0.049749 | 1.0887 | 1.0884 | 1.0884 | 1.0884 | 0.17799 | 12.1777 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27417 | 0.046624 | 1.082 | 1.0818 | 1.0818 | 1.0818 | 0.95966 | 0.16979 | 11.9876 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27427 | 0.046687 | 1.082 | 1.082 | 1.082 | 1.082 | 0.96049 | 0.16995 | 11.9915 | 0.0054 | 0.0044 | 0.0047333 | 0.64145 | 0.27427 | 0.046687 | 1.082 | 1.082 | 1.082 | 1.082 | 0.96049 | 0.16995 | 279 | 169.9541 | 0.96049 | 1.082 | 0.0047333 | 11.9915
0.28 | 0.31443 | 0.049775 | 1.0888 | 1.0884 | 1.0884 | 1.0884 | 0.17896 | 12.1997 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27517 | 0.046654 | 1.0821 | 1.0819 | 1.0819 | 1.0819 | 0.95975 | 0.17073 | 12.0096 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27517 | 0.046654 | 1.0819 | 1.0819 | 1.0819 | 1.0819 | 0.95975 | 0.17073 | 12.0096 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27517 | 0.046654 | 1.0819 | 1.0819 | 1.0819 | 1.0819 | 0.95975 | 0.17073 | 280 | 170.7273 | 0.95975 | 1.0819 | 0.0048333 | 12.0096
0.281 | 0.31547 | 0.049801 | 1.0888 | 1.0885 | 1.0885 | 1.0885 | 0.17993 | 12.2217 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27617 | 0.046684 | 1.0821 | 1.082 | 1.082 | 1.082 | 0.95984 | 0.17167 | 12.0317 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27617 | 0.046684 | 1.082 | 1.082 | 1.082 | 1.082 | 0.95984 | 0.17167 | 12.0317 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27617 | 0.046684 | 1.082 | 1.082 | 1.082 | 1.082 | 0.95984 | 0.17167 | 281 | 171.6687 | 0.95984 | 1.082 | 0.0048333 | 12.0317
0.282 | 0.31651 | 0.049826 | 1.0889 | 1.0885 | 1.0885 | 1.0885 | 0.1809 | 12.2436 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27717 | 0.046714 | 1.0822 | 1.082 | 1.082 | 1.082 | 0.95993 | 0.17261 | 12.0537 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27717 | 0.046714 | 1.082 | 1.082 | 1.082 | 1.082 | 0.95993 | 0.17261 | 12.0537 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27717 | 0.046714 | 1.082 | 1.082 | 1.082 | 1.082 | 0.95993 | 0.17261 | 282 | 172.6118 | 0.95993 | 1.082 | 0.0048333 | 12.0537
0.283 | 0.31756 | 0.049852 | 1.0889 | 1.0886 | 1.0886 | 1.0886 | 0.18187 | 12.2655 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27817 | 0.046743 | 1.0823 | 1.0821 | 1.0821 | 1.0821 | 0.96002 | 0.17356 | 12.0756 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27817 | 0.046743 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 0.96002 | 0.17356 | 12.0756 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27817 | 0.046743 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 0.96002 | 0.17356 | 283 | 173.5567 | 0.96002 | 1.0821 | 0.0048333 | 12.0756
0.284 | 0.3186 | 0.049877 | 1.089 | 1.0887 | 1.0886 | 1.0886 | 0.18285 | 12.2873 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27917 | 0.046773 | 1.0823 | 1.0821 | 1.0821 | 1.0821 | 0.96011 | 0.1745 | 12.0975 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27917 | 0.046773 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 0.96011 | 0.1745 | 12.0975 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.27917 | 0.046773 | 1.0821 | 1.0821 | 1.0821 | 1.0821 | 0.96011 | 0.1745 | 284 | 174.5032 | 0.96011 | 1.0821 | 0.0048333 | 12.0975
0.285 | 0.31964 | 0.049902 | 1.089 | 1.0887 | 1.0887 | 1.0887 | 0.18382 | 12.3091 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28017 | 0.046802 | 1.0824 | 1.0822 | 1.0822 | 1.0822 | 0.96019 | 0.17545 | 12.1194 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28017 | 0.046802 | 1.0822 | 1.0822 | 1.0822 | 1.0822 | 0.96019 | 0.17545 | 12.1194 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28017 | 0.046802 | 1.0822 | 1.0822 | 1.0822 | 1.0822 | 0.96019 | 0.17545 | 285 | 175.4515 | 0.96019 | 1.0822 | 0.0048333 | 12.1194
0.286 | 0.32068 | 0.049927 | 1.0891 | 1.0888 | 1.0887 | 1.0887 | 0.1848 | 12.3309 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28117 | 0.046831 | 1.0824 | 1.0823 | 1.0823 | 1.0823 | 0.96028 | 0.1764 | 12.1412 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28117 | 0.046831 | 1.0823 | 1.0823 | 1.0823 | 1.0823 | 0.96028 | 0.1764 | 12.1412 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28117 | 0.046831 | 1.0823 | 1.0823 | 1.0823 | 1.0823 | 0.96028 | 0.1764 | 286 | 176.4016 | 0.96028 | 1.0823 | 0.0048333 | 12.1412
0.287 | 0.32172 | 0.049952 | 1.0891 | 1.0888 | 1.0888 | 1.0888 | 0.18578 | 12.3527 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28217 | 0.04686 | 1.0825 | 1.0823 | 1.0823 | 1.0823 | 0.96037 | 0.17735 | 12.163 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28217 | 0.04686 | 1.0823 | 1.0823 | 1.0823 | 1.0823 | 0.96037 | 0.17735 | 12.163 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28217 | 0.04686 | 1.0823 | 1.0823 | 1.0823 | 1.0823 | 0.96037 | 0.17735 | 287 | 177.3533 | 0.96037 | 1.0823 | 0.0048333 | 12.163
0.288 | 0.32276 | 0.049977 | 1.0892 | 1.0889 | 1.0889 | 1.0889 | 0.18676 | 12.3744 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28317 | 0.046889 | 1.0826 | 1.0824 | 1.0824 | 1.0824 | 0.96045 | 0.17831 | 12.1848 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28317 | 0.046889 | 1.0824 | 1.0824 | 1.0824 | 1.0824 | 0.96045 | 0.17831 | 12.1848 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28317 | 0.046889 | 1.0824 | 1.0824 | 1.0824 | 1.0824 | 0.96045 | 0.17831 | 288 | 178.3068 | 0.96045 | 1.0824 | 0.0048333 | 12.1848
0.289 | 0.3238 | 0.050001 | 1.0892 | 1.0889 | 1.0889 | 1.0889 | 0.18774 | 12.396 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28417 | 0.046918 | 1.0826 | 1.0824 | 1.0824 | 1.0824 | 0.96054 | 0.17926 | 12.2065 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28417 | 0.046918 | 1.0824 | 1.0824 | 1.0824 | 1.0824 | 0.96054 | 0.17926 | 12.2065 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28417 | 0.046918 | 1.0824 | 1.0824 | 1.0824 | 1.0824 | 0.96054 | 0.17926 | 289 | 179.2619 | 0.96054 | 1.0824 | 0.0048333 | 12.2065
0.29 | 0.32484 | 0.050026 | 1.0893 | 1.089 | 1.089 | 1.089 | 0.18873 | 12.4176 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28517 | 0.046946 | 1.0827 | 1.0825 | 1.0825 | 1.0825 | 0.96062 | 0.18022 | 12.2282 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28517 | 0.046946 | 1.0825 | 1.0825 | 1.0825 | 1.0825 | 0.96062 | 0.18022 | 12.2282 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28517 | 0.046946 | 1.0825 | 1.0825 | 1.0825 | 1.0825 | 0.96062 | 0.18022 | 290 | 180.2188 | 0.96062 | 1.0825 | 0.0048333 | 12.2282
0.291 | 0.32589 | 0.05005 | 1.0893 | 1.089 | 1.089 | 1.089 | 0.18971 | 12.4392 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28617 | 0.046974 | 1.0827 | 1.0826 | 1.0826 | 1.0826 | 0.96071 | 0.18118 | 12.2498 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28617 | 0.046974 | 1.0826 | 1.0826 | 1.0826 | 1.0826 | 0.96071 | 0.18118 | 12.2498 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28617 | 0.046974 | 1.0826 | 1.0826 | 1.0826 | 1.0826 | 0.96071 | 0.18118 | 291 | 181.1774 | 0.96071 | 1.0826 | 0.0048333 | 12.2498
0.292 | 0.32693 | 0.050074 | 1.0894 | 1.0891 | 1.0891 | 1.0891 | 0.1907 | 12.4608 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28717 | 0.047002 | 1.0828 | 1.0826 | 1.0826 | 1.0826 | 0.96079 | 0.18214 | 12.2714 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28717 | 0.047002 | 1.0826 | 1.0826 | 1.0826 | 1.0826 | 0.96079 | 0.18214 | 12.2714 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28717 | 0.047002 | 1.0826 | 1.0826 | 1.0826 | 1.0826 | 0.96079 | 0.18214 | 292 | 182.1377 | 0.96079 | 1.0826 | 0.0048333 | 12.2714
0.293 | 0.32797 | 0.050098 | 1.0894 | 1.0891 | 1.0891 | 1.0891 | 0.19169 | 12.4823 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28817 | 0.04703 | 1.0829 | 1.0827 | 1.0827 | 1.0827 | 0.96087 | 0.1831 | 12.293 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28817 | 0.04703 | 1.0827 | 1.0827 | 1.0827 | 1.0827 | 0.96087 | 0.1831 | 12.293 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28817 | 0.04703 | 1.0827 | 1.0827 | 1.0827 | 1.0827 | 0.96087 | 0.1831 | 293 | 183.0997 | 0.96087 | 1.0827 | 0.0048333 | 12.293
0.294 | 0.32901 | 0.050122 | 1.0895 | 1.0892 | 1.0892 | 1.0892 | 0.19268 | 12.5038 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28917 | 0.047058 | 1.0829 | 1.0827 | 1.0827 | 1.0827 | 0.96096 | 0.18406 | 12.3145 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28917 | 0.047058 | 1.0827 | 1.0827 | 1.0827 | 1.0827 | 0.96096 | 0.18406 | 12.3145 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.28917 | 0.047058 | 1.0827 | 1.0827 | 1.0827 | 1.0827 | 0.96096 | 0.18406 | 294 | 184.0634 | 0.96096 | 1.0827 | 0.0048333 | 12.3145
0.295 | 0.33005 | 0.050146 | 1.0895 | 1.0892 | 1.0892 | 1.0892 | 0.19367 | 12.5252 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29017 | 0.047085 | 1.083 | 1.0828 | 1.0828 | 1.0828 | 0.96104 | 0.18503 | 12.336 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29017 | 0.047085 | 1.0828 | 1.0828 | 1.0828 | 1.0828 | 0.96104 | 0.18503 | 12.336 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29017 | 0.047085 | 1.0828 | 1.0828 | 1.0828 | 1.0828 | 0.96104 | 0.18503 | 295 | 185.0288 | 0.96104 | 1.0828 | 0.0048333 | 12.336
0.296 | 0.33109 | 0.050169 | 1.0896 | 1.0893 | 1.0893 | 1.0893 | 0.19467 | 12.5466 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29117 | 0.047113 | 1.083 | 1.0828 | 1.0828 | 1.0828 | 0.96112 | 0.186 | 12.3575 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29117 | 0.047113 | 1.0828 | 1.0828 | 1.0828 | 1.0828 | 0.96112 | 0.186 | 12.3575 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29117 | 0.047113 | 1.0828 | 1.0828 | 1.0828 | 1.0828 | 0.96112 | 0.186 | 296 | 185.9958 | 0.96112 | 1.0828 | 0.0048333 | 12.3575
0.297 | 0.33213 | 0.050192 | 1.0896 | 1.0893 | 1.0893 | 1.0893 | 0.19566 | 12.568 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29217 | 0.04714 | 1.0831 | 1.0829 | 1.0829 | 1.0829 | 0.9612 | 0.18696 | 12.3789 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29217 | 0.04714 | 1.0829 | 1.0829 | 1.0829 | 1.0829 | 0.9612 | 0.18696 | 12.3789 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29217 | 0.04714 | 1.0829 | 1.0829 | 1.0829 | 1.0829 | 0.9612 | 0.18696 | 297 | 186.9646 | 0.9612 | 1.0829 | 0.0048333 | 12.3789
0.298 | 0.33317 | 0.050216 | 1.0897 | 1.0894 | 1.0894 | 1.0894 | 0.19666 | 12.5893 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29317 | 0.047167 | 1.0831 | 1.083 | 1.083 | 1.083 | 0.96128 | 0.18794 | 12.4003 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29317 | 0.047167 | 1.083 | 1.083 | 1.083 | 1.083 | 0.96128 | 0.18794 | 12.4003 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29317 | 0.047167 | 1.083 | 1.083 | 1.083 | 1.083 | 0.96128 | 0.18794 | 298 | 187.9351 | 0.96128 | 1.083 | 0.0048333 | 12.4003
0.299 | 0.33421 | 0.050239 | 1.0897 | 1.0894 | 1.0894 | 1.0894 | 0.19766 | 12.6106 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29417 | 0.047194 | 1.0832 | 1.083 | 1.083 | 1.083 | 0.96136 | 0.18891 | 12.4216 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29417 | 0.047194 | 1.083 | 1.083 | 1.083 | 1.083 | 0.96136 | 0.18891 | 12.4216 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29417 | 0.047194 | 1.083 | 1.083 | 1.083 | 1.083 | 0.96136 | 0.18891 | 299 | 188.9072 | 0.96136 | 1.083 | 0.0048333 | 12.4216
0.3 | 0.33526 | 0.050262 | 1.0898 | 1.0895 | 1.0895 | 1.0895 | 0.19866 | 12.6319 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29517 | 0.047221 | 1.0833 | 1.0831 | 1.0831 | 1.0831 | 0.96144 | 0.18988 | 12.4429 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29517 | 0.047221 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 0.96144 | 0.18988 | 12.4429 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29517 | 0.047221 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 0.96144 | 0.18988 | 300 | 189.881 | 0.96144 | 1.0831 | 0.0048333 | 12.4429
0.301 | 0.3363 | 0.050285 | 1.0898 | 1.0895 | 1.0895 | 1.0895 | 0.19967 | 12.6531 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29617 | 0.047247 | 1.0833 | 1.0831 | 1.0831 | 1.0831 | 0.96152 | 0.19086 | 12.4642 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29617 | 0.047247 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 0.96152 | 0.19086 | 12.4642 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29617 | 0.047247 | 1.0831 | 1.0831 | 1.0831 | 1.0831 | 0.96152 | 0.19086 | 301 | 190.8565 | 0.96152 | 1.0831 | 0.0048333 | 12.4642
0.302 | 0.33734 | 0.050307 | 1.0899 | 1.0896 | 1.0896 | 1.0896 | 0.20067 | 12.6743 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29717 | 0.047274 | 1.0834 | 1.0832 | 1.0832 | 1.0832 | 0.96159 | 0.19183 | 12.4854 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29717 | 0.047274 | 1.0832 | 1.0832 | 1.0832 | 1.0832 | 0.96159 | 0.19183 | 12.4854 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29717 | 0.047274 | 1.0832 | 1.0832 | 1.0832 | 1.0832 | 0.96159 | 0.19183 | 302 | 191.8337 | 0.96159 | 1.0832 | 0.0048333 | 12.4854
0.303 | 0.33838 | 0.05033 | 1.0899 | 1.0896 | 1.0896 | 1.0896 | 0.20168 | 12.6954 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29817 | 0.0473 | 1.0834 | 1.0832 | 1.0832 | 1.0832 | 0.96167 | 0.19281 | 12.5066 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29817 | 0.0473 | 1.0832 | 1.0832 | 1.0832 | 1.0832 | 0.96167 | 0.19281 | 12.5066 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29817 | 0.0473 | 1.0832 | 1.0832 | 1.0832 | 1.0832 | 0.96167 | 0.19281 | 303 | 192.8125 | 0.96167 | 1.0832 | 0.0048333 | 12.5066
0.304 | 0.33942 | 0.050352 | 1.09 | 1.0897 | 1.0897 | 1.0897 | 0.20269 | 12.7166 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29917 | 0.047326 | 1.0835 | 1.0833 | 1.0833 | 1.0833 | 0.96175 | 0.19379 | 12.5278 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29917 | 0.047326 | 1.0833 | 1.0833 | 1.0833 | 1.0833 | 0.96175 | 0.19379 | 12.5278 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.29917 | 0.047326 | 1.0833 | 1.0833 | 1.0833 | 1.0833 | 0.96175 | 0.19379 | 304 | 193.793 | 0.96175 | 1.0833 | 0.0048333 | 12.5278
0.305 | 0.34046 | 0.050374 | 1.09 | 1.0897 | 1.0897 | 1.0897 | 0.20369 | 12.7376 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30017 | 0.047352 | 1.0835 | 1.0833 | 1.0833 | 1.0833 | 0.96182 | 0.19478 | 12.5489 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30017 | 0.047352 | 1.0833 | 1.0833 | 1.0833 | 1.0833 | 0.96182 | 0.19478 | 12.5489 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30017 | 0.047352 | 1.0833 | 1.0833 | 1.0833 | 1.0833 | 0.96182 | 0.19478 | 305 | 194.7752 | 0.96182 | 1.0833 | 0.0048333 | 12.5489
0.306 | 0.3415 | 0.050397 | 1.0901 | 1.0898 | 1.0897 | 1.0897 | 0.20471 | 12.7587 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30117 | 0.047378 | 1.0836 | 1.0834 | 1.0834 | 1.0834 | 0.9619 | 0.19576 | 12.57 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30117 | 0.047378 | 1.0834 | 1.0834 | 1.0834 | 1.0834 | 0.9619 | 0.19576 | 12.57 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30117 | 0.047378 | 1.0834 | 1.0834 | 1.0834 | 1.0834 | 0.9619 | 0.19576 | 306 | 195.7591 | 0.9619 | 1.0834 | 0.0048333 | 12.57
0.307 | 0.34254 | 0.050419 | 1.0901 | 1.0898 | 1.0898 | 1.0898 | 0.20572 | 12.7797 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30217 | 0.047404 | 1.0836 | 1.0835 | 1.0834 | 1.0834 | 0.96198 | 0.19674 | 12.5911 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30217 | 0.047404 | 1.0834 | 1.0834 | 1.0834 | 1.0834 | 0.96198 | 0.19674 | 12.5911 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30217 | 0.047404 | 1.0834 | 1.0834 | 1.0834 | 1.0834 | 0.96198 | 0.19674 | 307 | 196.7446 | 0.96198 | 1.0834 | 0.0048333 | 12.5911
0.308 | 0.34359 | 0.050441 | 1.0902 | 1.0899 | 1.0898 | 1.0898 | 0.20673 | 12.8007 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30317 | 0.047429 | 1.0837 | 1.0835 | 1.0835 | 1.0835 | 0.96205 | 0.19773 | 12.6121 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30317 | 0.047429 | 1.0835 | 1.0835 | 1.0835 | 1.0835 | 0.96205 | 0.19773 | 12.6121 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30317 | 0.047429 | 1.0835 | 1.0835 | 1.0835 | 1.0835 | 0.96205 | 0.19773 | 308 | 197.7317 | 0.96205 | 1.0835 | 0.0048333 | 12.6121
0.309 | 0.34463 | 0.050462 | 1.0902 | 1.0899 | 1.0899 | 1.0899 | 0.20775 | 12.8216 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30417 | 0.047455 | 1.0837 | 1.0836 | 1.0836 | 1.0836 | 0.96213 | 0.19872 | 12.6331 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30417 | 0.047455 | 1.0836 | 1.0836 | 1.0836 | 1.0836 | 0.96213 | 0.19872 | 12.6331 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30417 | 0.047455 | 1.0836 | 1.0836 | 1.0836 | 1.0836 | 0.96213 | 0.19872 | 309 | 198.7206 | 0.96213 | 1.0836 | 0.0048333 | 12.6331
0.31 | 0.34567 | 0.050484 | 1.0902 | 1.0899 | 1.0899 | 1.0899 | 0.20877 | 12.8425 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30517 | 0.04748 | 1.0838 | 1.0836 | 1.0836 | 1.0836 | 0.9622 | 0.19971 | 12.6541 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30517 | 0.04748 | 1.0836 | 1.0836 | 1.0836 | 1.0836 | 0.9622 | 0.19971 | 12.6541 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30517 | 0.04748 | 1.0836 | 1.0836 | 1.0836 | 1.0836 | 0.9622 | 0.19971 | 310 | 199.711 | 0.9622 | 1.0836 | 0.0048333 | 12.6541
0.311 | 0.34671 | 0.050506 | 1.0903 | 1.09 | 1.09 | 1.09 | 0.20979 | 12.8634 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30617 | 0.047505 | 1.0838 | 1.0837 | 1.0837 | 1.0837 | 0.96227 | 0.2007 | 12.675 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30617 | 0.047505 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 0.96227 | 0.2007 | 12.675 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30617 | 0.047505 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 0.96227 | 0.2007 | 311 | 200.7031 | 0.96227 | 1.0837 | 0.0048333 | 12.675
0.312 | 0.34775 | 0.050527 | 1.0903 | 1.09 | 1.09 | 1.09 | 0.21081 | 12.8843 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30717 | 0.04753 | 1.0839 | 1.0837 | 1.0837 | 1.0837 | 0.96235 | 0.2017 | 12.6959 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30717 | 0.04753 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 0.96235 | 0.2017 | 12.6959 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30717 | 0.04753 | 1.0837 | 1.0837 | 1.0837 | 1.0837 | 0.96235 | 0.2017 | 312 | 201.6969 | 0.96235 | 1.0837 | 0.0048333 | 12.6959
0.313 | 0.34879 | 0.050548 | 1.0904 | 1.0901 | 1.0901 | 1.0901 | 0.21183 | 12.9051 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30817 | 0.047555 | 1.0839 | 1.0838 | 1.0838 | 1.0838 | 0.96242 | 0.20269 | 12.7167 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30817 | 0.047555 | 1.0838 | 1.0838 | 1.0838 | 1.0838 | 0.96242 | 0.20269 | 12.7167 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30817 | 0.047555 | 1.0838 | 1.0838 | 1.0838 | 1.0838 | 0.96242 | 0.20269 | 313 | 202.6923 | 0.96242 | 1.0838 | 0.0048333 | 12.7167
0.314 | 0.34983 | 0.050569 | 1.0904 | 1.0901 | 1.0901 | 1.0901 | 0.21286 | 12.9258 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30917 | 0.047579 | 1.084 | 1.0838 | 1.0838 | 1.0838 | 0.96249 | 0.20369 | 12.7375 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30917 | 0.047579 | 1.0838 | 1.0838 | 1.0838 | 1.0838 | 0.96249 | 0.20369 | 12.7375 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.30917 | 0.047579 | 1.0838 | 1.0838 | 1.0838 | 1.0838 | 0.96249 | 0.20369 | 314 | 203.6894 | 0.96249 | 1.0838 | 0.0048333 | 12.7375
0.315 | 0.35087 | 0.05059 | 1.0905 | 1.0902 | 1.0902 | 1.0902 | 0.21388 | 12.9466 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31017 | 0.047604 | 1.084 | 1.0839 | 1.0839 | 1.0839 | 0.96256 | 0.20469 | 12.7583 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31017 | 0.047604 | 1.0839 | 1.0839 | 1.0839 | 1.0839 | 0.96256 | 0.20469 | 12.7583 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31017 | 0.047604 | 1.0839 | 1.0839 | 1.0839 | 1.0839 | 0.96256 | 0.20469 | 315 | 204.6881 | 0.96256 | 1.0839 | 0.0048333 | 12.7583
0.316 | 0.35191 | 0.050611 | 1.0905 | 1.0902 | 1.0902 | 1.0902 | 0.21491 | 12.9673 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31117 | 0.047628 | 1.0841 | 1.0839 | 1.0839 | 1.0839 | 0.96263 | 0.20569 | 12.7791 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31117 | 0.047628 | 1.0839 | 1.0839 | 1.0839 | 1.0839 | 0.96263 | 0.20569 | 12.7791 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31117 | 0.047628 | 1.0839 | 1.0839 | 1.0839 | 1.0839 | 0.96263 | 0.20569 | 316 | 205.6884 | 0.96263 | 1.0839 | 0.0048333 | 12.7791
0.317 | 0.35296 | 0.050632 | 1.0906 | 1.0903 | 1.0903 | 1.0903 | 0.21594 | 12.988 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31217 | 0.047652 | 1.0841 | 1.084 | 1.084 | 1.084 | 0.9627 | 0.20669 | 12.7998 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31217 | 0.047652 | 1.084 | 1.084 | 1.084 | 1.084 | 0.9627 | 0.20669 | 12.7998 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31217 | 0.047652 | 1.084 | 1.084 | 1.084 | 1.084 | 0.9627 | 0.20669 | 317 | 206.6903 | 0.9627 | 1.084 | 0.0048333 | 12.7998
0.318 | 0.354 | 0.050653 | 1.0906 | 1.0903 | 1.0903 | 1.0903 | 0.21697 | 13.0086 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31317 | 0.047676 | 1.0842 | 1.084 | 1.084 | 1.084 | 0.96277 | 0.20769 | 12.8205 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31317 | 0.047676 | 1.084 | 1.084 | 1.084 | 1.084 | 0.96277 | 0.20769 | 12.8205 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31317 | 0.047676 | 1.084 | 1.084 | 1.084 | 1.084 | 0.96277 | 0.20769 | 318 | 207.6939 | 0.96277 | 1.084 | 0.0048333 | 12.8205
0.319 | 0.35504 | 0.050673 | 1.0906 | 1.0903 | 1.0903 | 1.0903 | 0.21801 | 13.0292 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31417 | 0.0477 | 1.0842 | 1.0841 | 1.0841 | 1.0841 | 0.96284 | 0.2087 | 12.8411 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31417 | 0.0477 | 1.0841 | 1.0841 | 1.0841 | 1.0841 | 0.96284 | 0.2087 | 12.8411 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31417 | 0.0477 | 1.0841 | 1.0841 | 1.0841 | 1.0841 | 0.96284 | 0.2087 | 319 | 208.6992 | 0.96284 | 1.0841 | 0.0048333 | 12.8411
0.32 | 0.35608 | 0.050694 | 1.0907 | 1.0904 | 1.0904 | 1.0904 | 0.21904 | 13.0498 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31517 | 0.047724 | 1.0843 | 1.0841 | 1.0841 | 1.0841 | 0.96291 | 0.20971 | 12.8617 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31517 | 0.047724 | 1.0841 | 1.0841 | 1.0841 | 1.0841 | 0.96291 | 0.20971 | 12.8617 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31517 | 0.047724 | 1.0841 | 1.0841 | 1.0841 | 1.0841 | 0.96291 | 0.20971 | 320 | 209.706 | 0.96291 | 1.0841 | 0.0048333 | 12.8617
0.321 | 0.35712 | 0.050714 | 1.0907 | 1.0904 | 1.0904 | 1.0904 | 0.22008 | 13.0704 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31617 | 0.047748 | 1.0843 | 1.0842 | 1.0842 | 1.0842 | 0.96298 | 0.21071 | 12.8823 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31617 | 0.047748 | 1.0842 | 1.0842 | 1.0842 | 1.0842 | 0.96298 | 0.21071 | 12.8823 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31617 | 0.047748 | 1.0842 | 1.0842 | 1.0842 | 1.0842 | 0.96298 | 0.21071 | 321 | 210.7145 | 0.96298 | 1.0842 | 0.0048333 | 12.8823
0.322 | 0.35816 | 0.050734 | 1.0908 | 1.0905 | 1.0905 | 1.0905 | 0.22112 | 13.0909 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31717 | 0.047771 | 1.0844 | 1.0842 | 1.0842 | 1.0842 | 0.96305 | 0.21172 | 12.9029 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31717 | 0.047771 | 1.0842 | 1.0842 | 1.0842 | 1.0842 | 0.96305 | 0.21172 | 12.9029 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31717 | 0.047771 | 1.0842 | 1.0842 | 1.0842 | 1.0842 | 0.96305 | 0.21172 | 322 | 211.7246 | 0.96305 | 1.0842 | 0.0048333 | 12.9029
0.323 | 0.3592 | 0.050754 | 1.0908 | 1.0905 | 1.0905 | 1.0905 | 0.22216 | 13.1114 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31817 | 0.047795 | 1.0844 | 1.0843 | 1.0843 | 1.0843 | 0.96312 | 0.21274 | 12.9234 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31817 | 0.047795 | 1.0843 | 1.0843 | 1.0843 | 1.0843 | 0.96312 | 0.21274 | 12.9234 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31817 | 0.047795 | 1.0843 | 1.0843 | 1.0843 | 1.0843 | 0.96312 | 0.21274 | 323 | 212.7363 | 0.96312 | 1.0843 | 0.0048333 | 12.9234
0.324 | 0.36024 | 0.050774 | 1.0909 | 1.0906 | 1.0906 | 1.0906 | 0.2232 | 13.1318 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31917 | 0.047818 | 1.0845 | 1.0843 | 1.0843 | 1.0843 | 0.96319 | 0.21375 | 12.9439 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31917 | 0.047818 | 1.0843 | 1.0843 | 1.0843 | 1.0843 | 0.96319 | 0.21375 | 12.9439 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.31917 | 0.047818 | 1.0843 | 1.0843 | 1.0843 | 1.0843 | 0.96319 | 0.21375 | 324 | 213.7496 | 0.96319 | 1.0843 | 0.0048333 | 12.9439
0.325 | 0.36128 | 0.050794 | 1.0909 | 1.0906 | 1.0906 | 1.0906 | 0.22424 | 13.1522 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32017 | 0.047841 | 1.0845 | 1.0844 | 1.0844 | 1.0844 | 0.96325 | 0.21476 | 12.9643 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32017 | 0.047841 | 1.0844 | 1.0844 | 1.0844 | 1.0844 | 0.96325 | 0.21476 | 12.9643 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32017 | 0.047841 | 1.0844 | 1.0844 | 1.0844 | 1.0844 | 0.96325 | 0.21476 | 325 | 214.7645 | 0.96325 | 1.0844 | 0.0048333 | 12.9643
0.326 | 0.36233 | 0.050814 | 1.0909 | 1.0906 | 1.0906 | 1.0906 | 0.22528 | 13.1726 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32117 | 0.047864 | 1.0846 | 1.0844 | 1.0844 | 1.0844 | 0.96332 | 0.21578 | 12.9847 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32117 | 0.047864 | 1.0844 | 1.0844 | 1.0844 | 1.0844 | 0.96332 | 0.21578 | 12.9847 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32117 | 0.047864 | 1.0844 | 1.0844 | 1.0844 | 1.0844 | 0.96332 | 0.21578 | 326 | 215.7811 | 0.96332 | 1.0844 | 0.0048333 | 12.9847
0.327 | 0.36337 | 0.050834 | 1.091 | 1.0907 | 1.0907 | 1.0907 | 0.22633 | 13.193 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32217 | 0.047887 | 1.0846 | 1.0845 | 1.0845 | 1.0845 | 0.96339 | 0.2168 | 13.0051 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32217 | 0.047887 | 1.0845 | 1.0845 | 1.0845 | 1.0845 | 0.96339 | 0.2168 | 13.0051 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32217 | 0.047887 | 1.0845 | 1.0845 | 1.0845 | 1.0845 | 0.96339 | 0.2168 | 327 | 216.7992 | 0.96339 | 1.0845 | 0.0048333 | 13.0051
0.328 | 0.36441 | 0.050853 | 1.091 | 1.0907 | 1.0907 | 1.0907 | 0.22738 | 13.2133 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32317 | 0.04791 | 1.0847 | 1.0845 | 1.0845 | 1.0845 | 0.96345 | 0.21782 | 13.0255 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32317 | 0.04791 | 1.0845 | 1.0845 | 1.0845 | 1.0845 | 0.96345 | 0.21782 | 13.0255 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32317 | 0.04791 | 1.0845 | 1.0845 | 1.0845 | 1.0845 | 0.96345 | 0.21782 | 328 | 217.819 | 0.96345 | 1.0845 | 0.0048333 | 13.0255
0.329 | 0.36545 | 0.050873 | 1.0911 | 1.0908 | 1.0908 | 1.0908 | 0.22843 | 13.2336 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32417 | 0.047933 | 1.0847 | 1.0846 | 1.0846 | 1.0846 | 0.96352 | 0.21884 | 13.0458 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32417 | 0.047933 | 1.0846 | 1.0846 | 1.0846 | 1.0846 | 0.96352 | 0.21884 | 13.0458 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32417 | 0.047933 | 1.0846 | 1.0846 | 1.0846 | 1.0846 | 0.96352 | 0.21884 | 329 | 218.8403 | 0.96352 | 1.0846 | 0.0048333 | 13.0458
0.33 | 0.36649 | 0.050892 | 1.0911 | 1.0908 | 1.0908 | 1.0908 | 0.22948 | 13.2539 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32517 | 0.047955 | 1.0848 | 1.0846 | 1.0846 | 1.0846 | 0.96359 | 0.21986 | 13.0661 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32517 | 0.047955 | 1.0846 | 1.0846 | 1.0846 | 1.0846 | 0.96359 | 0.21986 | 13.0661 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32517 | 0.047955 | 1.0846 | 1.0846 | 1.0846 | 1.0846 | 0.96359 | 0.21986 | 330 | 219.8633 | 0.96359 | 1.0846 | 0.0048333 | 13.0661
0.331 | 0.36753 | 0.050911 | 1.0911 | 1.0909 | 1.0908 | 1.0908 | 0.23053 | 13.2741 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32617 | 0.047978 | 1.0848 | 1.0847 | 1.0846 | 1.0846 | 0.96365 | 0.22089 | 13.0864 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32617 | 0.047978 | 1.0846 | 1.0846 | 1.0846 | 1.0846 | 0.96365 | 0.22089 | 13.0864 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32617 | 0.047978 | 1.0846 | 1.0846 | 1.0846 | 1.0846 | 0.96365 | 0.22089 | 331 | 220.8878 | 0.96365 | 1.0846 | 0.0048333 | 13.0864
0.332 | 0.36857 | 0.05093 | 1.0912 | 1.0909 | 1.0909 | 1.0909 | 0.23158 | 13.2943 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32717 | 0.048 | 1.0849 | 1.0847 | 1.0847 | 1.0847 | 0.96371 | 0.22191 | 13.1066 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32717 | 0.048 | 1.0847 | 1.0847 | 1.0847 | 1.0847 | 0.96371 | 0.22191 | 13.1066 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32717 | 0.048 | 1.0847 | 1.0847 | 1.0847 | 1.0847 | 0.96371 | 0.22191 | 332 | 221.914 | 0.96371 | 1.0847 | 0.0048333 | 13.1066
0.333 | 0.36961 | 0.050949 | 1.0912 | 1.0909 | 1.0909 | 1.0909 | 0.23264 | 13.3145 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32817 | 0.048022 | 1.0849 | 1.0847 | 1.0847 | 1.0847 | 0.96378 | 0.22294 | 13.1268 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32817 | 0.048022 | 1.0847 | 1.0847 | 1.0847 | 1.0847 | 0.96378 | 0.22294 | 13.1268 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32817 | 0.048022 | 1.0847 | 1.0847 | 1.0847 | 1.0847 | 0.96378 | 0.22294 | 333 | 222.9417 | 0.96378 | 1.0847 | 0.0048333 | 13.1268
0.334 | 0.37066 | 0.050968 | 1.0913 | 1.091 | 1.091 | 1.091 | 0.2337 | 13.3346 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32917 | 0.048044 | 1.085 | 1.0848 | 1.0848 | 1.0848 | 0.96384 | 0.22397 | 13.147 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32917 | 0.048044 | 1.0848 | 1.0848 | 1.0848 | 1.0848 | 0.96384 | 0.22397 | 13.147 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.32917 | 0.048044 | 1.0848 | 1.0848 | 1.0848 | 1.0848 | 0.96384 | 0.22397 | 334 | 223.971 | 0.96384 | 1.0848 | 0.0048333 | 13.147
0.335 | 0.3717 | 0.050987 | 1.0913 | 1.091 | 1.091 | 1.091 | 0.23476 | 13.3547 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33017 | 0.048066 | 1.085 | 1.0848 | 1.0848 | 1.0848 | 0.96391 | 0.225 | 13.1671 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33017 | 0.048066 | 1.0848 | 1.0848 | 1.0848 | 1.0848 | 0.96391 | 0.225 | 13.1671 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33017 | 0.048066 | 1.0848 | 1.0848 | 1.0848 | 1.0848 | 0.96391 | 0.225 | 335 | 225.002 | 0.96391 | 1.0848 | 0.0048333 | 13.1671
0.336 | 0.37274 | 0.051006 | 1.0913 | 1.0911 | 1.091 | 1.091 | 0.23582 | 13.3748 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33117 | 0.048088 | 1.0851 | 1.0849 | 1.0849 | 1.0849 | 0.96397 | 0.22603 | 13.1872 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33117 | 0.048088 | 1.0849 | 1.0849 | 1.0849 | 1.0849 | 0.96397 | 0.22603 | 13.1872 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33117 | 0.048088 | 1.0849 | 1.0849 | 1.0849 | 1.0849 | 0.96397 | 0.22603 | 336 | 226.0345 | 0.96397 | 1.0849 | 0.0048333 | 13.1872
0.337 | 0.37378 | 0.051024 | 1.0914 | 1.0911 | 1.0911 | 1.0911 | 0.23688 | 13.3949 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33217 | 0.04811 | 1.0851 | 1.0849 | 1.0849 | 1.0849 | 0.96403 | 0.22707 | 13.2073 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33217 | 0.04811 | 1.0849 | 1.0849 | 1.0849 | 1.0849 | 0.96403 | 0.22707 | 13.2073 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33217 | 0.04811 | 1.0849 | 1.0849 | 1.0849 | 1.0849 | 0.96403 | 0.22707 | 337 | 227.0685 | 0.96403 | 1.0849 | 0.0048333 | 13.2073
0.338 | 0.37482 | 0.051043 | 1.0914 | 1.0911 | 1.0911 | 1.0911 | 0.23794 | 13.4149 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33317 | 0.048131 | 1.0851 | 1.085 | 1.085 | 1.085 | 0.96409 | 0.2281 | 13.2274 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33317 | 0.048131 | 1.085 | 1.085 | 1.085 | 1.085 | 0.96409 | 0.2281 | 13.2274 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33317 | 0.048131 | 1.085 | 1.085 | 1.085 | 1.085 | 0.96409 | 0.2281 | 338 | 228.1042 | 0.96409 | 1.085 | 0.0048333 | 13.2274
0.339 | 0.37586 | 0.051061 | 1.0914 | 1.0912 | 1.0912 | 1.0912 | 0.23901 | 13.4349 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33417 | 0.048153 | 1.0852 | 1.085 | 1.085 | 1.085 | 0.96416 | 0.22914 | 13.2474 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33417 | 0.048153 | 1.085 | 1.085 | 1.085 | 1.085 | 0.96416 | 0.22914 | 13.2474 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33417 | 0.048153 | 1.085 | 1.085 | 1.085 | 1.085 | 0.96416 | 0.22914 | 339 | 229.1415 | 0.96416 | 1.085 | 0.0048333 | 13.2474
0.34 | 0.3769 | 0.05108 | 1.0915 | 1.0912 | 1.0912 | 1.0912 | 0.24008 | 13.4548 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33517 | 0.048174 | 1.0852 | 1.0851 | 1.0851 | 1.0851 | 0.96422 | 0.23018 | 13.2674 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33517 | 0.048174 | 1.0851 | 1.0851 | 1.0851 | 1.0851 | 0.96422 | 0.23018 | 13.2674 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33517 | 0.048174 | 1.0851 | 1.0851 | 1.0851 | 1.0851 | 0.96422 | 0.23018 | 340 | 230.1803 | 0.96422 | 1.0851 | 0.0048333 | 13.2674
0.341 | 0.37794 | 0.051098 | 1.0915 | 1.0913 | 1.0912 | 1.0912 | 0.24114 | 13.4748 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33617 | 0.048196 | 1.0853 | 1.0851 | 1.0851 | 1.0851 | 0.96428 | 0.23122 | 13.2873 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33617 | 0.048196 | 1.0851 | 1.0851 | 1.0851 | 1.0851 | 0.96428 | 0.23122 | 13.2873 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33617 | 0.048196 | 1.0851 | 1.0851 | 1.0851 | 1.0851 | 0.96428 | 0.23122 | 341 | 231.2207 | 0.96428 | 1.0851 | 0.0048333 | 13.2873
0.342 | 0.37898 | 0.051116 | 1.0916 | 1.0913 | 1.0913 | 1.0913 | 0.24221 | 13.4947 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33717 | 0.048217 | 1.0853 | 1.0851 | 1.0851 | 1.0851 | 0.96434 | 0.23226 | 13.3073 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33717 | 0.048217 | 1.0851 | 1.0851 | 1.0851 | 1.0851 | 0.96434 | 0.23226 | 13.3073 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33717 | 0.048217 | 1.0851 | 1.0851 | 1.0851 | 1.0851 | 0.96434 | 0.23226 | 342 | 232.2626 | 0.96434 | 1.0851 | 0.0048333 | 13.3073
0.343 | 0.38003 | 0.051134 | 1.0916 | 1.0913 | 1.0913 | 1.0913 | 0.24329 | 13.5145 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33817 | 0.048238 | 1.0854 | 1.0852 | 1.0852 | 1.0852 | 0.9644 | 0.23331 | 13.3272 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33817 | 0.048238 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 0.9644 | 0.23331 | 13.3272 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33817 | 0.048238 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 0.9644 | 0.23331 | 343 | 233.3062 | 0.9644 | 1.0852 | 0.0048333 | 13.3272
0.344 | 0.38107 | 0.051152 | 1.0916 | 1.0914 | 1.0914 | 1.0914 | 0.24436 | 13.5344 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33917 | 0.048259 | 1.0854 | 1.0852 | 1.0852 | 1.0852 | 0.96446 | 0.23435 | 13.347 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33917 | 0.048259 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 0.96446 | 0.23435 | 13.347 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.33917 | 0.048259 | 1.0852 | 1.0852 | 1.0852 | 1.0852 | 0.96446 | 0.23435 | 344 | 234.3512 | 0.96446 | 1.0852 | 0.0048333 | 13.347
0.345 | 0.38211 | 0.05117 | 1.0917 | 1.0914 | 1.0914 | 1.0914 | 0.24543 | 13.5542 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34017 | 0.048279 | 1.0855 | 1.0853 | 1.0853 | 1.0853 | 0.96452 | 0.2354 | 13.3669 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34017 | 0.048279 | 1.0853 | 1.0853 | 1.0853 | 1.0853 | 0.96452 | 0.2354 | 13.3669 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34017 | 0.048279 | 1.0853 | 1.0853 | 1.0853 | 1.0853 | 0.96452 | 0.2354 | 345 | 235.3979 | 0.96452 | 1.0853 | 0.0048333 | 13.3669
0.346 | 0.38315 | 0.051187 | 1.0917 | 1.0914 | 1.0914 | 1.0914 | 0.24651 | 13.574 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34117 | 0.0483 | 1.0855 | 1.0853 | 1.0853 | 1.0853 | 0.96458 | 0.23645 | 13.3867 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34117 | 0.0483 | 1.0853 | 1.0853 | 1.0853 | 1.0853 | 0.96458 | 0.23645 | 13.3867 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34117 | 0.0483 | 1.0853 | 1.0853 | 1.0853 | 1.0853 | 0.96458 | 0.23645 | 346 | 236.4461 | 0.96458 | 1.0853 | 0.0048333 | 13.3867
0.347 | 0.38419 | 0.051205 | 1.0917 | 1.0915 | 1.0915 | 1.0915 | 0.24759 | 13.5938 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34217 | 0.048321 | 1.0855 | 1.0854 | 1.0854 | 1.0854 | 0.96464 | 0.2375 | 13.4065 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34217 | 0.048321 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 0.96464 | 0.2375 | 13.4065 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34217 | 0.048321 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 0.96464 | 0.2375 | 347 | 237.4959 | 0.96464 | 1.0854 | 0.0048333 | 13.4065
0.348 | 0.38523 | 0.051223 | 1.0918 | 1.0915 | 1.0915 | 1.0915 | 0.24867 | 13.6135 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34317 | 0.048341 | 1.0856 | 1.0854 | 1.0854 | 1.0854 | 0.9647 | 0.23855 | 13.4262 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34317 | 0.048341 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 0.9647 | 0.23855 | 13.4262 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34317 | 0.048341 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 0.9647 | 0.23855 | 348 | 238.5472 | 0.9647 | 1.0854 | 0.0048333 | 13.4262
0.349 | 0.38627 | 0.05124 | 1.0918 | 1.0916 | 1.0916 | 1.0916 | 0.24975 | 13.6332 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34417 | 0.048362 | 1.0856 | 1.0855 | 1.0854 | 1.0854 | 0.96476 | 0.2396 | 13.4459 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34417 | 0.048362 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 0.96476 | 0.2396 | 13.4459 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34417 | 0.048362 | 1.0854 | 1.0854 | 1.0854 | 1.0854 | 0.96476 | 0.2396 | 349 | 239.6001 | 0.96476 | 1.0854 | 0.0048333 | 13.4459
0.35 | 0.38731 | 0.051257 | 1.0919 | 1.0916 | 1.0916 | 1.0916 | 0.25083 | 13.6529 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34517 | 0.048382 | 1.0857 | 1.0855 | 1.0855 | 1.0855 | 0.96481 | 0.24065 | 13.4656 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34517 | 0.048382 | 1.0855 | 1.0855 | 1.0855 | 1.0855 | 0.96481 | 0.24065 | 13.4656 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34517 | 0.048382 | 1.0855 | 1.0855 | 1.0855 | 1.0855 | 0.96481 | 0.24065 | 350 | 240.6546 | 0.96481 | 1.0855 | 0.0048333 | 13.4656
0.351 | 0.38836 | 0.051275 | 1.0919 | 1.0916 | 1.0916 | 1.0916 | 0.25192 | 13.6725 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34617 | 0.048402 | 1.0857 | 1.0855 | 1.0855 | 1.0855 | 0.96487 | 0.24171 | 13.4853 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34617 | 0.048402 | 1.0855 | 1.0855 | 1.0855 | 1.0855 | 0.96487 | 0.24171 | 13.4853 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34617 | 0.048402 | 1.0855 | 1.0855 | 1.0855 | 1.0855 | 0.96487 | 0.24171 | 351 | 241.7106 | 0.96487 | 1.0855 | 0.0048333 | 13.4853
0.352 | 0.3894 | 0.051292 | 1.0919 | 1.0917 | 1.0917 | 1.0917 | 0.253 | 13.6921 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34717 | 0.048422 | 1.0858 | 1.0856 | 1.0856 | 1.0856 | 0.96493 | 0.24277 | 13.5049 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34717 | 0.048422 | 1.0856 | 1.0856 | 1.0856 | 1.0856 | 0.96493 | 0.24277 | 13.5049 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34717 | 0.048422 | 1.0856 | 1.0856 | 1.0856 | 1.0856 | 0.96493 | 0.24277 | 352 | 242.7681 | 0.96493 | 1.0856 | 0.0048333 | 13.5049
0.353 | 0.39044 | 0.051309 | 1.092 | 1.0917 | 1.0917 | 1.0917 | 0.25409 | 13.7117 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34817 | 0.048442 | 1.0858 | 1.0856 | 1.0856 | 1.0856 | 0.96499 | 0.24383 | 13.5246 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34817 | 0.048442 | 1.0856 | 1.0856 | 1.0856 | 1.0856 | 0.96499 | 0.24383 | 13.5246 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34817 | 0.048442 | 1.0856 | 1.0856 | 1.0856 | 1.0856 | 0.96499 | 0.24383 | 353 | 243.8272 | 0.96499 | 1.0856 | 0.0048333 | 13.5246
0.354 | 0.39148 | 0.051326 | 1.092 | 1.0917 | 1.0917 | 1.0917 | 0.25518 | 13.7313 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34917 | 0.048462 | 1.0858 | 1.0857 | 1.0857 | 1.0857 | 0.96504 | 0.24489 | 13.5441 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34917 | 0.048462 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 0.96504 | 0.24489 | 13.5441 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.34917 | 0.048462 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 0.96504 | 0.24489 | 354 | 244.8878 | 0.96504 | 1.0857 | 0.0048333 | 13.5441
0.355 | 0.39252 | 0.051343 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.25627 | 13.7508 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35017 | 0.048482 | 1.0859 | 1.0857 | 1.0857 | 1.0857 | 0.9651 | 0.24595 | 13.5637 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35017 | 0.048482 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 0.9651 | 0.24595 | 13.5637 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35017 | 0.048482 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 0.9651 | 0.24595 | 355 | 245.95 | 0.9651 | 1.0857 | 0.0048333 | 13.5637
0.356 | 0.39356 | 0.05136 | 1.0921 | 1.0918 | 1.0918 | 1.0918 | 0.25736 | 13.7703 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35117 | 0.048501 | 1.0859 | 1.0857 | 1.0857 | 1.0857 | 0.96515 | 0.24701 | 13.5832 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35117 | 0.048501 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 0.96515 | 0.24701 | 13.5832 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35117 | 0.048501 | 1.0857 | 1.0857 | 1.0857 | 1.0857 | 0.96515 | 0.24701 | 356 | 247.0137 | 0.96515 | 1.0857 | 0.0048333 | 13.5832
0.357 | 0.3946 | 0.051376 | 1.0921 | 1.0919 | 1.0918 | 1.0918 | 0.25846 | 13.7898 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35217 | 0.048521 | 1.086 | 1.0858 | 1.0858 | 1.0858 | 0.96521 | 0.24808 | 13.6027 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35217 | 0.048521 | 1.0858 | 1.0858 | 1.0858 | 1.0858 | 0.96521 | 0.24808 | 13.6027 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35217 | 0.048521 | 1.0858 | 1.0858 | 1.0858 | 1.0858 | 0.96521 | 0.24808 | 357 | 248.0789 | 0.96521 | 1.0858 | 0.0048333 | 13.6027
0.358 | 0.39564 | 0.051393 | 1.0921 | 1.0919 | 1.0919 | 1.0919 | 0.25955 | 13.8092 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35317 | 0.04854 | 1.086 | 1.0858 | 1.0858 | 1.0858 | 0.96527 | 0.24915 | 13.6222 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35317 | 0.04854 | 1.0858 | 1.0858 | 1.0858 | 1.0858 | 0.96527 | 0.24915 | 13.6222 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35317 | 0.04854 | 1.0858 | 1.0858 | 1.0858 | 1.0858 | 0.96527 | 0.24915 | 358 | 249.1457 | 0.96527 | 1.0858 | 0.0048333 | 13.6222
0.359 | 0.39668 | 0.05141 | 1.0922 | 1.0919 | 1.0919 | 1.0919 | 0.26065 | 13.8287 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35417 | 0.04856 | 1.086 | 1.0859 | 1.0859 | 1.0859 | 0.96532 | 0.25021 | 13.6416 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35417 | 0.04856 | 1.0859 | 1.0859 | 1.0859 | 1.0859 | 0.96532 | 0.25021 | 13.6416 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35417 | 0.04856 | 1.0859 | 1.0859 | 1.0859 | 1.0859 | 0.96532 | 0.25021 | 359 | 250.214 | 0.96532 | 1.0859 | 0.0048333 | 13.6416
0.36 | 0.39773 | 0.051426 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.26175 | 13.8481 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35517 | 0.048579 | 1.0861 | 1.0859 | 1.0859 | 1.0859 | 0.96538 | 0.25128 | 13.661 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35517 | 0.048579 | 1.0859 | 1.0859 | 1.0859 | 1.0859 | 0.96538 | 0.25128 | 13.661 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35517 | 0.048579 | 1.0859 | 1.0859 | 1.0859 | 1.0859 | 0.96538 | 0.25128 | 360 | 251.2838 | 0.96538 | 1.0859 | 0.0048333 | 13.661
0.361 | 0.39877 | 0.051443 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.26285 | 13.8674 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35617 | 0.048598 | 1.0861 | 1.0859 | 1.0859 | 1.0859 | 0.96543 | 0.25236 | 13.6804 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35617 | 0.048598 | 1.0859 | 1.0859 | 1.0859 | 1.0859 | 0.96543 | 0.25236 | 13.6804 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35617 | 0.048598 | 1.0859 | 1.0859 | 1.0859 | 1.0859 | 0.96543 | 0.25236 | 361 | 252.3552 | 0.96543 | 1.0859 | 0.0048333 | 13.6804
0.362 | 0.39981 | 0.051459 | 1.0923 | 1.092 | 1.092 | 1.092 | 0.26395 | 13.8868 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35717 | 0.048617 | 1.0862 | 1.086 | 1.086 | 1.086 | 0.96548 | 0.25343 | 13.6998 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35717 | 0.048617 | 1.086 | 1.086 | 1.086 | 1.086 | 0.96548 | 0.25343 | 13.6998 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35717 | 0.048617 | 1.086 | 1.086 | 1.086 | 1.086 | 0.96548 | 0.25343 | 362 | 253.4281 | 0.96548 | 1.086 | 0.0048333 | 13.6998
0.363 | 0.40085 | 0.051475 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.26505 | 13.9061 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35817 | 0.048636 | 1.0862 | 1.086 | 1.086 | 1.086 | 0.96554 | 0.2545 | 13.7191 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35817 | 0.048636 | 1.086 | 1.086 | 1.086 | 1.086 | 0.96554 | 0.2545 | 13.7191 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35817 | 0.048636 | 1.086 | 1.086 | 1.086 | 1.086 | 0.96554 | 0.2545 | 363 | 254.5025 | 0.96554 | 1.086 | 0.0048333 | 13.7191
0.364 | 0.40189 | 0.051491 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.26615 | 13.9254 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35917 | 0.048655 | 1.0862 | 1.0861 | 1.0861 | 1.0861 | 0.96559 | 0.25558 | 13.7384 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35917 | 0.048655 | 1.0861 | 1.0861 | 1.0861 | 1.0861 | 0.96559 | 0.25558 | 13.7384 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.35917 | 0.048655 | 1.0861 | 1.0861 | 1.0861 | 1.0861 | 0.96559 | 0.25558 | 364 | 255.5784 | 0.96559 | 1.0861 | 0.0048333 | 13.7384
0.365 | 0.40293 | 0.051507 | 1.0924 | 1.0921 | 1.0921 | 1.0921 | 0.26726 | 13.9446 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36017 | 0.048674 | 1.0863 | 1.0861 | 1.0861 | 1.0861 | 0.96565 | 0.25666 | 13.7577 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36017 | 0.048674 | 1.0861 | 1.0861 | 1.0861 | 1.0861 | 0.96565 | 0.25666 | 13.7577 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36017 | 0.048674 | 1.0861 | 1.0861 | 1.0861 | 1.0861 | 0.96565 | 0.25666 | 365 | 256.6559 | 0.96565 | 1.0861 | 0.0048333 | 13.7577
0.366 | 0.40397 | 0.051523 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.26837 | 13.9639 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36117 | 0.048693 | 1.0863 | 1.0861 | 1.0861 | 1.0861 | 0.9657 | 0.25773 | 13.777 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36117 | 0.048693 | 1.0861 | 1.0861 | 1.0861 | 1.0861 | 0.9657 | 0.25773 | 13.777 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36117 | 0.048693 | 1.0861 | 1.0861 | 1.0861 | 1.0861 | 0.9657 | 0.25773 | 366 | 257.7348 | 0.9657 | 1.0861 | 0.0048333 | 13.777
0.367 | 0.40501 | 0.051539 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.26948 | 13.9831 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36217 | 0.048711 | 1.0864 | 1.0862 | 1.0862 | 1.0862 | 0.96575 | 0.25882 | 13.7962 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36217 | 0.048711 | 1.0862 | 1.0862 | 1.0862 | 1.0862 | 0.96575 | 0.25882 | 13.7962 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36217 | 0.048711 | 1.0862 | 1.0862 | 1.0862 | 1.0862 | 0.96575 | 0.25882 | 367 | 258.8153 | 0.96575 | 1.0862 | 0.0048333 | 13.7962
0.368 | 0.40606 | 0.051555 | 1.0925 | 1.0922 | 1.0922 | 1.0922 | 0.27059 | 14.0023 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36303 | 0.048653 | 1.0862 | 1.0861 | 1.0861 | 1.0861 | 0.96487 | 0.25961 | 13.8102 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36317 | 0.04873 | 1.0862 | 1.0862 | 1.0862 | 1.0862 | 0.9658 | 0.2599 | 13.8154 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36317 | 0.04873 | 1.0862 | 1.0862 | 1.0862 | 1.0862 | 0.9658 | 0.2599 | 368 | 259.8973 | 0.9658 | 1.0862 | 0.0048333 | 13.8154
0.369 | 0.4071 | 0.051571 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.2717 | 14.0214 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36403 | 0.048672 | 1.0863 | 1.0861 | 1.0861 | 1.0861 | 0.96492 | 0.26069 | 13.8294 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36417 | 0.048748 | 1.0863 | 1.0863 | 1.0863 | 1.0863 | 0.96586 | 0.26098 | 13.8346 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36417 | 0.048748 | 1.0863 | 1.0863 | 1.0863 | 1.0863 | 0.96586 | 0.26098 | 369 | 260.9808 | 0.96586 | 1.0863 | 0.0048333 | 13.8346
0.37 | 0.40814 | 0.051587 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.27281 | 14.0406 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36503 | 0.04869 | 1.0863 | 1.0861 | 1.0861 | 1.0861 | 0.96498 | 0.26177 | 13.8486 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36517 | 0.048766 | 1.0863 | 1.0863 | 1.0863 | 1.0863 | 0.96591 | 0.26207 | 13.8537 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36517 | 0.048766 | 1.0863 | 1.0863 | 1.0863 | 1.0863 | 0.96591 | 0.26207 | 370 | 262.0658 | 0.96591 | 1.0863 | 0.0048333 | 13.8537
0.371 | 0.40918 | 0.051602 | 1.0926 | 1.0923 | 1.0923 | 1.0923 | 0.27393 | 14.0597 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36603 | 0.048709 | 1.0864 | 1.0862 | 1.0862 | 1.0862 | 0.96503 | 0.26286 | 13.8677 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36617 | 0.048785 | 1.0863 | 1.0863 | 1.0863 | 1.0863 | 0.96596 | 0.26315 | 13.8728 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36617 | 0.048785 | 1.0863 | 1.0863 | 1.0863 | 1.0863 | 0.96596 | 0.26315 | 371 | 263.1524 | 0.96596 | 1.0863 | 0.0048333 | 13.8728
0.372 | 0.41022 | 0.051618 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.27505 | 14.0787 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36703 | 0.048727 | 1.0864 | 1.0862 | 1.0862 | 1.0862 | 0.96508 | 0.26395 | 13.8868 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36717 | 0.048803 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.96601 | 0.26424 | 13.8919 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36717 | 0.048803 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.96601 | 0.26424 | 372 | 264.2404 | 0.96601 | 1.0864 | 0.0048333 | 13.8919
0.373 | 0.41126 | 0.051633 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.27616 | 14.0978 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36803 | 0.048745 | 1.0864 | 1.0863 | 1.0863 | 1.0863 | 0.96514 | 0.26504 | 13.9058 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36817 | 0.048821 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.96606 | 0.26533 | 13.911 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36817 | 0.048821 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.96606 | 0.26533 | 373 | 265.3299 | 0.96606 | 1.0864 | 0.0048333 | 13.911
0.374 | 0.4123 | 0.051649 | 1.0927 | 1.0924 | 1.0924 | 1.0924 | 0.27728 | 14.1168 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.36903 | 0.048763 | 1.0865 | 1.0863 | 1.0863 | 1.0863 | 0.96519 | 0.26613 | 13.9249 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36917 | 0.048839 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.96611 | 0.26642 | 13.93 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.36917 | 0.048839 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.96611 | 0.26642 | 374 | 266.4209 | 0.96611 | 1.0864 | 0.0048333 | 13.93
0.375 | 0.41334 | 0.051664 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.2784 | 14.1358 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37003 | 0.048781 | 1.0865 | 1.0863 | 1.0863 | 1.0863 | 0.96524 | 0.26722 | 13.9439 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.37017 | 0.048857 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.96616 | 0.26751 | 13.949 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.37017 | 0.048857 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.96616 | 0.26751 | 375 | 267.5134 | 0.96616 | 1.0865 | 0.0048333 | 13.949
0.376 | 0.41438 | 0.051679 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.27953 | 14.1548 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37103 | 0.048799 | 1.0866 | 1.0864 | 1.0864 | 1.0864 | 0.96529 | 0.26831 | 13.9629 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.37117 | 0.048874 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.96621 | 0.26861 | 13.968 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.37117 | 0.048874 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.96621 | 0.26861 | 376 | 268.6075 | 0.96621 | 1.0865 | 0.0048333 | 13.968
0.377 | 0.41543 | 0.051694 | 1.0928 | 1.0925 | 1.0925 | 1.0925 | 0.28065 | 14.1737 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37203 | 0.048817 | 1.0866 | 1.0864 | 1.0864 | 1.0864 | 0.96534 | 0.26941 | 13.9819 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.37217 | 0.048892 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.96626 | 0.2697 | 13.987 | 0.0055 | 0.0045 | 0.0048333 | 0.64125 | 0.37217 | 0.048892 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.96626 | 0.2697 | 377 | 269.703 | 0.96626 | 1.0866 | 0.0048333 | 13.987
0.378 | 0.41647 | 0.051709 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.28178 | 14.1927 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37303 | 0.048834 | 1.0866 | 1.0864 | 1.0864 | 1.0864 | 0.9654 | 0.2705 | 14.0008 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37303 | 0.048834 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.9654 | 0.2705 | 14.0008 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37303 | 0.048834 | 1.0864 | 1.0864 | 1.0864 | 1.0864 | 0.9654 | 0.2705 | 378 | 270.5027 | 0.9654 | 1.0864 | 0.0049667 | 14.0008
0.379 | 0.41751 | 0.051724 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.2829 | 14.2116 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37403 | 0.048852 | 1.0867 | 1.0865 | 1.0865 | 1.0865 | 0.96545 | 0.2716 | 14.0197 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37403 | 0.048852 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.96545 | 0.2716 | 14.0197 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37403 | 0.048852 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.96545 | 0.2716 | 379 | 271.6004 | 0.96545 | 1.0865 | 0.0049667 | 14.0197
0.38 | 0.41855 | 0.051739 | 1.0929 | 1.0926 | 1.0926 | 1.0926 | 0.28403 | 14.2305 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37503 | 0.048869 | 1.0867 | 1.0865 | 1.0865 | 1.0865 | 0.9655 | 0.2727 | 14.0386 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37503 | 0.048869 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.9655 | 0.2727 | 14.0386 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37503 | 0.048869 | 1.0865 | 1.0865 | 1.0865 | 1.0865 | 0.9655 | 0.2727 | 380 | 272.6996 | 0.9655 | 1.0865 | 0.0049667 | 14.0386
0.381 | 0.41959 | 0.051754 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.28516 | 14.2493 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37603 | 0.048887 | 1.0867 | 1.0866 | 1.0866 | 1.0866 | 0.96555 | 0.2738 | 14.0575 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37603 | 0.048887 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.96555 | 0.2738 | 14.0575 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37603 | 0.048887 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.96555 | 0.2738 | 381 | 273.8003 | 0.96555 | 1.0866 | 0.0049667 | 14.0575
0.382 | 0.42063 | 0.051769 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.2863 | 14.2681 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37703 | 0.048904 | 1.0868 | 1.0866 | 1.0866 | 1.0866 | 0.9656 | 0.2749 | 14.0763 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37703 | 0.048904 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.9656 | 0.2749 | 14.0763 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37703 | 0.048904 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.9656 | 0.2749 | 382 | 274.9024 | 0.9656 | 1.0866 | 0.0049667 | 14.0763
0.383 | 0.42167 | 0.051784 | 1.093 | 1.0927 | 1.0927 | 1.0927 | 0.28743 | 14.2869 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37803 | 0.048921 | 1.0868 | 1.0866 | 1.0866 | 1.0866 | 0.96565 | 0.27601 | 14.0951 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37803 | 0.048921 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.96565 | 0.27601 | 14.0951 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37803 | 0.048921 | 1.0866 | 1.0866 | 1.0866 | 1.0866 | 0.96565 | 0.27601 | 383 | 276.0061 | 0.96565 | 1.0866 | 0.0049667 | 14.0951
0.384 | 0.42271 | 0.051798 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.28856 | 14.3057 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37903 | 0.048939 | 1.0868 | 1.0867 | 1.0867 | 1.0867 | 0.9657 | 0.27711 | 14.1139 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37903 | 0.048939 | 1.0867 | 1.0867 | 1.0867 | 1.0867 | 0.9657 | 0.27711 | 14.1139 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.37903 | 0.048939 | 1.0867 | 1.0867 | 1.0867 | 1.0867 | 0.9657 | 0.27711 | 384 | 277.1112 | 0.9657 | 1.0867 | 0.0049667 | 14.1139
0.385 | 0.42375 | 0.051813 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.2897 | 14.3245 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38003 | 0.048956 | 1.0869 | 1.0867 | 1.0867 | 1.0867 | 0.96575 | 0.27822 | 14.1327 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38003 | 0.048956 | 1.0867 | 1.0867 | 1.0867 | 1.0867 | 0.96575 | 0.27822 | 14.1327 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38003 | 0.048956 | 1.0867 | 1.0867 | 1.0867 | 1.0867 | 0.96575 | 0.27822 | 385 | 278.2178 | 0.96575 | 1.0867 | 0.0049667 | 14.1327
0.386 | 0.4248 | 0.051828 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.29084 | 14.3432 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38103 | 0.048973 | 1.0869 | 1.0867 | 1.0867 | 1.0867 | 0.96579 | 0.27933 | 14.1514 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38103 | 0.048973 | 1.0867 | 1.0867 | 1.0867 | 1.0867 | 0.96579 | 0.27933 | 14.1514 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38103 | 0.048973 | 1.0867 | 1.0867 | 1.0867 | 1.0867 | 0.96579 | 0.27933 | 386 | 279.3259 | 0.96579 | 1.0867 | 0.0049667 | 14.1514
0.387 | 0.42584 | 0.051842 | 1.0931 | 1.0929 | 1.0928 | 1.0928 | 0.29198 | 14.3619 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38203 | 0.04899 | 1.087 | 1.0868 | 1.0868 | 1.0868 | 0.96584 | 0.28044 | 14.1701 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38203 | 0.04899 | 1.0868 | 1.0868 | 1.0868 | 1.0868 | 0.96584 | 0.28044 | 14.1701 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38203 | 0.04899 | 1.0868 | 1.0868 | 1.0868 | 1.0868 | 0.96584 | 0.28044 | 387 | 280.4354 | 0.96584 | 1.0868 | 0.0049667 | 14.1701
0.388 | 0.42688 | 0.051856 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.29312 | 14.3806 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38303 | 0.049007 | 1.087 | 1.0868 | 1.0868 | 1.0868 | 0.96589 | 0.28155 | 14.1888 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38303 | 0.049007 | 1.0868 | 1.0868 | 1.0868 | 1.0868 | 0.96589 | 0.28155 | 14.1888 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38303 | 0.049007 | 1.0868 | 1.0868 | 1.0868 | 1.0868 | 0.96589 | 0.28155 | 388 | 281.5464 | 0.96589 | 1.0868 | 0.0049667 | 14.1888
0.389 | 0.42792 | 0.051871 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.29426 | 14.3992 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38403 | 0.049023 | 1.087 | 1.0868 | 1.0868 | 1.0868 | 0.96594 | 0.28266 | 14.2075 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38403 | 0.049023 | 1.0868 | 1.0868 | 1.0868 | 1.0868 | 0.96594 | 0.28266 | 14.2075 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38403 | 0.049023 | 1.0868 | 1.0868 | 1.0868 | 1.0868 | 0.96594 | 0.28266 | 389 | 282.6589 | 0.96594 | 1.0868 | 0.0049667 | 14.2075
0.39 | 0.42896 | 0.051885 | 1.0932 | 1.0929 | 1.0929 | 1.0929 | 0.2954 | 14.4179 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38503 | 0.04904 | 1.0871 | 1.0869 | 1.0869 | 1.0869 | 0.96599 | 0.28377 | 14.2261 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38503 | 0.04904 | 1.0869 | 1.0869 | 1.0869 | 1.0869 | 0.96599 | 0.28377 | 14.2261 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38503 | 0.04904 | 1.0869 | 1.0869 | 1.0869 | 1.0869 | 0.96599 | 0.28377 | 390 | 283.7729 | 0.96599 | 1.0869 | 0.0049667 | 14.2261
0.391 | 0.43 | 0.051899 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.29655 | 14.4365 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38603 | 0.049057 | 1.0871 | 1.0869 | 1.0869 | 1.0869 | 0.96604 | 0.28489 | 14.2447 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38603 | 0.049057 | 1.0869 | 1.0869 | 1.0869 | 1.0869 | 0.96604 | 0.28489 | 14.2447 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38603 | 0.049057 | 1.0869 | 1.0869 | 1.0869 | 1.0869 | 0.96604 | 0.28489 | 391 | 284.8883 | 0.96604 | 1.0869 | 0.0049667 | 14.2447
0.392 | 0.43104 | 0.051913 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.2977 | 14.455 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38703 | 0.049073 | 1.0871 | 1.0869 | 1.0869 | 1.0869 | 0.96608 | 0.28601 | 14.2633 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38703 | 0.049073 | 1.0869 | 1.0869 | 1.0869 | 1.0869 | 0.96608 | 0.28601 | 14.2633 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38703 | 0.049073 | 1.0869 | 1.0869 | 1.0869 | 1.0869 | 0.96608 | 0.28601 | 392 | 286.0052 | 0.96608 | 1.0869 | 0.0049667 | 14.2633
0.393 | 0.43208 | 0.051927 | 1.0933 | 1.093 | 1.093 | 1.093 | 0.29884 | 14.4736 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38803 | 0.04909 | 1.0872 | 1.087 | 1.087 | 1.087 | 0.96613 | 0.28712 | 14.2819 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38803 | 0.04909 | 1.087 | 1.087 | 1.087 | 1.087 | 0.96613 | 0.28712 | 14.2819 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38803 | 0.04909 | 1.087 | 1.087 | 1.087 | 1.087 | 0.96613 | 0.28712 | 393 | 287.1235 | 0.96613 | 1.087 | 0.0049667 | 14.2819
0.394 | 0.43313 | 0.051941 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.29999 | 14.4921 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38903 | 0.049106 | 1.0872 | 1.087 | 1.087 | 1.087 | 0.96618 | 0.28824 | 14.3004 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38903 | 0.049106 | 1.087 | 1.087 | 1.087 | 1.087 | 0.96618 | 0.28824 | 14.3004 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.38903 | 0.049106 | 1.087 | 1.087 | 1.087 | 1.087 | 0.96618 | 0.28824 | 394 | 288.2433 | 0.96618 | 1.087 | 0.0049667 | 14.3004
0.395 | 0.43417 | 0.051955 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.30114 | 14.5107 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39003 | 0.049123 | 1.0872 | 1.0871 | 1.087 | 1.087 | 0.96623 | 0.28936 | 14.3189 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39003 | 0.049123 | 1.087 | 1.087 | 1.087 | 1.087 | 0.96623 | 0.28936 | 14.3189 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39003 | 0.049123 | 1.087 | 1.087 | 1.087 | 1.087 | 0.96623 | 0.28936 | 395 | 289.3646 | 0.96623 | 1.087 | 0.0049667 | 14.3189
0.396 | 0.43521 | 0.051969 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.3023 | 14.5291 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39103 | 0.049139 | 1.0873 | 1.0871 | 1.0871 | 1.0871 | 0.96627 | 0.29049 | 14.3374 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39103 | 0.049139 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 0.96627 | 0.29049 | 14.3374 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39103 | 0.049139 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 0.96627 | 0.29049 | 396 | 290.4873 | 0.96627 | 1.0871 | 0.0049667 | 14.3374
0.397 | 0.43625 | 0.051983 | 1.0934 | 1.0932 | 1.0931 | 1.0931 | 0.30345 | 14.5476 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39203 | 0.049155 | 1.0873 | 1.0871 | 1.0871 | 1.0871 | 0.96632 | 0.29161 | 14.3559 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39203 | 0.049155 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 0.96632 | 0.29161 | 14.3559 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39203 | 0.049155 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 0.96632 | 0.29161 | 397 | 291.6115 | 0.96632 | 1.0871 | 0.0049667 | 14.3559
0.398 | 0.43729 | 0.051996 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.30461 | 14.5661 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39303 | 0.049171 | 1.0873 | 1.0872 | 1.0871 | 1.0871 | 0.96636 | 0.29274 | 14.3743 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39303 | 0.049171 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 0.96636 | 0.29274 | 14.3743 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39303 | 0.049171 | 1.0871 | 1.0871 | 1.0871 | 1.0871 | 0.96636 | 0.29274 | 398 | 292.7371 | 0.96636 | 1.0871 | 0.0049667 | 14.3743
0.399 | 0.43833 | 0.05201 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.30576 | 14.5845 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39403 | 0.049187 | 1.0874 | 1.0872 | 1.0872 | 1.0872 | 0.96641 | 0.29386 | 14.3928 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39403 | 0.049187 | 1.0872 | 1.0872 | 1.0872 | 1.0872 | 0.96641 | 0.29386 | 14.3928 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39403 | 0.049187 | 1.0872 | 1.0872 | 1.0872 | 1.0872 | 0.96641 | 0.29386 | 399 | 293.8642 | 0.96641 | 1.0872 | 0.0049667 | 14.3928
0.4 | 0.43937 | 0.052024 | 1.0935 | 1.0932 | 1.0932 | 1.0932 | 0.30692 | 14.6029 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39503 | 0.049203 | 1.0874 | 1.0872 | 1.0872 | 1.0872 | 0.96646 | 0.29499 | 14.4112 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39503 | 0.049203 | 1.0872 | 1.0872 | 1.0872 | 1.0872 | 0.96646 | 0.29499 | 14.4112 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39503 | 0.049203 | 1.0872 | 1.0872 | 1.0872 | 1.0872 | 0.96646 | 0.29499 | 400 | 294.9927 | 0.96646 | 1.0872 | 0.0049667 | 14.4112
0.401 | 0.44041 | 0.052037 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.30808 | 14.6212 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39603 | 0.049219 | 1.0874 | 1.0873 | 1.0873 | 1.0873 | 0.9665 | 0.29612 | 14.4295 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39603 | 0.049219 | 1.0873 | 1.0873 | 1.0873 | 1.0873 | 0.9665 | 0.29612 | 14.4295 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39603 | 0.049219 | 1.0873 | 1.0873 | 1.0873 | 1.0873 | 0.9665 | 0.29612 | 401 | 296.1226 | 0.9665 | 1.0873 | 0.0049667 | 14.4295
0.402 | 0.44145 | 0.052051 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.30924 | 14.6396 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39703 | 0.049235 | 1.0875 | 1.0873 | 1.0873 | 1.0873 | 0.96655 | 0.29725 | 14.4479 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39703 | 0.049235 | 1.0873 | 1.0873 | 1.0873 | 1.0873 | 0.96655 | 0.29725 | 14.4479 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39703 | 0.049235 | 1.0873 | 1.0873 | 1.0873 | 1.0873 | 0.96655 | 0.29725 | 402 | 297.2541 | 0.96655 | 1.0873 | 0.0049667 | 14.4479
0.403 | 0.4425 | 0.052064 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.31041 | 14.6579 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39803 | 0.04925 | 1.0875 | 1.0873 | 1.0873 | 1.0873 | 0.96659 | 0.29839 | 14.4662 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39803 | 0.04925 | 1.0873 | 1.0873 | 1.0873 | 1.0873 | 0.96659 | 0.29839 | 14.4662 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39803 | 0.04925 | 1.0873 | 1.0873 | 1.0873 | 1.0873 | 0.96659 | 0.29839 | 403 | 298.3869 | 0.96659 | 1.0873 | 0.0049667 | 14.4662
0.404 | 0.44354 | 0.052077 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.31157 | 14.6762 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39903 | 0.049266 | 1.0875 | 1.0874 | 1.0874 | 1.0874 | 0.96664 | 0.29952 | 14.4845 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39903 | 0.049266 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96664 | 0.29952 | 14.4845 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.39903 | 0.049266 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96664 | 0.29952 | 404 | 299.5212 | 0.96664 | 1.0874 | 0.0049667 | 14.4845
0.405 | 0.44458 | 0.052091 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.31274 | 14.6945 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40003 | 0.049282 | 1.0876 | 1.0874 | 1.0874 | 1.0874 | 0.96668 | 0.30066 | 14.5028 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40003 | 0.049282 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96668 | 0.30066 | 14.5028 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40003 | 0.049282 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96668 | 0.30066 | 405 | 300.6569 | 0.96668 | 1.0874 | 0.0049667 | 14.5028
0.406 | 0.44562 | 0.052104 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.3139 | 14.7128 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40103 | 0.049297 | 1.0876 | 1.0874 | 1.0874 | 1.0874 | 0.96673 | 0.30179 | 14.5211 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40103 | 0.049297 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96673 | 0.30179 | 14.5211 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40103 | 0.049297 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96673 | 0.30179 | 406 | 301.7941 | 0.96673 | 1.0874 | 0.0049667 | 14.5211
0.407 | 0.44666 | 0.052117 | 1.0937 | 1.0934 | 1.0934 | 1.0934 | 0.31507 | 14.731 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40203 | 0.049313 | 1.0876 | 1.0875 | 1.0874 | 1.0874 | 0.96677 | 0.30293 | 14.5393 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40203 | 0.049313 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96677 | 0.30293 | 14.5393 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40203 | 0.049313 | 1.0874 | 1.0874 | 1.0874 | 1.0874 | 0.96677 | 0.30293 | 407 | 302.9327 | 0.96677 | 1.0874 | 0.0049667 | 14.5393
0.408 | 0.4477 | 0.05213 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.31624 | 14.7492 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40303 | 0.049328 | 1.0877 | 1.0875 | 1.0875 | 1.0875 | 0.96681 | 0.30407 | 14.5575 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40303 | 0.049328 | 1.0875 | 1.0875 | 1.0875 | 1.0875 | 0.96681 | 0.30407 | 14.5575 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40303 | 0.049328 | 1.0875 | 1.0875 | 1.0875 | 1.0875 | 0.96681 | 0.30407 | 408 | 304.0728 | 0.96681 | 1.0875 | 0.0049667 | 14.5575
0.409 | 0.44874 | 0.052143 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.31741 | 14.7674 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40403 | 0.049343 | 1.0877 | 1.0875 | 1.0875 | 1.0875 | 0.96686 | 0.30521 | 14.5757 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40403 | 0.049343 | 1.0875 | 1.0875 | 1.0875 | 1.0875 | 0.96686 | 0.30521 | 14.5757 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40403 | 0.049343 | 1.0875 | 1.0875 | 1.0875 | 1.0875 | 0.96686 | 0.30521 | 409 | 305.2142 | 0.96686 | 1.0875 | 0.0049667 | 14.5757
0.41 | 0.44978 | 0.052156 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.31859 | 14.7856 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40503 | 0.049359 | 1.0877 | 1.0876 | 1.0875 | 1.0875 | 0.9669 | 0.30636 | 14.5939 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40503 | 0.049359 | 1.0875 | 1.0875 | 1.0875 | 1.0875 | 0.9669 | 0.30636 | 14.5939 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40503 | 0.049359 | 1.0875 | 1.0875 | 1.0875 | 1.0875 | 0.9669 | 0.30636 | 410 | 306.3571 | 0.9669 | 1.0875 | 0.0049667 | 14.5939
0.411 | 0.45083 | 0.052169 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.31976 | 14.8037 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40603 | 0.049374 | 1.0878 | 1.0876 | 1.0876 | 1.0876 | 0.96694 | 0.3075 | 14.6121 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40603 | 0.049374 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 0.96694 | 0.3075 | 14.6121 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40603 | 0.049374 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 0.96694 | 0.3075 | 411 | 307.5015 | 0.96694 | 1.0876 | 0.0049667 | 14.6121
0.412 | 0.45187 | 0.052182 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.32094 | 14.8218 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40703 | 0.049389 | 1.0878 | 1.0876 | 1.0876 | 1.0876 | 0.96699 | 0.30865 | 14.6302 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40703 | 0.049389 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 0.96699 | 0.30865 | 14.6302 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40703 | 0.049389 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 0.96699 | 0.30865 | 412 | 308.6472 | 0.96699 | 1.0876 | 0.0049667 | 14.6302
0.413 | 0.45291 | 0.052195 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.32211 | 14.8399 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40803 | 0.049404 | 1.0878 | 1.0876 | 1.0876 | 1.0876 | 0.96703 | 0.30979 | 14.6483 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40803 | 0.049404 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 0.96703 | 0.30979 | 14.6483 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40803 | 0.049404 | 1.0876 | 1.0876 | 1.0876 | 1.0876 | 0.96703 | 0.30979 | 413 | 309.7944 | 0.96703 | 1.0876 | 0.0049667 | 14.6483
0.414 | 0.45395 | 0.052208 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.32329 | 14.858 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40903 | 0.049419 | 1.0879 | 1.0877 | 1.0877 | 1.0877 | 0.96707 | 0.31094 | 14.6664 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40903 | 0.049419 | 1.0877 | 1.0877 | 1.0877 | 1.0877 | 0.96707 | 0.31094 | 14.6664 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.40903 | 0.049419 | 1.0877 | 1.0877 | 1.0877 | 1.0877 | 0.96707 | 0.31094 | 414 | 310.943 | 0.96707 | 1.0877 | 0.0049667 | 14.6664
0.415 | 0.45499 | 0.05222 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.32447 | 14.8761 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41003 | 0.049434 | 1.0879 | 1.0877 | 1.0877 | 1.0877 | 0.96711 | 0.31209 | 14.6844 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41003 | 0.049434 | 1.0877 | 1.0877 | 1.0877 | 1.0877 | 0.96711 | 0.31209 | 14.6844 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41003 | 0.049434 | 1.0877 | 1.0877 | 1.0877 | 1.0877 | 0.96711 | 0.31209 | 415 | 312.093 | 0.96711 | 1.0877 | 0.0049667 | 14.6844
0.416 | 0.45603 | 0.052233 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.32565 | 14.8941 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41103 | 0.049449 | 1.0879 | 1.0877 | 1.0877 | 1.0877 | 0.96716 | 0.31324 | 14.7025 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41103 | 0.049449 | 1.0877 | 1.0877 | 1.0877 | 1.0877 | 0.96716 | 0.31324 | 14.7025 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41103 | 0.049449 | 1.0877 | 1.0877 | 1.0877 | 1.0877 | 0.96716 | 0.31324 | 416 | 313.2445 | 0.96716 | 1.0877 | 0.0049667 | 14.7025
0.417 | 0.45707 | 0.052246 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.32684 | 14.9121 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41203 | 0.049464 | 1.088 | 1.0878 | 1.0878 | 1.0878 | 0.9672 | 0.3144 | 14.7205 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41203 | 0.049464 | 1.0878 | 1.0878 | 1.0878 | 1.0878 | 0.9672 | 0.3144 | 14.7205 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41203 | 0.049464 | 1.0878 | 1.0878 | 1.0878 | 1.0878 | 0.9672 | 0.3144 | 417 | 314.3973 | 0.9672 | 1.0878 | 0.0049667 | 14.7205
0.418 | 0.45811 | 0.052258 | 1.094 | 1.0938 | 1.0937 | 1.0937 | 0.32802 | 14.9301 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41303 | 0.049478 | 1.088 | 1.0878 | 1.0878 | 1.0878 | 0.96724 | 0.31555 | 14.7385 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41303 | 0.049478 | 1.0878 | 1.0878 | 1.0878 | 1.0878 | 0.96724 | 0.31555 | 14.7385 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41303 | 0.049478 | 1.0878 | 1.0878 | 1.0878 | 1.0878 | 0.96724 | 0.31555 | 418 | 315.5516 | 0.96724 | 1.0878 | 0.0049667 | 14.7385
0.419 | 0.45915 | 0.052271 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.32921 | 14.9481 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41403 | 0.049493 | 1.088 | 1.0878 | 1.0878 | 1.0878 | 0.96728 | 0.31671 | 14.7564 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41403 | 0.049493 | 1.0878 | 1.0878 | 1.0878 | 1.0878 | 0.96728 | 0.31671 | 14.7564 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41403 | 0.049493 | 1.0878 | 1.0878 | 1.0878 | 1.0878 | 0.96728 | 0.31671 | 419 | 316.7073 | 0.96728 | 1.0878 | 0.0049667 | 14.7564
0.42 | 0.4602 | 0.052283 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.3304 | 14.966 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41503 | 0.049507 | 1.088 | 1.0879 | 1.0879 | 1.0879 | 0.96732 | 0.31786 | 14.7744 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41503 | 0.049507 | 1.0879 | 1.0879 | 1.0879 | 1.0879 | 0.96732 | 0.31786 | 14.7744 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41503 | 0.049507 | 1.0879 | 1.0879 | 1.0879 | 1.0879 | 0.96732 | 0.31786 | 420 | 317.8644 | 0.96732 | 1.0879 | 0.0049667 | 14.7744
0.421 | 0.46124 | 0.052295 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.33158 | 14.984 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41603 | 0.049522 | 1.0881 | 1.0879 | 1.0879 | 1.0879 | 0.96737 | 0.31902 | 14.7923 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41603 | 0.049522 | 1.0879 | 1.0879 | 1.0879 | 1.0879 | 0.96737 | 0.31902 | 14.7923 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41603 | 0.049522 | 1.0879 | 1.0879 | 1.0879 | 1.0879 | 0.96737 | 0.31902 | 421 | 319.0229 | 0.96737 | 1.0879 | 0.0049667 | 14.7923
0.422 | 0.46228 | 0.052308 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.33277 | 15.0019 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41703 | 0.049536 | 1.0881 | 1.0879 | 1.0879 | 1.0879 | 0.96741 | 0.32018 | 14.8102 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41703 | 0.049536 | 1.0879 | 1.0879 | 1.0879 | 1.0879 | 0.96741 | 0.32018 | 14.8102 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41703 | 0.049536 | 1.0879 | 1.0879 | 1.0879 | 1.0879 | 0.96741 | 0.32018 | 422 | 320.1829 | 0.96741 | 1.0879 | 0.0049667 | 14.8102
0.423 | 0.46332 | 0.05232 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.33397 | 15.0198 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41803 | 0.049551 | 1.0881 | 1.088 | 1.088 | 1.088 | 0.96745 | 0.32134 | 14.8281 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41803 | 0.049551 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96745 | 0.32134 | 14.8281 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41803 | 0.049551 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96745 | 0.32134 | 423 | 321.3442 | 0.96745 | 1.088 | 0.0049667 | 14.8281
0.424 | 0.46436 | 0.052332 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.33516 | 15.0376 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41903 | 0.049565 | 1.0882 | 1.088 | 1.088 | 1.088 | 0.96749 | 0.32251 | 14.846 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41903 | 0.049565 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96749 | 0.32251 | 14.846 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.41903 | 0.049565 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96749 | 0.32251 | 424 | 322.5069 | 0.96749 | 1.088 | 0.0049667 | 14.846
0.425 | 0.4654 | 0.052344 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.33635 | 15.0555 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42003 | 0.049579 | 1.0882 | 1.088 | 1.088 | 1.088 | 0.96753 | 0.32367 | 14.8638 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42003 | 0.049579 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96753 | 0.32367 | 14.8638 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42003 | 0.049579 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96753 | 0.32367 | 425 | 323.6711 | 0.96753 | 1.088 | 0.0049667 | 14.8638
0.426 | 0.46644 | 0.052356 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.33755 | 15.0733 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42103 | 0.049594 | 1.0882 | 1.088 | 1.088 | 1.088 | 0.96757 | 0.32484 | 14.8816 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42103 | 0.049594 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96757 | 0.32484 | 14.8816 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42103 | 0.049594 | 1.088 | 1.088 | 1.088 | 1.088 | 0.96757 | 0.32484 | 426 | 324.8366 | 0.96757 | 1.088 | 0.0049667 | 14.8816
0.427 | 0.46748 | 0.052368 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.33875 | 15.0911 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42203 | 0.049608 | 1.0883 | 1.0881 | 1.0881 | 1.0881 | 0.96761 | 0.326 | 14.8994 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42203 | 0.049608 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 0.96761 | 0.326 | 14.8994 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42203 | 0.049608 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 0.96761 | 0.326 | 427 | 326.0036 | 0.96761 | 1.0881 | 0.0049667 | 14.8994
0.428 | 0.46853 | 0.05238 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.33995 | 15.1089 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42303 | 0.049622 | 1.0883 | 1.0881 | 1.0881 | 1.0881 | 0.96765 | 0.32717 | 14.9172 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42303 | 0.049622 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 0.96765 | 0.32717 | 14.9172 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42303 | 0.049622 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 0.96765 | 0.32717 | 428 | 327.1719 | 0.96765 | 1.0881 | 0.0049667 | 14.9172
0.429 | 0.46957 | 0.052392 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.34115 | 15.1266 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42403 | 0.049636 | 1.0883 | 1.0881 | 1.0881 | 1.0881 | 0.96769 | 0.32834 | 14.935 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42403 | 0.049636 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 0.96769 | 0.32834 | 14.935 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42403 | 0.049636 | 1.0881 | 1.0881 | 1.0881 | 1.0881 | 0.96769 | 0.32834 | 429 | 328.3417 | 0.96769 | 1.0881 | 0.0049667 | 14.935
0.43 | 0.47061 | 0.052404 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.34235 | 15.1444 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42503 | 0.04965 | 1.0883 | 1.0882 | 1.0882 | 1.0882 | 0.96773 | 0.32951 | 14.9527 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42503 | 0.04965 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96773 | 0.32951 | 14.9527 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42503 | 0.04965 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96773 | 0.32951 | 430 | 329.5128 | 0.96773 | 1.0882 | 0.0049667 | 14.9527
0.431 | 0.47165 | 0.052416 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.34355 | 15.1621 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42603 | 0.049664 | 1.0884 | 1.0882 | 1.0882 | 1.0882 | 0.96777 | 0.33069 | 14.9704 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42603 | 0.049664 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96777 | 0.33069 | 14.9704 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42603 | 0.049664 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96777 | 0.33069 | 431 | 330.6853 | 0.96777 | 1.0882 | 0.0049667 | 14.9704
0.432 | 0.47269 | 0.052428 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.34475 | 15.1798 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42703 | 0.049678 | 1.0884 | 1.0882 | 1.0882 | 1.0882 | 0.96781 | 0.33186 | 14.9881 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42703 | 0.049678 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96781 | 0.33186 | 14.9881 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42703 | 0.049678 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96781 | 0.33186 | 432 | 331.8592 | 0.96781 | 1.0882 | 0.0049667 | 14.9881
0.433 | 0.47373 | 0.05244 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.34596 | 15.1975 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42803 | 0.049691 | 1.0884 | 1.0883 | 1.0882 | 1.0882 | 0.96785 | 0.33303 | 15.0058 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42803 | 0.049691 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96785 | 0.33303 | 15.0058 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42803 | 0.049691 | 1.0882 | 1.0882 | 1.0882 | 1.0882 | 0.96785 | 0.33303 | 433 | 333.0346 | 0.96785 | 1.0882 | 0.0049667 | 15.0058
0.434 | 0.47477 | 0.052451 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.34717 | 15.2151 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42903 | 0.049705 | 1.0885 | 1.0883 | 1.0883 | 1.0883 | 0.96788 | 0.33421 | 15.0234 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42903 | 0.049705 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 0.96788 | 0.33421 | 15.0234 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.42903 | 0.049705 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 0.96788 | 0.33421 | 434 | 334.2113 | 0.96788 | 1.0883 | 0.0049667 | 15.0234
0.435 | 0.47581 | 0.052463 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.34838 | 15.2328 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43003 | 0.049719 | 1.0885 | 1.0883 | 1.0883 | 1.0883 | 0.96792 | 0.33539 | 15.0411 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43003 | 0.049719 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 0.96792 | 0.33539 | 15.0411 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43003 | 0.049719 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 0.96792 | 0.33539 | 435 | 335.3893 | 0.96792 | 1.0883 | 0.0049667 | 15.0411
0.436 | 0.47685 | 0.052475 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.34959 | 15.2504 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43103 | 0.049732 | 1.0885 | 1.0883 | 1.0883 | 1.0883 | 0.96796 | 0.33657 | 15.0587 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43103 | 0.049732 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 0.96796 | 0.33657 | 15.0587 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43103 | 0.049732 | 1.0883 | 1.0883 | 1.0883 | 1.0883 | 0.96796 | 0.33657 | 436 | 336.5688 | 0.96796 | 1.0883 | 0.0049667 | 15.0587
0.437 | 0.4779 | 0.052486 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.3508 | 15.268 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43203 | 0.049746 | 1.0885 | 1.0884 | 1.0884 | 1.0884 | 0.968 | 0.33775 | 15.0763 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43203 | 0.049746 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 0.968 | 0.33775 | 15.0763 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43203 | 0.049746 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 0.968 | 0.33775 | 437 | 337.7497 | 0.968 | 1.0884 | 0.0049667 | 15.0763
0.438 | 0.47894 | 0.052498 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.35201 | 15.2855 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43303 | 0.04976 | 1.0886 | 1.0884 | 1.0884 | 1.0884 | 0.96804 | 0.33893 | 15.0938 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43303 | 0.04976 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 0.96804 | 0.33893 | 15.0938 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43303 | 0.04976 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 0.96804 | 0.33893 | 438 | 338.9319 | 0.96804 | 1.0884 | 0.0049667 | 15.0938
0.439 | 0.47998 | 0.052509 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.35322 | 15.3031 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43403 | 0.049773 | 1.0886 | 1.0884 | 1.0884 | 1.0884 | 0.96808 | 0.34012 | 15.1114 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43403 | 0.049773 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 0.96808 | 0.34012 | 15.1114 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43403 | 0.049773 | 1.0884 | 1.0884 | 1.0884 | 1.0884 | 0.96808 | 0.34012 | 439 | 340.1155 | 0.96808 | 1.0884 | 0.0049667 | 15.1114
0.44 | 0.48102 | 0.05252 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.35444 | 15.3206 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43503 | 0.049786 | 1.0886 | 1.0885 | 1.0885 | 1.0885 | 0.96811 | 0.3413 | 15.1289 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43503 | 0.049786 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96811 | 0.3413 | 15.1289 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43503 | 0.049786 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96811 | 0.3413 | 440 | 341.3005 | 0.96811 | 1.0885 | 0.0049667 | 15.1289
0.441 | 0.48206 | 0.052532 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.35566 | 15.3381 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43603 | 0.0498 | 1.0887 | 1.0885 | 1.0885 | 1.0885 | 0.96815 | 0.34249 | 15.1464 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43603 | 0.0498 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96815 | 0.34249 | 15.1464 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43603 | 0.0498 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96815 | 0.34249 | 441 | 342.4869 | 0.96815 | 1.0885 | 0.0049667 | 15.1464
0.442 | 0.4831 | 0.052543 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.35688 | 15.3556 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43703 | 0.049813 | 1.0887 | 1.0885 | 1.0885 | 1.0885 | 0.96819 | 0.34367 | 15.1639 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43703 | 0.049813 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96819 | 0.34367 | 15.1639 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43703 | 0.049813 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96819 | 0.34367 | 442 | 343.6747 | 0.96819 | 1.0885 | 0.0049667 | 15.1639
0.443 | 0.48414 | 0.052554 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.3581 | 15.3731 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43803 | 0.049826 | 1.0887 | 1.0885 | 1.0885 | 1.0885 | 0.96823 | 0.34486 | 15.1814 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43803 | 0.049826 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96823 | 0.34486 | 15.1814 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43803 | 0.049826 | 1.0885 | 1.0885 | 1.0885 | 1.0885 | 0.96823 | 0.34486 | 443 | 344.8638 | 0.96823 | 1.0885 | 0.0049667 | 15.1814
0.444 | 0.48518 | 0.052565 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.35932 | 15.3906 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43903 | 0.049839 | 1.0887 | 1.0886 | 1.0886 | 1.0886 | 0.96826 | 0.34605 | 15.1988 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43903 | 0.049839 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.96826 | 0.34605 | 15.1988 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.43903 | 0.049839 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.96826 | 0.34605 | 444 | 346.0543 | 0.96826 | 1.0886 | 0.0049667 | 15.1988
0.445 | 0.48622 | 0.052577 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.36054 | 15.408 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44003 | 0.049852 | 1.0888 | 1.0886 | 1.0886 | 1.0886 | 0.9683 | 0.34725 | 15.2163 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44003 | 0.049852 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.9683 | 0.34725 | 15.2163 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44003 | 0.049852 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.9683 | 0.34725 | 445 | 347.2462 | 0.9683 | 1.0886 | 0.0049667 | 15.2163
0.446 | 0.48727 | 0.052588 | 1.0946 | 1.0945 | 1.0945 | 1.0945 | 0.36176 | 15.4254 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44103 | 0.049866 | 1.0888 | 1.0886 | 1.0886 | 1.0886 | 0.96834 | 0.34844 | 15.2337 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44103 | 0.049866 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.96834 | 0.34844 | 15.2337 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44103 | 0.049866 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.96834 | 0.34844 | 446 | 348.4394 | 0.96834 | 1.0886 | 0.0049667 | 15.2337
0.447 | 0.48831 | 0.052599 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.36299 | 15.4428 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44203 | 0.049879 | 1.0888 | 1.0887 | 1.0886 | 1.0886 | 0.96837 | 0.34963 | 15.2511 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44203 | 0.049879 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.96837 | 0.34963 | 15.2511 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44203 | 0.049879 | 1.0886 | 1.0886 | 1.0886 | 1.0886 | 0.96837 | 0.34963 | 447 | 349.634 | 0.96837 | 1.0886 | 0.0049667 | 15.2511
0.448 | 0.48935 | 0.05261 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.36422 | 15.4602 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44303 | 0.049891 | 1.0889 | 1.0887 | 1.0887 | 1.0887 | 0.96841 | 0.35083 | 15.2684 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44303 | 0.049891 | 1.0887 | 1.0887 | 1.0887 | 1.0887 | 0.96841 | 0.35083 | 15.2684 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44303 | 0.049891 | 1.0887 | 1.0887 | 1.0887 | 1.0887 | 0.96841 | 0.35083 | 448 | 350.83 | 0.96841 | 1.0887 | 0.0049667 | 15.2684
0.449 | 0.49039 | 0.052621 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.36544 | 15.4776 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44403 | 0.049904 | 1.0889 | 1.0887 | 1.0887 | 1.0887 | 0.96845 | 0.35203 | 15.2858 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44403 | 0.049904 | 1.0887 | 1.0887 | 1.0887 | 1.0887 | 0.96845 | 0.35203 | 15.2858 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44403 | 0.049904 | 1.0887 | 1.0887 | 1.0887 | 1.0887 | 0.96845 | 0.35203 | 449 | 352.0273 | 0.96845 | 1.0887 | 0.0049667 | 15.2858
0.45 | 0.49143 | 0.052632 | 1.0947 | 1.0946 | 1.0946 | 1.0946 | 0.36667 | 15.4949 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44503 | 0.049917 | 1.0889 | 1.0887 | 1.0887 | 1.0887 | 0.96848 | 0.35323 | 15.3031 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44503 | 0.049917 | 1.0887 | 1.0887 | 1.0887 | 1.0887 | 0.96848 | 0.35323 | 15.3031 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44503 | 0.049917 | 1.0887 | 1.0887 | 1.0887 | 1.0887 | 0.96848 | 0.35323 | 450 | 353.2261 | 0.96848 | 1.0887 | 0.0049667 | 15.3031
0.451 | 0.49247 | 0.052643 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.3679 | 15.5122 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44603 | 0.04993 | 1.0889 | 1.0888 | 1.0888 | 1.0888 | 0.96852 | 0.35443 | 15.3204 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44603 | 0.04993 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96852 | 0.35443 | 15.3204 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44603 | 0.04993 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96852 | 0.35443 | 451 | 354.4261 | 0.96852 | 1.0888 | 0.0049667 | 15.3204
0.452 | 0.49351 | 0.052653 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.36914 | 15.5295 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44703 | 0.049943 | 1.089 | 1.0888 | 1.0888 | 1.0888 | 0.96855 | 0.35563 | 15.3377 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44703 | 0.049943 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96855 | 0.35563 | 15.3377 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44703 | 0.049943 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96855 | 0.35563 | 452 | 355.6275 | 0.96855 | 1.0888 | 0.0049667 | 15.3377
0.453 | 0.49455 | 0.052664 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.37037 | 15.5468 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44803 | 0.049955 | 1.089 | 1.0888 | 1.0888 | 1.0888 | 0.96859 | 0.35683 | 15.355 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44803 | 0.049955 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96859 | 0.35683 | 15.355 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44803 | 0.049955 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96859 | 0.35683 | 453 | 356.8303 | 0.96859 | 1.0888 | 0.0049667 | 15.355
0.454 | 0.4956 | 0.052675 | 1.0948 | 1.0947 | 1.0946 | 1.0946 | 0.3716 | 15.5641 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44903 | 0.049968 | 1.089 | 1.0888 | 1.0888 | 1.0888 | 0.96862 | 0.35803 | 15.3722 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44903 | 0.049968 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96862 | 0.35803 | 15.3722 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.44903 | 0.049968 | 1.0888 | 1.0888 | 1.0888 | 1.0888 | 0.96862 | 0.35803 | 454 | 358.0345 | 0.96862 | 1.0888 | 0.0049667 | 15.3722
0.455 | 0.49664 | 0.052686 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.37284 | 15.5813 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45003 | 0.049981 | 1.089 | 1.0889 | 1.0889 | 1.0889 | 0.96866 | 0.35924 | 15.3895 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45003 | 0.049981 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96866 | 0.35924 | 15.3895 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45003 | 0.049981 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96866 | 0.35924 | 455 | 359.24 | 0.96866 | 1.0889 | 0.0049667 | 15.3895
0.456 | 0.49768 | 0.052696 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.37408 | 15.5985 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45103 | 0.049993 | 1.0891 | 1.0889 | 1.0889 | 1.0889 | 0.96869 | 0.36045 | 15.4067 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45103 | 0.049993 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96869 | 0.36045 | 15.4067 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45103 | 0.049993 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96869 | 0.36045 | 456 | 360.4468 | 0.96869 | 1.0889 | 0.0049667 | 15.4067
0.457 | 0.49872 | 0.052707 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.37532 | 15.6157 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45203 | 0.050006 | 1.0891 | 1.0889 | 1.0889 | 1.0889 | 0.96873 | 0.36166 | 15.4239 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45203 | 0.050006 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96873 | 0.36166 | 15.4239 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45203 | 0.050006 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96873 | 0.36166 | 457 | 361.655 | 0.96873 | 1.0889 | 0.0049667 | 15.4239
0.458 | 0.49976 | 0.052718 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.37656 | 15.6329 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45303 | 0.050018 | 1.0891 | 1.0889 | 1.0889 | 1.0889 | 0.96876 | 0.36286 | 15.4411 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45303 | 0.050018 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96876 | 0.36286 | 15.4411 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45303 | 0.050018 | 1.0889 | 1.0889 | 1.0889 | 1.0889 | 0.96876 | 0.36286 | 458 | 362.8646 | 0.96876 | 1.0889 | 0.0049667 | 15.4411
0.459 | 0.5008 | 0.052728 | 1.0949 | 1.0948 | 1.0948 | 1.0948 | 0.3778 | 15.6501 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45403 | 0.05003 | 1.0892 | 1.089 | 1.089 | 1.089 | 0.9688 | 0.36408 | 15.4582 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45403 | 0.05003 | 1.089 | 1.089 | 1.089 | 1.089 | 0.9688 | 0.36408 | 15.4582 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45403 | 0.05003 | 1.089 | 1.089 | 1.089 | 1.089 | 0.9688 | 0.36408 | 459 | 364.0755 | 0.9688 | 1.089 | 0.0049667 | 15.4582
0.46 | 0.50184 | 0.052739 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.37904 | 15.6672 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45503 | 0.050043 | 1.0892 | 1.089 | 1.089 | 1.089 | 0.96883 | 0.36529 | 15.4754 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45503 | 0.050043 | 1.089 | 1.089 | 1.089 | 1.089 | 0.96883 | 0.36529 | 15.4754 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45503 | 0.050043 | 1.089 | 1.089 | 1.089 | 1.089 | 0.96883 | 0.36529 | 460 | 365.2877 | 0.96883 | 1.089 | 0.0049667 | 15.4754
0.461 | 0.50288 | 0.052749 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.38029 | 15.6843 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45603 | 0.050055 | 1.0892 | 1.089 | 1.089 | 1.089 | 0.96887 | 0.3665 | 15.4925 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45603 | 0.050055 | 1.089 | 1.089 | 1.089 | 1.089 | 0.96887 | 0.3665 | 15.4925 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45603 | 0.050055 | 1.089 | 1.089 | 1.089 | 1.089 | 0.96887 | 0.3665 | 461 | 366.5013 | 0.96887 | 1.089 | 0.0049667 | 15.4925
0.462 | 0.50392 | 0.052759 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.38153 | 15.7015 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45703 | 0.050067 | 1.0892 | 1.0891 | 1.089 | 1.089 | 0.9689 | 0.36772 | 15.5096 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45703 | 0.050067 | 1.089 | 1.089 | 1.089 | 1.089 | 0.9689 | 0.36772 | 15.5096 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45703 | 0.050067 | 1.089 | 1.089 | 1.089 | 1.089 | 0.9689 | 0.36772 | 462 | 367.7163 | 0.9689 | 1.089 | 0.0049667 | 15.5096
0.463 | 0.50497 | 0.05277 | 1.095 | 1.0949 | 1.0949 | 1.0949 | 0.38278 | 15.7185 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45803 | 0.050079 | 1.0893 | 1.0891 | 1.0891 | 1.0891 | 0.96894 | 0.36893 | 15.5267 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45803 | 0.050079 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 0.96894 | 0.36893 | 15.5267 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45803 | 0.050079 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 0.96894 | 0.36893 | 463 | 368.9326 | 0.96894 | 1.0891 | 0.0049667 | 15.5267
0.464 | 0.50601 | 0.05278 | 1.095 | 1.0949 | 1.0949 | 1.0949 | 0.38403 | 15.7356 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45903 | 0.050092 | 1.0893 | 1.0891 | 1.0891 | 1.0891 | 0.96897 | 0.37015 | 15.5437 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45903 | 0.050092 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 0.96897 | 0.37015 | 15.5437 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.45903 | 0.050092 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 0.96897 | 0.37015 | 464 | 370.1502 | 0.96897 | 1.0891 | 0.0049667 | 15.5437
0.465 | 0.50705 | 0.05279 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.38528 | 15.7527 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46003 | 0.050104 | 1.0893 | 1.0891 | 1.0891 | 1.0891 | 0.969 | 0.37137 | 15.5608 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46003 | 0.050104 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 0.969 | 0.37137 | 15.5608 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46003 | 0.050104 | 1.0891 | 1.0891 | 1.0891 | 1.0891 | 0.969 | 0.37137 | 465 | 371.3692 | 0.969 | 1.0891 | 0.0049667 | 15.5608
0.466 | 0.50809 | 0.052801 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.38653 | 15.7697 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46103 | 0.050116 | 1.0893 | 1.0892 | 1.0892 | 1.0892 | 0.96904 | 0.37259 | 15.5778 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46103 | 0.050116 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96904 | 0.37259 | 15.5778 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46103 | 0.050116 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96904 | 0.37259 | 466 | 372.5895 | 0.96904 | 1.0892 | 0.0049667 | 15.5778
0.467 | 0.50913 | 0.052811 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.38778 | 15.7867 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46203 | 0.050128 | 1.0894 | 1.0892 | 1.0892 | 1.0892 | 0.96907 | 0.37381 | 15.5948 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46203 | 0.050128 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96907 | 0.37381 | 15.5948 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46203 | 0.050128 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96907 | 0.37381 | 467 | 373.8111 | 0.96907 | 1.0892 | 0.0049667 | 15.5948
0.468 | 0.51017 | 0.052821 | 1.0951 | 1.095 | 1.095 | 1.095 | 0.38904 | 15.8037 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46303 | 0.05014 | 1.0894 | 1.0892 | 1.0892 | 1.0892 | 0.96911 | 0.37503 | 15.6118 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46303 | 0.05014 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96911 | 0.37503 | 15.6118 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46303 | 0.05014 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96911 | 0.37503 | 468 | 375.0341 | 0.96911 | 1.0892 | 0.0049667 | 15.6118
0.469 | 0.51121 | 0.052831 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.39029 | 15.8207 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46403 | 0.050152 | 1.0894 | 1.0892 | 1.0892 | 1.0892 | 0.96914 | 0.37626 | 15.6288 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46403 | 0.050152 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96914 | 0.37626 | 15.6288 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46403 | 0.050152 | 1.0892 | 1.0892 | 1.0892 | 1.0892 | 0.96914 | 0.37626 | 469 | 376.2584 | 0.96914 | 1.0892 | 0.0049667 | 15.6288
0.47 | 0.51225 | 0.052841 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.39155 | 15.8377 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46503 | 0.050163 | 1.0894 | 1.0893 | 1.0893 | 1.0893 | 0.96917 | 0.37748 | 15.6457 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46503 | 0.050163 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.96917 | 0.37748 | 15.6457 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46503 | 0.050163 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.96917 | 0.37748 | 470 | 377.4841 | 0.96917 | 1.0893 | 0.0049667 | 15.6457
0.471 | 0.5133 | 0.052851 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.39281 | 15.8546 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46603 | 0.050175 | 1.0895 | 1.0893 | 1.0893 | 1.0893 | 0.9692 | 0.37871 | 15.6626 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46603 | 0.050175 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.9692 | 0.37871 | 15.6626 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46603 | 0.050175 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.9692 | 0.37871 | 471 | 378.7111 | 0.9692 | 1.0893 | 0.0049667 | 15.6626
0.472 | 0.51434 | 0.052861 | 1.0952 | 1.0951 | 1.0951 | 1.0951 | 0.39407 | 15.8715 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46703 | 0.050187 | 1.0895 | 1.0893 | 1.0893 | 1.0893 | 0.96924 | 0.37994 | 15.6796 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46703 | 0.050187 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.96924 | 0.37994 | 15.6796 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46703 | 0.050187 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.96924 | 0.37994 | 472 | 379.9394 | 0.96924 | 1.0893 | 0.0049667 | 15.6796
0.473 | 0.51538 | 0.052871 | 1.0952 | 1.0951 | 1.0951 | 1.0951 | 0.39533 | 15.8885 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46803 | 0.050199 | 1.0895 | 1.0893 | 1.0893 | 1.0893 | 0.96927 | 0.38117 | 15.6964 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46803 | 0.050199 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.96927 | 0.38117 | 15.6964 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46803 | 0.050199 | 1.0893 | 1.0893 | 1.0893 | 1.0893 | 0.96927 | 0.38117 | 473 | 381.169 | 0.96927 | 1.0893 | 0.0049667 | 15.6964
0.474 | 0.51642 | 0.052881 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.39659 | 15.9053 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46903 | 0.05021 | 1.0895 | 1.0894 | 1.0894 | 1.0894 | 0.9693 | 0.3824 | 15.7133 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46903 | 0.05021 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.9693 | 0.3824 | 15.7133 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.46903 | 0.05021 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.9693 | 0.3824 | 474 | 382.4 | 0.9693 | 1.0894 | 0.0049667 | 15.7133
0.475 | 0.51746 | 0.052891 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.39785 | 15.9222 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47003 | 0.050222 | 1.0896 | 1.0894 | 1.0894 | 1.0894 | 0.96934 | 0.38363 | 15.7302 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47003 | 0.050222 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.96934 | 0.38363 | 15.7302 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47003 | 0.050222 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.96934 | 0.38363 | 475 | 383.6323 | 0.96934 | 1.0894 | 0.0049667 | 15.7302
0.476 | 0.5185 | 0.052901 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.39912 | 15.9391 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47103 | 0.050234 | 1.0896 | 1.0894 | 1.0894 | 1.0894 | 0.96937 | 0.38487 | 15.747 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47103 | 0.050234 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.96937 | 0.38487 | 15.747 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47103 | 0.050234 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.96937 | 0.38487 | 476 | 384.8659 | 0.96937 | 1.0894 | 0.0049667 | 15.747
0.477 | 0.51954 | 0.052911 | 1.0953 | 1.0952 | 1.0952 | 1.0952 | 0.40039 | 15.9559 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47203 | 0.050245 | 1.0896 | 1.0894 | 1.0894 | 1.0894 | 0.9694 | 0.3861 | 15.7639 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47203 | 0.050245 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.9694 | 0.3861 | 15.7639 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47203 | 0.050245 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.9694 | 0.3861 | 477 | 386.1009 | 0.9694 | 1.0894 | 0.0049667 | 15.7639
0.478 | 0.52058 | 0.05292 | 1.0953 | 1.0952 | 1.0952 | 1.0952 | 0.40165 | 15.9727 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47303 | 0.050257 | 1.0896 | 1.0895 | 1.0894 | 1.0894 | 0.96943 | 0.38734 | 15.7807 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47303 | 0.050257 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.96943 | 0.38734 | 15.7807 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47303 | 0.050257 | 1.0894 | 1.0894 | 1.0894 | 1.0894 | 0.96943 | 0.38734 | 478 | 387.3371 | 0.96943 | 1.0894 | 0.0049667 | 15.7807
0.479 | 0.52162 | 0.05293 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.40292 | 15.9895 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47403 | 0.050268 | 1.0897 | 1.0895 | 1.0895 | 1.0895 | 0.96946 | 0.38857 | 15.7975 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47403 | 0.050268 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.96946 | 0.38857 | 15.7975 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47403 | 0.050268 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.96946 | 0.38857 | 479 | 388.5747 | 0.96946 | 1.0895 | 0.0049667 | 15.7975
0.48 | 0.52267 | 0.05294 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.40419 | 16.0063 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.47493 | 0.050227 | 1.0896 | 1.0894 | 1.0894 | 1.0894 | 0.96889 | 0.38953 | 15.8104 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47503 | 0.050279 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.9695 | 0.38981 | 15.8142 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47503 | 0.050279 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.9695 | 0.38981 | 480 | 389.8136 | 0.9695 | 1.0895 | 0.0049667 | 15.8142
0.481 | 0.52371 | 0.052949 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.40546 | 16.0231 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.47593 | 0.050238 | 1.0896 | 1.0894 | 1.0894 | 1.0894 | 0.96892 | 0.39077 | 15.8271 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47603 | 0.050291 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.96953 | 0.39105 | 15.831 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47603 | 0.050291 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.96953 | 0.39105 | 481 | 391.0538 | 0.96953 | 1.0895 | 0.0049667 | 15.831
0.482 | 0.52475 | 0.052959 | 1.0954 | 1.0953 | 1.0953 | 1.0953 | 0.40674 | 16.0398 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.47693 | 0.05025 | 1.0896 | 1.0894 | 1.0894 | 1.0894 | 0.96895 | 0.39201 | 15.8439 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47703 | 0.050302 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.96956 | 0.3923 | 15.8477 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47703 | 0.050302 | 1.0895 | 1.0895 | 1.0895 | 1.0895 | 0.96956 | 0.3923 | 482 | 392.2954 | 0.96956 | 1.0895 | 0.0049667 | 15.8477
0.483 | 0.52579 | 0.052969 | 1.0954 | 1.0953 | 1.0953 | 1.0953 | 0.40801 | 16.0566 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.47793 | 0.050261 | 1.0896 | 1.0895 | 1.0895 | 1.0895 | 0.96898 | 0.39325 | 15.8606 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47803 | 0.050313 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96959 | 0.39354 | 15.8644 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47803 | 0.050313 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96959 | 0.39354 | 483 | 393.5382 | 0.96959 | 1.0896 | 0.0049667 | 15.8644
0.484 | 0.52683 | 0.052978 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.40929 | 16.0733 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.47893 | 0.050272 | 1.0897 | 1.0895 | 1.0895 | 1.0895 | 0.96901 | 0.3945 | 15.8773 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47903 | 0.050325 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96962 | 0.39478 | 15.8811 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.47903 | 0.050325 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96962 | 0.39478 | 484 | 394.7824 | 0.96962 | 1.0896 | 0.0049667 | 15.8811
0.485 | 0.52787 | 0.052988 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.41056 | 16.09 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.47993 | 0.050283 | 1.0897 | 1.0895 | 1.0895 | 1.0895 | 0.96905 | 0.39574 | 15.894 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48003 | 0.050336 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96965 | 0.39603 | 15.8978 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48003 | 0.050336 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96965 | 0.39603 | 485 | 396.0279 | 0.96965 | 1.0896 | 0.0049667 | 15.8978
0.486 | 0.52891 | 0.052997 | 1.0955 | 1.0954 | 1.0953 | 1.0953 | 0.41184 | 16.1067 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48093 | 0.050294 | 1.0897 | 1.0895 | 1.0895 | 1.0895 | 0.96908 | 0.39699 | 15.9106 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48103 | 0.050347 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96968 | 0.39727 | 15.9145 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48103 | 0.050347 | 1.0896 | 1.0896 | 1.0896 | 1.0896 | 0.96968 | 0.39727 | 486 | 397.2747 | 0.96968 | 1.0896 | 0.0049667 | 15.9145
0.487 | 0.52995 | 0.053006 | 1.0955 | 1.0954 | 1.0954 | 1.0954 | 0.41312 | 16.1233 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48193 | 0.050306 | 1.0897 | 1.0896 | 1.0896 | 1.0896 | 0.96911 | 0.39823 | 15.9273 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48203 | 0.050358 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96971 | 0.39852 | 15.9311 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48203 | 0.050358 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96971 | 0.39852 | 487 | 398.5228 | 0.96971 | 1.0897 | 0.0049667 | 15.9311
0.488 | 0.531 | 0.053016 | 1.0955 | 1.0954 | 1.0954 | 1.0954 | 0.4144 | 16.14 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48293 | 0.050317 | 1.0898 | 1.0896 | 1.0896 | 1.0896 | 0.96914 | 0.39948 | 15.9439 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48303 | 0.050369 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96974 | 0.39977 | 15.9478 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48303 | 0.050369 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96974 | 0.39977 | 488 | 399.7722 | 0.96974 | 1.0897 | 0.0049667 | 15.9478
0.489 | 0.53204 | 0.053025 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.41568 | 16.1566 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48393 | 0.050328 | 1.0898 | 1.0896 | 1.0896 | 1.0896 | 0.96917 | 0.40073 | 15.9605 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48403 | 0.05038 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96977 | 0.40102 | 15.9644 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48403 | 0.05038 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96977 | 0.40102 | 489 | 401.0229 | 0.96977 | 1.0897 | 0.0049667 | 15.9644
0.49 | 0.53308 | 0.053035 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.41697 | 16.1732 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48493 | 0.050339 | 1.0898 | 1.0896 | 1.0896 | 1.0896 | 0.9692 | 0.40198 | 15.9771 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48503 | 0.050391 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96981 | 0.40227 | 15.981 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48503 | 0.050391 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96981 | 0.40227 | 490 | 402.2749 | 0.96981 | 1.0897 | 0.0049667 | 15.981
0.491 | 0.53412 | 0.053044 | 1.0956 | 1.0955 | 1.0955 | 1.0954 | 0.41825 | 16.1898 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48593 | 0.05035 | 1.0898 | 1.0897 | 1.0896 | 1.0896 | 0.96923 | 0.40324 | 15.9937 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48603 | 0.050402 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96984 | 0.40353 | 15.9976 | 0.0057 | 0.0046 | 0.0049667 | 0.64098 | 0.48603 | 0.050402 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96984 | 0.40353 | 491 | 403.5282 | 0.96984 | 1.0898 | 0.0049667 | 15.9976
0.492 | 0.53516 | 0.053053 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.41954 | 16.2064 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48693 | 0.050361 | 1.0899 | 1.0897 | 1.0897 | 1.0897 | 0.96926 | 0.40449 | 16.0103 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48693 | 0.050361 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96926 | 0.40449 | 16.0103 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48693 | 0.050361 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96926 | 0.40449 | 492 | 404.4907 | 0.96926 | 1.0897 | 0.0050667 | 16.0103
0.493 | 0.5362 | 0.053062 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.42083 | 16.2229 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48793 | 0.050371 | 1.0899 | 1.0897 | 1.0897 | 1.0897 | 0.9693 | 0.40575 | 16.0268 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48793 | 0.050371 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.9693 | 0.40575 | 16.0268 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48793 | 0.050371 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.9693 | 0.40575 | 493 | 405.746 | 0.9693 | 1.0897 | 0.0050667 | 16.0268
0.494 | 0.53724 | 0.053071 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.42211 | 16.2395 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48893 | 0.050382 | 1.0899 | 1.0897 | 1.0897 | 1.0897 | 0.96933 | 0.407 | 16.0433 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48893 | 0.050382 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96933 | 0.407 | 16.0433 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48893 | 0.050382 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96933 | 0.407 | 494 | 407.0026 | 0.96933 | 1.0897 | 0.0050667 | 16.0433
0.495 | 0.53828 | 0.053081 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.4234 | 16.256 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48993 | 0.050393 | 1.0899 | 1.0897 | 1.0897 | 1.0897 | 0.96936 | 0.40826 | 16.0598 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48993 | 0.050393 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96936 | 0.40826 | 16.0598 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.48993 | 0.050393 | 1.0897 | 1.0897 | 1.0897 | 1.0897 | 0.96936 | 0.40826 | 495 | 408.2605 | 0.96936 | 1.0897 | 0.0050667 | 16.0598
0.496 | 0.53932 | 0.05309 | 1.0957 | 1.0956 | 1.0956 | 1.0955 | 0.4247 | 16.2725 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49093 | 0.050404 | 1.0899 | 1.0898 | 1.0898 | 1.0898 | 0.96939 | 0.40952 | 16.0763 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49093 | 0.050404 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96939 | 0.40952 | 16.0763 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49093 | 0.050404 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96939 | 0.40952 | 496 | 409.5197 | 0.96939 | 1.0898 | 0.0050667 | 16.0763
0.497 | 0.54037 | 0.053099 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 0.42599 | 16.289 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49193 | 0.050415 | 1.09 | 1.0898 | 1.0898 | 1.0898 | 0.96942 | 0.41078 | 16.0928 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49193 | 0.050415 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96942 | 0.41078 | 16.0928 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49193 | 0.050415 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96942 | 0.41078 | 497 | 410.7802 | 0.96942 | 1.0898 | 0.0050667 | 16.0928
0.498 | 0.54141 | 0.053108 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 0.42728 | 16.3055 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49293 | 0.050425 | 1.09 | 1.0898 | 1.0898 | 1.0898 | 0.96945 | 0.41204 | 16.1093 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49293 | 0.050425 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96945 | 0.41204 | 16.1093 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49293 | 0.050425 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96945 | 0.41204 | 498 | 412.0419 | 0.96945 | 1.0898 | 0.0050667 | 16.1093
0.499 | 0.54245 | 0.053117 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.42858 | 16.3219 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49393 | 0.050436 | 1.09 | 1.0898 | 1.0898 | 1.0898 | 0.96948 | 0.41331 | 16.1257 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49393 | 0.050436 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96948 | 0.41331 | 16.1257 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49393 | 0.050436 | 1.0898 | 1.0898 | 1.0898 | 1.0898 | 0.96948 | 0.41331 | 499 | 413.305 | 0.96948 | 1.0898 | 0.0050667 | 16.1257
0.5 | 0.54349 | 0.053126 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.42987 | 16.3384 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49493 | 0.050446 | 1.09 | 1.0899 | 1.0899 | 1.0899 | 0.96951 | 0.41457 | 16.1421 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49493 | 0.050446 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96951 | 0.41457 | 16.1421 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49493 | 0.050446 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96951 | 0.41457 | 500 | 414.5694 | 0.96951 | 1.0899 | 0.0050667 | 16.1421
0.501 | 0.54453 | 0.053135 | 1.0958 | 1.0957 | 1.0956 | 1.0956 | 0.43117 | 16.3548 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49593 | 0.050457 | 1.0901 | 1.0899 | 1.0899 | 1.0899 | 0.96954 | 0.41584 | 16.1586 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49593 | 0.050457 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96954 | 0.41584 | 16.1586 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49593 | 0.050457 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96954 | 0.41584 | 501 | 415.835 | 0.96954 | 1.0899 | 0.0050667 | 16.1586
0.502 | 0.54557 | 0.053144 | 1.0958 | 1.0957 | 1.0957 | 1.0957 | 0.43247 | 16.3712 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49693 | 0.050468 | 1.0901 | 1.0899 | 1.0899 | 1.0899 | 0.96957 | 0.4171 | 16.175 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49693 | 0.050468 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96957 | 0.4171 | 16.175 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49693 | 0.050468 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96957 | 0.4171 | 502 | 417.102 | 0.96957 | 1.0899 | 0.0050667 | 16.175
0.503 | 0.54661 | 0.053153 | 1.0958 | 1.0957 | 1.0957 | 1.0957 | 0.43377 | 16.3876 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49793 | 0.050478 | 1.0901 | 1.0899 | 1.0899 | 1.0899 | 0.9696 | 0.41837 | 16.1913 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49793 | 0.050478 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.9696 | 0.41837 | 16.1913 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49793 | 0.050478 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.9696 | 0.41837 | 503 | 418.3702 | 0.9696 | 1.0899 | 0.0050667 | 16.1913
0.504 | 0.54765 | 0.053161 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.43507 | 16.404 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49893 | 0.050488 | 1.0901 | 1.0899 | 1.0899 | 1.0899 | 0.96962 | 0.41964 | 16.2077 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49893 | 0.050488 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96962 | 0.41964 | 16.2077 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49893 | 0.050488 | 1.0899 | 1.0899 | 1.0899 | 1.0899 | 0.96962 | 0.41964 | 504 | 419.6397 | 0.96962 | 1.0899 | 0.0050667 | 16.2077
0.505 | 0.54869 | 0.05317 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.43638 | 16.4204 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49993 | 0.050499 | 1.0901 | 1.09 | 1.09 | 1.09 | 0.96965 | 0.42091 | 16.224 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49993 | 0.050499 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96965 | 0.42091 | 16.224 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.49993 | 0.050499 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96965 | 0.42091 | 505 | 420.9105 | 0.96965 | 1.09 | 0.0050667 | 16.224
0.506 | 0.54974 | 0.053179 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.43768 | 16.4367 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50093 | 0.050509 | 1.0902 | 1.09 | 1.09 | 1.09 | 0.96968 | 0.42218 | 16.2404 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50093 | 0.050509 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96968 | 0.42218 | 16.2404 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50093 | 0.050509 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96968 | 0.42218 | 506 | 422.1826 | 0.96968 | 1.09 | 0.0050667 | 16.2404
0.507 | 0.55078 | 0.053188 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.43899 | 16.453 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50193 | 0.050519 | 1.0902 | 1.09 | 1.09 | 1.09 | 0.96971 | 0.42346 | 16.2567 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50193 | 0.050519 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96971 | 0.42346 | 16.2567 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50193 | 0.050519 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96971 | 0.42346 | 507 | 423.456 | 0.96971 | 1.09 | 0.0050667 | 16.2567
0.508 | 0.55182 | 0.053196 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.44029 | 16.4694 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50293 | 0.05053 | 1.0902 | 1.09 | 1.09 | 1.09 | 0.96974 | 0.42473 | 16.273 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50293 | 0.05053 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96974 | 0.42473 | 16.273 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50293 | 0.05053 | 1.09 | 1.09 | 1.09 | 1.09 | 0.96974 | 0.42473 | 508 | 424.7306 | 0.96974 | 1.09 | 0.0050667 | 16.273
0.509 | 0.55286 | 0.053205 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.4416 | 16.4856 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50393 | 0.05054 | 1.0902 | 1.0901 | 1.0901 | 1.0901 | 0.96977 | 0.42601 | 16.2892 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50393 | 0.05054 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96977 | 0.42601 | 16.2892 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50393 | 0.05054 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96977 | 0.42601 | 509 | 426.0066 | 0.96977 | 1.0901 | 0.0050667 | 16.2892
0.51 | 0.5539 | 0.053214 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.44291 | 16.5019 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50493 | 0.05055 | 1.0903 | 1.0901 | 1.0901 | 1.0901 | 0.9698 | 0.42728 | 16.3055 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50493 | 0.05055 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.9698 | 0.42728 | 16.3055 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50493 | 0.05055 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.9698 | 0.42728 | 510 | 427.2838 | 0.9698 | 1.0901 | 0.0050667 | 16.3055
0.511 | 0.55494 | 0.053222 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.44422 | 16.5182 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50593 | 0.05056 | 1.0903 | 1.0901 | 1.0901 | 1.0901 | 0.96983 | 0.42856 | 16.3218 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50593 | 0.05056 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96983 | 0.42856 | 16.3218 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50593 | 0.05056 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96983 | 0.42856 | 511 | 428.5623 | 0.96983 | 1.0901 | 0.0050667 | 16.3218
0.512 | 0.55598 | 0.053231 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.44554 | 16.5344 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50693 | 0.050571 | 1.0903 | 1.0901 | 1.0901 | 1.0901 | 0.96986 | 0.42984 | 16.338 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50693 | 0.050571 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96986 | 0.42984 | 16.338 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50693 | 0.050571 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96986 | 0.42984 | 512 | 429.842 | 0.96986 | 1.0901 | 0.0050667 | 16.338
0.513 | 0.55702 | 0.053239 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.44685 | 16.5507 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50793 | 0.050581 | 1.0903 | 1.0901 | 1.0901 | 1.0901 | 0.96988 | 0.43112 | 16.3542 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50793 | 0.050581 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96988 | 0.43112 | 16.3542 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50793 | 0.050581 | 1.0901 | 1.0901 | 1.0901 | 1.0901 | 0.96988 | 0.43112 | 513 | 431.123 | 0.96988 | 1.0901 | 0.0050667 | 16.3542
0.514 | 0.55807 | 0.053248 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.44816 | 16.5669 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50893 | 0.050591 | 1.0903 | 1.0902 | 1.0902 | 1.0902 | 0.96991 | 0.43241 | 16.3704 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50893 | 0.050591 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.96991 | 0.43241 | 16.3704 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50893 | 0.050591 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.96991 | 0.43241 | 514 | 432.4054 | 0.96991 | 1.0902 | 0.0050667 | 16.3704
0.515 | 0.55911 | 0.053256 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.44948 | 16.5831 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50993 | 0.050601 | 1.0904 | 1.0902 | 1.0902 | 1.0902 | 0.96994 | 0.43369 | 16.3866 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50993 | 0.050601 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.96994 | 0.43369 | 16.3866 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.50993 | 0.050601 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.96994 | 0.43369 | 515 | 433.6889 | 0.96994 | 1.0902 | 0.0050667 | 16.3866
0.516 | 0.56015 | 0.053265 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.4508 | 16.5993 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51093 | 0.050611 | 1.0904 | 1.0902 | 1.0902 | 1.0902 | 0.96997 | 0.43497 | 16.4027 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51093 | 0.050611 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.96997 | 0.43497 | 16.4027 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51093 | 0.050611 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.96997 | 0.43497 | 516 | 434.9738 | 0.96997 | 1.0902 | 0.0050667 | 16.4027
0.517 | 0.56119 | 0.053273 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.45212 | 16.6155 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51193 | 0.050621 | 1.0904 | 1.0902 | 1.0902 | 1.0902 | 0.97 | 0.43626 | 16.4189 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51193 | 0.050621 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.97 | 0.43626 | 16.4189 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51193 | 0.050621 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.97 | 0.43626 | 517 | 436.2599 | 0.97 | 1.0902 | 0.0050667 | 16.4189
0.518 | 0.56223 | 0.053282 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.45344 | 16.6316 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51293 | 0.050631 | 1.0904 | 1.0903 | 1.0902 | 1.0902 | 0.97002 | 0.43755 | 16.435 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51293 | 0.050631 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.97002 | 0.43755 | 16.435 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51293 | 0.050631 | 1.0902 | 1.0902 | 1.0902 | 1.0902 | 0.97002 | 0.43755 | 518 | 437.5473 | 0.97002 | 1.0902 | 0.0050667 | 16.435
0.519 | 0.56327 | 0.05329 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.45476 | 16.6477 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51393 | 0.05064 | 1.0905 | 1.0903 | 1.0903 | 1.0903 | 0.97005 | 0.43884 | 16.4512 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51393 | 0.05064 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97005 | 0.43884 | 16.4512 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51393 | 0.05064 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97005 | 0.43884 | 519 | 438.8359 | 0.97005 | 1.0903 | 0.0050667 | 16.4512
0.52 | 0.56431 | 0.053298 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.45608 | 16.6639 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51493 | 0.05065 | 1.0905 | 1.0903 | 1.0903 | 1.0903 | 0.97008 | 0.44013 | 16.4673 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51493 | 0.05065 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97008 | 0.44013 | 16.4673 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51493 | 0.05065 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97008 | 0.44013 | 520 | 440.1259 | 0.97008 | 1.0903 | 0.0050667 | 16.4673
0.521 | 0.56535 | 0.053307 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.4574 | 16.68 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51593 | 0.05066 | 1.0905 | 1.0903 | 1.0903 | 1.0903 | 0.97011 | 0.44142 | 16.4833 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51593 | 0.05066 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97011 | 0.44142 | 16.4833 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51593 | 0.05066 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97011 | 0.44142 | 521 | 441.4171 | 0.97011 | 1.0903 | 0.0050667 | 16.4833
0.522 | 0.56639 | 0.053315 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.45873 | 16.6961 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51693 | 0.05067 | 1.0905 | 1.0903 | 1.0903 | 1.0903 | 0.97013 | 0.44271 | 16.4994 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51693 | 0.05067 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97013 | 0.44271 | 16.4994 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51693 | 0.05067 | 1.0903 | 1.0903 | 1.0903 | 1.0903 | 0.97013 | 0.44271 | 522 | 442.7095 | 0.97013 | 1.0903 | 0.0050667 | 16.4994
0.523 | 0.56744 | 0.053323 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.46005 | 16.7121 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51793 | 0.05068 | 1.0905 | 1.0904 | 1.0904 | 1.0904 | 0.97016 | 0.444 | 16.5155 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51793 | 0.05068 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97016 | 0.444 | 16.5155 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51793 | 0.05068 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97016 | 0.444 | 523 | 444.0032 | 0.97016 | 1.0904 | 0.0050667 | 16.5155
0.524 | 0.56848 | 0.053331 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.46138 | 16.7282 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51893 | 0.050689 | 1.0906 | 1.0904 | 1.0904 | 1.0904 | 0.97019 | 0.4453 | 16.5315 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51893 | 0.050689 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97019 | 0.4453 | 16.5315 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51893 | 0.050689 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97019 | 0.4453 | 524 | 445.2982 | 0.97019 | 1.0904 | 0.0050667 | 16.5315
0.525 | 0.56952 | 0.05334 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.46271 | 16.7442 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51993 | 0.050699 | 1.0906 | 1.0904 | 1.0904 | 1.0904 | 0.97022 | 0.44659 | 16.5475 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51993 | 0.050699 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97022 | 0.44659 | 16.5475 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.51993 | 0.050699 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97022 | 0.44659 | 525 | 446.5944 | 0.97022 | 1.0904 | 0.0050667 | 16.5475
0.526 | 0.57056 | 0.053348 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.46404 | 16.7603 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52093 | 0.050709 | 1.0906 | 1.0904 | 1.0904 | 1.0904 | 0.97024 | 0.44789 | 16.5635 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52093 | 0.050709 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97024 | 0.44789 | 16.5635 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52093 | 0.050709 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97024 | 0.44789 | 526 | 447.8919 | 0.97024 | 1.0904 | 0.0050667 | 16.5635
0.527 | 0.5716 | 0.053356 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.46537 | 16.7763 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52193 | 0.050718 | 1.0906 | 1.0904 | 1.0904 | 1.0904 | 0.97027 | 0.44919 | 16.5795 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52193 | 0.050718 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97027 | 0.44919 | 16.5795 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52193 | 0.050718 | 1.0904 | 1.0904 | 1.0904 | 1.0904 | 0.97027 | 0.44919 | 527 | 449.1907 | 0.97027 | 1.0904 | 0.0050667 | 16.5795
0.528 | 0.57264 | 0.053364 | 1.0963 | 1.0962 | 1.0961 | 1.0961 | 0.46671 | 16.7923 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52293 | 0.050728 | 1.0906 | 1.0905 | 1.0905 | 1.0905 | 0.9703 | 0.45049 | 16.5955 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52293 | 0.050728 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.9703 | 0.45049 | 16.5955 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52293 | 0.050728 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.9703 | 0.45049 | 528 | 450.4907 | 0.9703 | 1.0905 | 0.0050667 | 16.5955
0.529 | 0.57368 | 0.053372 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.46804 | 16.8083 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52393 | 0.050737 | 1.0907 | 1.0905 | 1.0905 | 1.0905 | 0.97032 | 0.45179 | 16.6115 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52393 | 0.050737 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.97032 | 0.45179 | 16.6115 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52393 | 0.050737 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.97032 | 0.45179 | 529 | 451.7919 | 0.97032 | 1.0905 | 0.0050667 | 16.6115
0.53 | 0.57472 | 0.05338 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.46938 | 16.8242 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52493 | 0.050747 | 1.0907 | 1.0905 | 1.0905 | 1.0905 | 0.97035 | 0.45309 | 16.6274 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52493 | 0.050747 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.97035 | 0.45309 | 16.6274 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52493 | 0.050747 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.97035 | 0.45309 | 530 | 453.0944 | 0.97035 | 1.0905 | 0.0050667 | 16.6274
0.531 | 0.57577 | 0.053388 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.47071 | 16.8402 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52593 | 0.050756 | 1.0907 | 1.0905 | 1.0905 | 1.0905 | 0.97038 | 0.4544 | 16.6434 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52593 | 0.050756 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.97038 | 0.4544 | 16.6434 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52593 | 0.050756 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.97038 | 0.4544 | 531 | 454.3982 | 0.97038 | 1.0905 | 0.0050667 | 16.6434
0.532 | 0.57681 | 0.053396 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.47205 | 16.8561 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52693 | 0.050766 | 1.0907 | 1.0905 | 1.0905 | 1.0905 | 0.9704 | 0.4557 | 16.6593 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52693 | 0.050766 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.9704 | 0.4557 | 16.6593 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52693 | 0.050766 | 1.0905 | 1.0905 | 1.0905 | 1.0905 | 0.9704 | 0.4557 | 532 | 455.7032 | 0.9704 | 1.0905 | 0.0050667 | 16.6593
0.533 | 0.57785 | 0.053404 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.47339 | 16.8721 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52793 | 0.050775 | 1.0907 | 1.0906 | 1.0906 | 1.0906 | 0.97043 | 0.45701 | 16.6752 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52793 | 0.050775 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97043 | 0.45701 | 16.6752 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52793 | 0.050775 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97043 | 0.45701 | 533 | 457.0095 | 0.97043 | 1.0906 | 0.0050667 | 16.6752
0.534 | 0.57889 | 0.053412 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.47473 | 16.888 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52893 | 0.050784 | 1.0908 | 1.0906 | 1.0906 | 1.0906 | 0.97045 | 0.45832 | 16.6911 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52893 | 0.050784 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97045 | 0.45832 | 16.6911 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52893 | 0.050784 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97045 | 0.45832 | 534 | 458.317 | 0.97045 | 1.0906 | 0.0050667 | 16.6911
0.535 | 0.57993 | 0.05342 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.47607 | 16.9039 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52993 | 0.050794 | 1.0908 | 1.0906 | 1.0906 | 1.0906 | 0.97048 | 0.45963 | 16.7069 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52993 | 0.050794 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97048 | 0.45963 | 16.7069 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.52993 | 0.050794 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97048 | 0.45963 | 535 | 459.6257 | 0.97048 | 1.0906 | 0.0050667 | 16.7069
0.536 | 0.58097 | 0.053428 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.47741 | 16.9197 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53093 | 0.050803 | 1.0908 | 1.0906 | 1.0906 | 1.0906 | 0.97051 | 0.46094 | 16.7228 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53093 | 0.050803 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97051 | 0.46094 | 16.7228 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53093 | 0.050803 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97051 | 0.46094 | 536 | 460.9357 | 0.97051 | 1.0906 | 0.0050667 | 16.7228
0.537 | 0.58201 | 0.053436 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.47876 | 16.9356 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53193 | 0.050812 | 1.0908 | 1.0906 | 1.0906 | 1.0906 | 0.97053 | 0.46225 | 16.7386 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53193 | 0.050812 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97053 | 0.46225 | 16.7386 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53193 | 0.050812 | 1.0906 | 1.0906 | 1.0906 | 1.0906 | 0.97053 | 0.46225 | 537 | 462.247 | 0.97053 | 1.0906 | 0.0050667 | 16.7386
0.538 | 0.58305 | 0.053444 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.4801 | 16.9515 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53293 | 0.050822 | 1.0908 | 1.0907 | 1.0907 | 1.0907 | 0.97056 | 0.46356 | 16.7545 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53293 | 0.050822 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97056 | 0.46356 | 16.7545 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53293 | 0.050822 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97056 | 0.46356 | 538 | 463.5595 | 0.97056 | 1.0907 | 0.0050667 | 16.7545
0.539 | 0.58409 | 0.053451 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.48145 | 16.9673 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53393 | 0.050831 | 1.0909 | 1.0907 | 1.0907 | 1.0907 | 0.97058 | 0.46487 | 16.7703 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53393 | 0.050831 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97058 | 0.46487 | 16.7703 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53393 | 0.050831 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97058 | 0.46487 | 539 | 464.8732 | 0.97058 | 1.0907 | 0.0050667 | 16.7703
0.54 | 0.58514 | 0.053459 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.4828 | 16.9831 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53493 | 0.05084 | 1.0909 | 1.0907 | 1.0907 | 1.0907 | 0.97061 | 0.46619 | 16.7861 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53493 | 0.05084 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97061 | 0.46619 | 16.7861 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53493 | 0.05084 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97061 | 0.46619 | 540 | 466.1882 | 0.97061 | 1.0907 | 0.0050667 | 16.7861
0.541 | 0.58618 | 0.053467 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.48415 | 16.9989 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53593 | 0.050849 | 1.0909 | 1.0907 | 1.0907 | 1.0907 | 0.97064 | 0.4675 | 16.8019 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53593 | 0.050849 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97064 | 0.4675 | 16.8019 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53593 | 0.050849 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97064 | 0.4675 | 541 | 467.5044 | 0.97064 | 1.0907 | 0.0050667 | 16.8019
0.542 | 0.58722 | 0.053475 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.4855 | 17.0147 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53693 | 0.050858 | 1.0909 | 1.0907 | 1.0907 | 1.0907 | 0.97066 | 0.46882 | 16.8176 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53693 | 0.050858 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97066 | 0.46882 | 16.8176 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53693 | 0.050858 | 1.0907 | 1.0907 | 1.0907 | 1.0907 | 0.97066 | 0.46882 | 542 | 468.8219 | 0.97066 | 1.0907 | 0.0050667 | 16.8176
0.543 | 0.58826 | 0.053482 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.48685 | 17.0305 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53793 | 0.050867 | 1.0909 | 1.0908 | 1.0908 | 1.0908 | 0.97069 | 0.47014 | 16.8334 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53793 | 0.050867 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97069 | 0.47014 | 16.8334 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53793 | 0.050867 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97069 | 0.47014 | 543 | 470.1406 | 0.97069 | 1.0908 | 0.0050667 | 16.8334
0.544 | 0.5893 | 0.05349 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.4882 | 17.0462 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53893 | 0.050876 | 1.091 | 1.0908 | 1.0908 | 1.0908 | 0.97071 | 0.47146 | 16.8491 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53893 | 0.050876 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97071 | 0.47146 | 16.8491 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53893 | 0.050876 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97071 | 0.47146 | 544 | 471.4605 | 0.97071 | 1.0908 | 0.0050667 | 16.8491
0.545 | 0.59034 | 0.053497 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.48956 | 17.062 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53993 | 0.050885 | 1.091 | 1.0908 | 1.0908 | 1.0908 | 0.97074 | 0.47278 | 16.8648 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53993 | 0.050885 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97074 | 0.47278 | 16.8648 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.53993 | 0.050885 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97074 | 0.47278 | 545 | 472.7817 | 0.97074 | 1.0908 | 0.0050667 | 16.8648
0.546 | 0.59138 | 0.053505 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.49091 | 17.0777 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54093 | 0.050894 | 1.091 | 1.0908 | 1.0908 | 1.0908 | 0.97076 | 0.4741 | 16.8806 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54093 | 0.050894 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97076 | 0.4741 | 16.8806 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54093 | 0.050894 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97076 | 0.4741 | 546 | 474.1041 | 0.97076 | 1.0908 | 0.0050667 | 16.8806
0.547 | 0.59242 | 0.053513 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.49227 | 17.0934 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54193 | 0.050903 | 1.091 | 1.0908 | 1.0908 | 1.0908 | 0.97079 | 0.47543 | 16.8963 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54193 | 0.050903 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97079 | 0.47543 | 16.8963 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54193 | 0.050903 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97079 | 0.47543 | 547 | 475.4277 | 0.97079 | 1.0908 | 0.0050667 | 16.8963
0.548 | 0.59347 | 0.05352 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.49363 | 17.1091 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54293 | 0.050912 | 1.091 | 1.0909 | 1.0908 | 1.0908 | 0.97081 | 0.47675 | 16.9119 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54293 | 0.050912 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97081 | 0.47675 | 16.9119 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54293 | 0.050912 | 1.0908 | 1.0908 | 1.0908 | 1.0908 | 0.97081 | 0.47675 | 548 | 476.7526 | 0.97081 | 1.0908 | 0.0050667 | 16.9119
0.549 | 0.59451 | 0.053528 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.49499 | 17.1248 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54393 | 0.050921 | 1.091 | 1.0909 | 1.0909 | 1.0909 | 0.97084 | 0.47808 | 16.9276 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54393 | 0.050921 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97084 | 0.47808 | 16.9276 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54393 | 0.050921 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97084 | 0.47808 | 549 | 478.0787 | 0.97084 | 1.0909 | 0.0050667 | 16.9276
0.55 | 0.59555 | 0.053535 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.49635 | 17.1405 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54493 | 0.05093 | 1.0911 | 1.0909 | 1.0909 | 1.0909 | 0.97086 | 0.47941 | 16.9433 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54493 | 0.05093 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97086 | 0.47941 | 16.9433 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54493 | 0.05093 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97086 | 0.47941 | 550 | 479.406 | 0.97086 | 1.0909 | 0.0050667 | 16.9433
0.551 | 0.59659 | 0.053543 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.49771 | 17.1562 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54593 | 0.050939 | 1.0911 | 1.0909 | 1.0909 | 1.0909 | 0.97089 | 0.48073 | 16.9589 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54593 | 0.050939 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97089 | 0.48073 | 16.9589 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54593 | 0.050939 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97089 | 0.48073 | 551 | 480.7346 | 0.97089 | 1.0909 | 0.0050667 | 16.9589
0.552 | 0.59763 | 0.05355 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.49907 | 17.1718 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54693 | 0.050948 | 1.0911 | 1.0909 | 1.0909 | 1.0909 | 0.97091 | 0.48206 | 16.9745 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54693 | 0.050948 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97091 | 0.48206 | 16.9745 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54693 | 0.050948 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97091 | 0.48206 | 552 | 482.0644 | 0.97091 | 1.0909 | 0.0050667 | 16.9745
0.553 | 0.59867 | 0.053558 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.50043 | 17.1874 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54793 | 0.050956 | 1.0911 | 1.0909 | 1.0909 | 1.0909 | 0.97093 | 0.4834 | 16.9901 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54793 | 0.050956 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97093 | 0.4834 | 16.9901 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54793 | 0.050956 | 1.0909 | 1.0909 | 1.0909 | 1.0909 | 0.97093 | 0.4834 | 553 | 483.3954 | 0.97093 | 1.0909 | 0.0050667 | 16.9901
0.554 | 0.59971 | 0.053565 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.5018 | 17.2031 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54893 | 0.050965 | 1.0911 | 1.091 | 1.091 | 1.091 | 0.97096 | 0.48473 | 17.0057 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54893 | 0.050965 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97096 | 0.48473 | 17.0057 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54893 | 0.050965 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97096 | 0.48473 | 554 | 484.7276 | 0.97096 | 1.091 | 0.0050667 | 17.0057
0.555 | 0.60075 | 0.053572 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.50317 | 17.2187 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54993 | 0.050974 | 1.0912 | 1.091 | 1.091 | 1.091 | 0.97098 | 0.48606 | 17.0213 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54993 | 0.050974 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97098 | 0.48606 | 17.0213 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.54993 | 0.050974 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97098 | 0.48606 | 555 | 486.0611 | 0.97098 | 1.091 | 0.0050667 | 17.0213
0.556 | 0.60179 | 0.05358 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.50453 | 17.2343 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55093 | 0.050982 | 1.0912 | 1.091 | 1.091 | 1.091 | 0.97101 | 0.4874 | 17.0369 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55093 | 0.050982 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97101 | 0.4874 | 17.0369 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55093 | 0.050982 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97101 | 0.4874 | 556 | 487.3958 | 0.97101 | 1.091 | 0.0050667 | 17.0369
0.557 | 0.60284 | 0.053587 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.5059 | 17.2498 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55193 | 0.050991 | 1.0912 | 1.091 | 1.091 | 1.091 | 0.97103 | 0.48873 | 17.0524 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55193 | 0.050991 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97103 | 0.48873 | 17.0524 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55193 | 0.050991 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97103 | 0.48873 | 557 | 488.7317 | 0.97103 | 1.091 | 0.0050667 | 17.0524
0.558 | 0.60388 | 0.053594 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.50727 | 17.2654 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55293 | 0.051 | 1.0912 | 1.091 | 1.091 | 1.091 | 0.97105 | 0.49007 | 17.0679 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55293 | 0.051 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97105 | 0.49007 | 17.0679 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55293 | 0.051 | 1.091 | 1.091 | 1.091 | 1.091 | 0.97105 | 0.49007 | 558 | 490.0688 | 0.97105 | 1.091 | 0.0050667 | 17.0679
0.559 | 0.60492 | 0.053602 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.50865 | 17.2809 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55393 | 0.051008 | 1.0912 | 1.0911 | 1.0911 | 1.0911 | 0.97108 | 0.49141 | 17.0835 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55393 | 0.051008 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97108 | 0.49141 | 17.0835 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55393 | 0.051008 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97108 | 0.49141 | 559 | 491.4072 | 0.97108 | 1.0911 | 0.0050667 | 17.0835
0.56 | 0.60596 | 0.053609 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.51002 | 17.2965 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55493 | 0.051017 | 1.0913 | 1.0911 | 1.0911 | 1.0911 | 0.9711 | 0.49275 | 17.099 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55493 | 0.051017 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.9711 | 0.49275 | 17.099 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55493 | 0.051017 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.9711 | 0.49275 | 560 | 492.7467 | 0.9711 | 1.0911 | 0.0050667 | 17.099
0.561 | 0.607 | 0.053616 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.51139 | 17.312 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55593 | 0.051025 | 1.0913 | 1.0911 | 1.0911 | 1.0911 | 0.97113 | 0.49409 | 17.1145 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55593 | 0.051025 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97113 | 0.49409 | 17.1145 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55593 | 0.051025 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97113 | 0.49409 | 561 | 494.0875 | 0.97113 | 1.0911 | 0.0050667 | 17.1145
0.562 | 0.60804 | 0.053623 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.51277 | 17.3275 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55693 | 0.051034 | 1.0913 | 1.0911 | 1.0911 | 1.0911 | 0.97115 | 0.49543 | 17.13 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55693 | 0.051034 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97115 | 0.49543 | 17.13 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55693 | 0.051034 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97115 | 0.49543 | 562 | 495.4295 | 0.97115 | 1.0911 | 0.0050667 | 17.13
0.563 | 0.60908 | 0.05363 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.51414 | 17.343 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55793 | 0.051042 | 1.0913 | 1.0911 | 1.0911 | 1.0911 | 0.97117 | 0.49677 | 17.1454 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55793 | 0.051042 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97117 | 0.49677 | 17.1454 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55793 | 0.051042 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.97117 | 0.49677 | 563 | 496.7727 | 0.97117 | 1.0911 | 0.0050667 | 17.1454
0.564 | 0.61012 | 0.053638 | 1.0969 | 1.0968 | 1.0967 | 1.0967 | 0.51552 | 17.3585 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55893 | 0.051051 | 1.0913 | 1.0912 | 1.0911 | 1.0911 | 0.9712 | 0.49812 | 17.1609 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55893 | 0.051051 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.9712 | 0.49812 | 17.1609 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55893 | 0.051051 | 1.0911 | 1.0911 | 1.0911 | 1.0911 | 0.9712 | 0.49812 | 564 | 498.1172 | 0.9712 | 1.0911 | 0.0050667 | 17.1609
0.565 | 0.61116 | 0.053645 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.5169 | 17.3739 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55993 | 0.051059 | 1.0913 | 1.0912 | 1.0912 | 1.0912 | 0.97122 | 0.49946 | 17.1763 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55993 | 0.051059 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97122 | 0.49946 | 17.1763 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.55993 | 0.051059 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97122 | 0.49946 | 565 | 499.4628 | 0.97122 | 1.0912 | 0.0050667 | 17.1763
0.566 | 0.61221 | 0.053652 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.51828 | 17.3894 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56093 | 0.051068 | 1.0914 | 1.0912 | 1.0912 | 1.0912 | 0.97124 | 0.50081 | 17.1917 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56093 | 0.051068 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97124 | 0.50081 | 17.1917 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56093 | 0.051068 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97124 | 0.50081 | 566 | 500.8097 | 0.97124 | 1.0912 | 0.0050667 | 17.1917
0.567 | 0.61325 | 0.053659 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.51966 | 17.4048 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56193 | 0.051076 | 1.0914 | 1.0912 | 1.0912 | 1.0912 | 0.97127 | 0.50216 | 17.2072 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56193 | 0.051076 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97127 | 0.50216 | 17.2072 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56193 | 0.051076 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97127 | 0.50216 | 567 | 502.1577 | 0.97127 | 1.0912 | 0.0050667 | 17.2072
0.568 | 0.61429 | 0.053666 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.52105 | 17.4202 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56293 | 0.051084 | 1.0914 | 1.0912 | 1.0912 | 1.0912 | 0.97129 | 0.50351 | 17.2225 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56293 | 0.051084 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97129 | 0.50351 | 17.2225 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56293 | 0.051084 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97129 | 0.50351 | 568 | 503.507 | 0.97129 | 1.0912 | 0.0050667 | 17.2225
0.569 | 0.61533 | 0.053673 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.52243 | 17.4357 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56393 | 0.051093 | 1.0914 | 1.0912 | 1.0912 | 1.0912 | 0.97131 | 0.50486 | 17.2379 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56393 | 0.051093 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97131 | 0.50486 | 17.2379 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56393 | 0.051093 | 1.0912 | 1.0912 | 1.0912 | 1.0912 | 0.97131 | 0.50486 | 569 | 504.8575 | 0.97131 | 1.0912 | 0.0050667 | 17.2379
0.57 | 0.61637 | 0.05368 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.52382 | 17.4511 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56493 | 0.051101 | 1.0914 | 1.0913 | 1.0913 | 1.0913 | 0.97134 | 0.50621 | 17.2533 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56493 | 0.051101 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97134 | 0.50621 | 17.2533 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56493 | 0.051101 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97134 | 0.50621 | 570 | 506.2092 | 0.97134 | 1.0913 | 0.0050667 | 17.2533
0.571 | 0.61741 | 0.053687 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.5252 | 17.4664 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56593 | 0.051109 | 1.0915 | 1.0913 | 1.0913 | 1.0913 | 0.97136 | 0.50756 | 17.2687 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56593 | 0.051109 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97136 | 0.50756 | 17.2687 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56593 | 0.051109 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97136 | 0.50756 | 571 | 507.5621 | 0.97136 | 1.0913 | 0.0050667 | 17.2687
0.572 | 0.61845 | 0.053694 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.52659 | 17.4818 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56693 | 0.051117 | 1.0915 | 1.0913 | 1.0913 | 1.0913 | 0.97138 | 0.50892 | 17.284 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56693 | 0.051117 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97138 | 0.50892 | 17.284 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56693 | 0.051117 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97138 | 0.50892 | 572 | 508.9162 | 0.97138 | 1.0913 | 0.0050667 | 17.284
0.573 | 0.61949 | 0.053701 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.52798 | 17.4972 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56793 | 0.051126 | 1.0915 | 1.0913 | 1.0913 | 1.0913 | 0.9714 | 0.51027 | 17.2993 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56793 | 0.051126 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.9714 | 0.51027 | 17.2993 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56793 | 0.051126 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.9714 | 0.51027 | 573 | 510.2715 | 0.9714 | 1.0913 | 0.0050667 | 17.2993
0.574 | 0.62054 | 0.053708 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.52937 | 17.5125 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56893 | 0.051134 | 1.0915 | 1.0913 | 1.0913 | 1.0913 | 0.97143 | 0.51163 | 17.3146 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56893 | 0.051134 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97143 | 0.51163 | 17.3146 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56893 | 0.051134 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97143 | 0.51163 | 574 | 511.628 | 0.97143 | 1.0913 | 0.0050667 | 17.3146
0.575 | 0.62158 | 0.053715 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.53076 | 17.5278 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56993 | 0.051142 | 1.0915 | 1.0913 | 1.0913 | 1.0913 | 0.97145 | 0.51299 | 17.33 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56993 | 0.051142 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97145 | 0.51299 | 17.33 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.56993 | 0.051142 | 1.0913 | 1.0913 | 1.0913 | 1.0913 | 0.97145 | 0.51299 | 575 | 512.9858 | 0.97145 | 1.0913 | 0.0050667 | 17.33
0.576 | 0.62262 | 0.053722 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.53215 | 17.5431 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57093 | 0.05115 | 1.0915 | 1.0914 | 1.0914 | 1.0914 | 0.97147 | 0.51434 | 17.3452 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57093 | 0.05115 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97147 | 0.51434 | 17.3452 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57093 | 0.05115 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97147 | 0.51434 | 576 | 514.3447 | 0.97147 | 1.0914 | 0.0050667 | 17.3452
0.577 | 0.62366 | 0.053728 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.53355 | 17.5584 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57193 | 0.051158 | 1.0916 | 1.0914 | 1.0914 | 1.0914 | 0.97149 | 0.5157 | 17.3605 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57193 | 0.051158 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97149 | 0.5157 | 17.3605 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57193 | 0.051158 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97149 | 0.5157 | 577 | 515.7048 | 0.97149 | 1.0914 | 0.0050667 | 17.3605
0.578 | 0.6247 | 0.053735 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.53494 | 17.5737 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57293 | 0.051166 | 1.0916 | 1.0914 | 1.0914 | 1.0914 | 0.97152 | 0.51707 | 17.3758 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57293 | 0.051166 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97152 | 0.51707 | 17.3758 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57293 | 0.051166 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97152 | 0.51707 | 578 | 517.0661 | 0.97152 | 1.0914 | 0.0050667 | 17.3758
0.579 | 0.62574 | 0.053742 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.53634 | 17.589 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57393 | 0.051174 | 1.0916 | 1.0914 | 1.0914 | 1.0914 | 0.97154 | 0.51843 | 17.391 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57393 | 0.051174 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97154 | 0.51843 | 17.391 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57393 | 0.051174 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97154 | 0.51843 | 579 | 518.4286 | 0.97154 | 1.0914 | 0.0050667 | 17.391
0.58 | 0.62678 | 0.053749 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.53773 | 17.6043 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57493 | 0.051182 | 1.0916 | 1.0914 | 1.0914 | 1.0914 | 0.97156 | 0.51979 | 17.4063 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57493 | 0.051182 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97156 | 0.51979 | 17.4063 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57493 | 0.051182 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97156 | 0.51979 | 580 | 519.7924 | 0.97156 | 1.0914 | 0.0050667 | 17.4063
0.581 | 0.62782 | 0.053756 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.53913 | 17.6195 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57593 | 0.05119 | 1.0916 | 1.0915 | 1.0914 | 1.0914 | 0.97158 | 0.52116 | 17.4215 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57593 | 0.05119 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97158 | 0.52116 | 17.4215 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57593 | 0.05119 | 1.0914 | 1.0914 | 1.0914 | 1.0914 | 0.97158 | 0.52116 | 581 | 521.1573 | 0.97158 | 1.0914 | 0.0050667 | 17.4215
0.582 | 0.62886 | 0.053762 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.54053 | 17.6348 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57693 | 0.051198 | 1.0916 | 1.0915 | 1.0915 | 1.0915 | 0.97161 | 0.52252 | 17.4367 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57693 | 0.051198 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97161 | 0.52252 | 17.4367 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57693 | 0.051198 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97161 | 0.52252 | 582 | 522.5234 | 0.97161 | 1.0915 | 0.0050667 | 17.4367
0.583 | 0.62991 | 0.053769 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.54193 | 17.65 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57793 | 0.051206 | 1.0917 | 1.0915 | 1.0915 | 1.0915 | 0.97163 | 0.52389 | 17.4519 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57793 | 0.051206 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97163 | 0.52389 | 17.4519 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57793 | 0.051206 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97163 | 0.52389 | 583 | 523.8907 | 0.97163 | 1.0915 | 0.0050667 | 17.4519
0.584 | 0.63095 | 0.053776 | 1.0972 | 1.0971 | 1.097 | 1.097 | 0.54334 | 17.6652 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57893 | 0.051214 | 1.0917 | 1.0915 | 1.0915 | 1.0915 | 0.97165 | 0.52526 | 17.4671 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57893 | 0.051214 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97165 | 0.52526 | 17.4671 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57893 | 0.051214 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97165 | 0.52526 | 584 | 525.2592 | 0.97165 | 1.0915 | 0.0050667 | 17.4671
0.585 | 0.63199 | 0.053782 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.54474 | 17.6804 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57993 | 0.051222 | 1.0917 | 1.0915 | 1.0915 | 1.0915 | 0.97167 | 0.52663 | 17.4822 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57993 | 0.051222 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97167 | 0.52663 | 17.4822 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.57993 | 0.051222 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97167 | 0.52663 | 585 | 526.6289 | 0.97167 | 1.0915 | 0.0050667 | 17.4822
0.586 | 0.63303 | 0.053789 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.54614 | 17.6956 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58093 | 0.05123 | 1.0917 | 1.0915 | 1.0915 | 1.0915 | 0.97169 | 0.528 | 17.4974 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58093 | 0.05123 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97169 | 0.528 | 17.4974 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58093 | 0.05123 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97169 | 0.528 | 586 | 527.9997 | 0.97169 | 1.0915 | 0.0050667 | 17.4974
0.587 | 0.63407 | 0.053796 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.54755 | 17.7107 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58193 | 0.051238 | 1.0917 | 1.0916 | 1.0915 | 1.0915 | 0.97171 | 0.52937 | 17.5125 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58193 | 0.051238 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97171 | 0.52937 | 17.5125 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58193 | 0.051238 | 1.0915 | 1.0915 | 1.0915 | 1.0915 | 0.97171 | 0.52937 | 587 | 529.3718 | 0.97171 | 1.0915 | 0.0050667 | 17.5125
0.588 | 0.63511 | 0.053802 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.54896 | 17.7259 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58293 | 0.051246 | 1.0917 | 1.0916 | 1.0916 | 1.0916 | 0.97174 | 0.53075 | 17.5277 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58293 | 0.051246 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97174 | 0.53075 | 17.5277 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58293 | 0.051246 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97174 | 0.53075 | 588 | 530.745 | 0.97174 | 1.0916 | 0.0050667 | 17.5277
0.589 | 0.63615 | 0.053809 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.55036 | 17.741 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58393 | 0.051253 | 1.0918 | 1.0916 | 1.0916 | 1.0916 | 0.97176 | 0.53212 | 17.5428 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58393 | 0.051253 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97176 | 0.53212 | 17.5428 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58393 | 0.051253 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97176 | 0.53212 | 589 | 532.1195 | 0.97176 | 1.0916 | 0.0050667 | 17.5428
0.59 | 0.63719 | 0.053816 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.55177 | 17.7562 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58493 | 0.051261 | 1.0918 | 1.0916 | 1.0916 | 1.0916 | 0.97178 | 0.5335 | 17.5579 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58493 | 0.051261 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97178 | 0.5335 | 17.5579 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58493 | 0.051261 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97178 | 0.5335 | 590 | 533.4951 | 0.97178 | 1.0916 | 0.0050667 | 17.5579
0.591 | 0.63824 | 0.053822 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.55318 | 17.7713 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58593 | 0.051269 | 1.0918 | 1.0916 | 1.0916 | 1.0916 | 0.9718 | 0.53487 | 17.573 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58593 | 0.051269 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.9718 | 0.53487 | 17.573 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58593 | 0.051269 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.9718 | 0.53487 | 591 | 534.8719 | 0.9718 | 1.0916 | 0.0050667 | 17.573
0.592 | 0.63928 | 0.053829 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.5546 | 17.7864 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58693 | 0.051277 | 1.0918 | 1.0916 | 1.0916 | 1.0916 | 0.97182 | 0.53625 | 17.5881 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58693 | 0.051277 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97182 | 0.53625 | 17.5881 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58693 | 0.051277 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97182 | 0.53625 | 592 | 536.2499 | 0.97182 | 1.0916 | 0.0050667 | 17.5881
0.593 | 0.64032 | 0.053835 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.55601 | 17.8015 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58793 | 0.051284 | 1.0918 | 1.0917 | 1.0916 | 1.0916 | 0.97184 | 0.53763 | 17.6031 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58793 | 0.051284 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97184 | 0.53763 | 17.6031 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58793 | 0.051284 | 1.0916 | 1.0916 | 1.0916 | 1.0916 | 0.97184 | 0.53763 | 593 | 537.6291 | 0.97184 | 1.0916 | 0.0050667 | 17.6031
0.594 | 0.64136 | 0.053842 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.55742 | 17.8166 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58893 | 0.051292 | 1.0918 | 1.0917 | 1.0917 | 1.0917 | 0.97186 | 0.53901 | 17.6182 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58893 | 0.051292 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97186 | 0.53901 | 17.6182 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58893 | 0.051292 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97186 | 0.53901 | 594 | 539.0095 | 0.97186 | 1.0917 | 0.0050667 | 17.6182
0.595 | 0.6424 | 0.053848 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.55884 | 17.8316 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58993 | 0.0513 | 1.0919 | 1.0917 | 1.0917 | 1.0917 | 0.97188 | 0.54039 | 17.6332 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58993 | 0.0513 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97188 | 0.54039 | 17.6332 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.58993 | 0.0513 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97188 | 0.54039 | 595 | 540.391 | 0.97188 | 1.0917 | 0.0050667 | 17.6332
0.596 | 0.64344 | 0.053855 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.56026 | 17.8467 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59093 | 0.051307 | 1.0919 | 1.0917 | 1.0917 | 1.0917 | 0.97191 | 0.54177 | 17.6482 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59093 | 0.051307 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97191 | 0.54177 | 17.6482 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59093 | 0.051307 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97191 | 0.54177 | 596 | 541.7737 | 0.97191 | 1.0917 | 0.0050667 | 17.6482
0.597 | 0.64448 | 0.053861 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.56167 | 17.8617 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59193 | 0.051315 | 1.0919 | 1.0917 | 1.0917 | 1.0917 | 0.97193 | 0.54316 | 17.6633 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59193 | 0.051315 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97193 | 0.54316 | 17.6633 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59193 | 0.051315 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97193 | 0.54316 | 597 | 543.1577 | 0.97193 | 1.0917 | 0.0050667 | 17.6633
0.598 | 0.64552 | 0.053867 | 1.0973 | 1.0973 | 1.0972 | 1.0972 | 0.56309 | 17.8768 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59293 | 0.051322 | 1.0919 | 1.0917 | 1.0917 | 1.0917 | 0.97195 | 0.54454 | 17.6783 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59293 | 0.051322 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97195 | 0.54454 | 17.6783 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59293 | 0.051322 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97195 | 0.54454 | 598 | 544.5427 | 0.97195 | 1.0917 | 0.0050667 | 17.6783
0.599 | 0.64656 | 0.053874 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.56451 | 17.8918 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59393 | 0.05133 | 1.0919 | 1.0917 | 1.0917 | 1.0917 | 0.97197 | 0.54593 | 17.6933 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59393 | 0.05133 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97197 | 0.54593 | 17.6933 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59393 | 0.05133 | 1.0917 | 1.0917 | 1.0917 | 1.0917 | 0.97197 | 0.54593 | 599 | 545.929 | 0.97197 | 1.0917 | 0.0050667 | 17.6933
0.6 | 0.64761 | 0.05388 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.56593 | 17.9068 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59493 | 0.051337 | 1.0919 | 1.0918 | 1.0918 | 1.0918 | 0.97199 | 0.54732 | 17.7082 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59493 | 0.051337 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97199 | 0.54732 | 17.7082 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59493 | 0.051337 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97199 | 0.54732 | 600 | 547.3164 | 0.97199 | 1.0918 | 0.0050667 | 17.7082
0.601 | 0.64865 | 0.053886 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.56736 | 17.9218 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59593 | 0.051345 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97201 | 0.54871 | 17.7232 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59593 | 0.051345 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97201 | 0.54871 | 17.7232 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59593 | 0.051345 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97201 | 0.54871 | 601 | 548.7051 | 0.97201 | 1.0918 | 0.0050667 | 17.7232
0.602 | 0.64969 | 0.053893 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.56878 | 17.9368 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59693 | 0.051352 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97203 | 0.55009 | 17.7381 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59693 | 0.051352 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97203 | 0.55009 | 17.7381 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59693 | 0.051352 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97203 | 0.55009 | 602 | 550.0948 | 0.97203 | 1.0918 | 0.0050667 | 17.7381
0.603 | 0.65073 | 0.053899 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.57021 | 17.9517 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59793 | 0.05136 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97205 | 0.55149 | 17.7531 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59793 | 0.05136 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97205 | 0.55149 | 17.7531 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59793 | 0.05136 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97205 | 0.55149 | 603 | 551.4858 | 0.97205 | 1.0918 | 0.0050667 | 17.7531
0.604 | 0.65177 | 0.053905 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.57163 | 17.9667 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59893 | 0.051367 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97207 | 0.55288 | 17.768 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59893 | 0.051367 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97207 | 0.55288 | 17.768 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59893 | 0.051367 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97207 | 0.55288 | 604 | 552.8779 | 0.97207 | 1.0918 | 0.0050667 | 17.768
0.605 | 0.65281 | 0.053912 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.57306 | 17.9816 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59993 | 0.051375 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97209 | 0.55427 | 17.7829 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59993 | 0.051375 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97209 | 0.55427 | 17.7829 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.59993 | 0.051375 | 1.0918 | 1.0918 | 1.0918 | 1.0918 | 0.97209 | 0.55427 | 605 | 554.2713 | 0.97209 | 1.0918 | 0.0050667 | 17.7829
0.606 | 0.65385 | 0.053918 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.57449 | 17.9966 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60093 | 0.051382 | 1.092 | 1.0919 | 1.0919 | 1.0919 | 0.97211 | 0.55567 | 17.7978 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60093 | 0.051382 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97211 | 0.55567 | 17.7978 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60093 | 0.051382 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97211 | 0.55567 | 606 | 555.6657 | 0.97211 | 1.0919 | 0.0050667 | 17.7978
0.607 | 0.65489 | 0.053924 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.57592 | 18.0115 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60183 | 0.05134 | 1.0919 | 1.0918 | 1.0918 | 1.0918 | 0.97159 | 0.55669 | 17.8088 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60193 | 0.051389 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97213 | 0.55706 | 17.8127 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60193 | 0.051389 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97213 | 0.55706 | 607 | 557.0614 | 0.97213 | 1.0919 | 0.0050667 | 17.8127
0.608 | 0.65594 | 0.05393 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.57735 | 18.0264 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60283 | 0.051348 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97161 | 0.55809 | 17.8237 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60293 | 0.051397 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97215 | 0.55846 | 17.8276 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60293 | 0.051397 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97215 | 0.55846 | 608 | 558.4582 | 0.97215 | 1.0919 | 0.0050667 | 17.8276
0.609 | 0.65698 | 0.053936 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.57878 | 18.0413 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60383 | 0.051355 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97163 | 0.55949 | 17.8385 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60393 | 0.051404 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97217 | 0.55986 | 17.8424 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60393 | 0.051404 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97217 | 0.55986 | 609 | 559.8562 | 0.97217 | 1.0919 | 0.0050667 | 17.8424
0.61 | 0.65802 | 0.053943 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.58021 | 18.0561 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60483 | 0.051362 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97165 | 0.56089 | 17.8534 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60493 | 0.051411 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97219 | 0.56126 | 17.8573 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60493 | 0.051411 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97219 | 0.56126 | 610 | 561.2553 | 0.97219 | 1.0919 | 0.0050667 | 17.8573
0.611 | 0.65906 | 0.053949 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.58165 | 18.071 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60583 | 0.05137 | 1.092 | 1.0918 | 1.0918 | 1.0918 | 0.97167 | 0.56229 | 17.8682 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60593 | 0.051419 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97221 | 0.56266 | 17.8721 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60593 | 0.051419 | 1.0919 | 1.0919 | 1.0919 | 1.0919 | 0.97221 | 0.56266 | 611 | 562.6557 | 0.97221 | 1.0919 | 0.0050667 | 17.8721
0.612 | 0.6601 | 0.053955 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.58308 | 18.0859 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60683 | 0.051377 | 1.092 | 1.0919 | 1.0918 | 1.0918 | 0.97169 | 0.56369 | 17.8831 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60693 | 0.051426 | 1.0919 | 1.0919 | 1.092 | 1.092 | 0.97223 | 0.56406 | 17.887 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60693 | 0.051426 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97223 | 0.56406 | 612 | 564.0571 | 0.97223 | 1.092 | 0.0050667 | 17.887
0.613 | 0.66114 | 0.053961 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.58452 | 18.1007 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60783 | 0.051384 | 1.092 | 1.0919 | 1.0919 | 1.0919 | 0.97171 | 0.56509 | 17.8979 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60793 | 0.051433 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97225 | 0.56546 | 17.9018 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60793 | 0.051433 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97225 | 0.56546 | 613 | 565.4598 | 0.97225 | 1.092 | 0.0050667 | 17.9018
0.614 | 0.66218 | 0.053967 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.58596 | 18.1155 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60883 | 0.051391 | 1.0921 | 1.0919 | 1.0919 | 1.0919 | 0.97173 | 0.56649 | 17.9127 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60893 | 0.05144 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97227 | 0.56686 | 17.9166 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60893 | 0.05144 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97227 | 0.56686 | 614 | 566.8636 | 0.97227 | 1.092 | 0.0050667 | 17.9166
0.615 | 0.66322 | 0.053973 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.5874 | 18.1304 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.60983 | 0.051398 | 1.0921 | 1.0919 | 1.0919 | 1.0919 | 0.97175 | 0.5679 | 17.9275 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60993 | 0.051447 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97229 | 0.56827 | 17.9314 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.60993 | 0.051447 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97229 | 0.56827 | 615 | 568.2686 | 0.97229 | 1.092 | 0.0050667 | 17.9314
0.616 | 0.66426 | 0.053979 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.58884 | 18.1452 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61083 | 0.051406 | 1.0921 | 1.0919 | 1.0919 | 1.0919 | 0.97177 | 0.5693 | 17.9422 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61093 | 0.051455 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97231 | 0.56967 | 17.9461 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61093 | 0.051455 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97231 | 0.56967 | 616 | 569.6747 | 0.97231 | 1.092 | 0.0050667 | 17.9461
0.617 | 0.66531 | 0.053985 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.59028 | 18.16 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61183 | 0.051413 | 1.0921 | 1.0919 | 1.0919 | 1.0919 | 0.97179 | 0.57071 | 17.957 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61193 | 0.051462 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97233 | 0.57108 | 17.9609 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61193 | 0.051462 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97233 | 0.57108 | 617 | 571.082 | 0.97233 | 1.092 | 0.0050667 | 17.9609
0.618 | 0.66635 | 0.053991 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.59172 | 18.1747 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61283 | 0.05142 | 1.0921 | 1.0919 | 1.0919 | 1.0919 | 0.97181 | 0.57212 | 17.9718 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61293 | 0.051469 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97235 | 0.57249 | 17.9757 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61293 | 0.051469 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97235 | 0.57249 | 618 | 572.4904 | 0.97235 | 1.092 | 0.0050667 | 17.9757
0.619 | 0.66739 | 0.053997 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.59317 | 18.1895 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61383 | 0.051427 | 1.0921 | 1.092 | 1.092 | 1.092 | 0.97183 | 0.57353 | 17.9865 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61393 | 0.051476 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97237 | 0.5739 | 17.9904 | 0.0058 | 0.0047 | 0.0050667 | 0.64078 | 0.61393 | 0.051476 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97237 | 0.5739 | 619 | 573.9 | 0.97237 | 1.0921 | 0.0050667 | 17.9904
0.62 | 0.66843 | 0.054003 | 1.0976 | 1.0976 | 1.0975 | 1.0975 | 0.59461 | 18.2043 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61483 | 0.051434 | 1.0921 | 1.092 | 1.092 | 1.092 | 0.97185 | 0.57494 | 18.0012 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61483 | 0.051434 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97185 | 0.57494 | 18.0012 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61483 | 0.051434 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97185 | 0.57494 | 620 | 574.9357 | 0.97185 | 1.092 | 0.0051667 | 18.0012
0.621 | 0.66947 | 0.054009 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.59606 | 18.219 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61583 | 0.051441 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.97187 | 0.57635 | 18.0159 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61583 | 0.051441 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97187 | 0.57635 | 18.0159 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61583 | 0.051441 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97187 | 0.57635 | 621 | 576.3469 | 0.97187 | 1.092 | 0.0051667 | 18.0159
0.622 | 0.67051 | 0.054015 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.59751 | 18.2338 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61683 | 0.051448 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.97189 | 0.57776 | 18.0306 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61683 | 0.051448 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97189 | 0.57776 | 18.0306 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61683 | 0.051448 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97189 | 0.57776 | 622 | 577.7593 | 0.97189 | 1.092 | 0.0051667 | 18.0306
0.623 | 0.67155 | 0.054021 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.59895 | 18.2485 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61783 | 0.051455 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.97191 | 0.57917 | 18.0453 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61783 | 0.051455 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97191 | 0.57917 | 18.0453 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61783 | 0.051455 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97191 | 0.57917 | 623 | 579.1729 | 0.97191 | 1.092 | 0.0051667 | 18.0453
0.624 | 0.67259 | 0.054027 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.6004 | 18.2632 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61883 | 0.051462 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.97193 | 0.58059 | 18.06 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61883 | 0.051462 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97193 | 0.58059 | 18.06 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61883 | 0.051462 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97193 | 0.58059 | 624 | 580.5876 | 0.97193 | 1.092 | 0.0051667 | 18.06
0.625 | 0.67363 | 0.054033 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.60186 | 18.2779 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61983 | 0.051469 | 1.0922 | 1.092 | 1.092 | 1.092 | 0.97195 | 0.582 | 18.0747 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61983 | 0.051469 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97195 | 0.582 | 18.0747 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.61983 | 0.051469 | 1.092 | 1.092 | 1.092 | 1.092 | 0.97195 | 0.582 | 625 | 582.0034 | 0.97195 | 1.092 | 0.0051667 | 18.0747
0.626 | 0.67468 | 0.054039 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.60331 | 18.2926 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62083 | 0.051476 | 1.0922 | 1.0921 | 1.0921 | 1.0921 | 0.97197 | 0.58342 | 18.0893 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62083 | 0.051476 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97197 | 0.58342 | 18.0893 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62083 | 0.051476 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97197 | 0.58342 | 626 | 583.4205 | 0.97197 | 1.0921 | 0.0051667 | 18.0893
0.627 | 0.67572 | 0.054045 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.60476 | 18.3073 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62183 | 0.051483 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.97199 | 0.58484 | 18.104 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62183 | 0.051483 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97199 | 0.58484 | 18.104 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62183 | 0.051483 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97199 | 0.58484 | 627 | 584.8386 | 0.97199 | 1.0921 | 0.0051667 | 18.104
0.628 | 0.67676 | 0.05405 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.60622 | 18.3219 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62283 | 0.05149 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.97201 | 0.58626 | 18.1186 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62283 | 0.05149 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97201 | 0.58626 | 18.1186 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62283 | 0.05149 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97201 | 0.58626 | 628 | 586.2579 | 0.97201 | 1.0921 | 0.0051667 | 18.1186
0.629 | 0.6778 | 0.054056 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.60767 | 18.3366 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62383 | 0.051497 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.97202 | 0.58768 | 18.1332 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62383 | 0.051497 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97202 | 0.58768 | 18.1332 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62383 | 0.051497 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97202 | 0.58768 | 629 | 587.6784 | 0.97202 | 1.0921 | 0.0051667 | 18.1332
0.63 | 0.67884 | 0.054062 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.60913 | 18.3512 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62483 | 0.051504 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.97204 | 0.5891 | 18.1479 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62483 | 0.051504 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97204 | 0.5891 | 18.1479 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62483 | 0.051504 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97204 | 0.5891 | 630 | 589.1 | 0.97204 | 1.0921 | 0.0051667 | 18.1479
0.631 | 0.67988 | 0.054068 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.61059 | 18.3659 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62583 | 0.051511 | 1.0923 | 1.0921 | 1.0921 | 1.0921 | 0.97206 | 0.59052 | 18.1625 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62583 | 0.051511 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97206 | 0.59052 | 18.1625 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62583 | 0.051511 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97206 | 0.59052 | 631 | 590.5228 | 0.97206 | 1.0921 | 0.0051667 | 18.1625
0.632 | 0.68092 | 0.054074 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.61204 | 18.3805 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62683 | 0.051518 | 1.0923 | 1.0922 | 1.0921 | 1.0921 | 0.97208 | 0.59195 | 18.177 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62683 | 0.051518 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97208 | 0.59195 | 18.177 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62683 | 0.051518 | 1.0921 | 1.0921 | 1.0921 | 1.0921 | 0.97208 | 0.59195 | 632 | 591.9467 | 0.97208 | 1.0921 | 0.0051667 | 18.177
0.633 | 0.68196 | 0.054079 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.6135 | 18.3951 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62783 | 0.051524 | 1.0923 | 1.0922 | 1.0922 | 1.0922 | 0.9721 | 0.59337 | 18.1916 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62783 | 0.051524 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.9721 | 0.59337 | 18.1916 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62783 | 0.051524 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.9721 | 0.59337 | 633 | 593.3717 | 0.9721 | 1.0922 | 0.0051667 | 18.1916
0.634 | 0.68301 | 0.054085 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.61497 | 18.4097 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62883 | 0.051531 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.97212 | 0.5948 | 18.2062 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62883 | 0.051531 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97212 | 0.5948 | 18.2062 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62883 | 0.051531 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97212 | 0.5948 | 634 | 594.7979 | 0.97212 | 1.0922 | 0.0051667 | 18.2062
0.635 | 0.68405 | 0.054091 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.61643 | 18.4243 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62983 | 0.051538 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.97214 | 0.59623 | 18.2207 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62983 | 0.051538 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97214 | 0.59623 | 18.2207 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.62983 | 0.051538 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97214 | 0.59623 | 635 | 596.2252 | 0.97214 | 1.0922 | 0.0051667 | 18.2207
0.636 | 0.68509 | 0.054096 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.61789 | 18.4388 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63083 | 0.051545 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.97216 | 0.59765 | 18.2353 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63083 | 0.051545 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97216 | 0.59765 | 18.2353 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63083 | 0.051545 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97216 | 0.59765 | 636 | 597.6537 | 0.97216 | 1.0922 | 0.0051667 | 18.2353
0.637 | 0.68613 | 0.054102 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.61936 | 18.4534 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63183 | 0.051551 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.97218 | 0.59908 | 18.2498 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63183 | 0.051551 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97218 | 0.59908 | 18.2498 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63183 | 0.051551 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97218 | 0.59908 | 637 | 599.0833 | 0.97218 | 1.0922 | 0.0051667 | 18.2498
0.638 | 0.68717 | 0.054108 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.62082 | 18.4679 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63283 | 0.051558 | 1.0924 | 1.0922 | 1.0922 | 1.0922 | 0.97219 | 0.60051 | 18.2643 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63283 | 0.051558 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97219 | 0.60051 | 18.2643 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63283 | 0.051558 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97219 | 0.60051 | 638 | 600.5141 | 0.97219 | 1.0922 | 0.0051667 | 18.2643
0.639 | 0.68821 | 0.054113 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.62229 | 18.4825 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63383 | 0.051565 | 1.0924 | 1.0923 | 1.0922 | 1.0922 | 0.97221 | 0.60195 | 18.2788 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63383 | 0.051565 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97221 | 0.60195 | 18.2788 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63383 | 0.051565 | 1.0922 | 1.0922 | 1.0922 | 1.0922 | 0.97221 | 0.60195 | 639 | 601.946 | 0.97221 | 1.0922 | 0.0051667 | 18.2788
0.64 | 0.68925 | 0.054119 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.62376 | 18.497 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63483 | 0.051572 | 1.0924 | 1.0923 | 1.0923 | 1.0923 | 0.97223 | 0.60338 | 18.2933 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63483 | 0.051572 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97223 | 0.60338 | 18.2933 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63483 | 0.051572 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97223 | 0.60338 | 640 | 603.379 | 0.97223 | 1.0923 | 0.0051667 | 18.2933
0.641 | 0.69029 | 0.054125 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.62523 | 18.5115 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63583 | 0.051578 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.97225 | 0.60481 | 18.3078 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63583 | 0.051578 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97225 | 0.60481 | 18.3078 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63583 | 0.051578 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97225 | 0.60481 | 641 | 604.8132 | 0.97225 | 1.0923 | 0.0051667 | 18.3078
0.642 | 0.69133 | 0.05413 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.6267 | 18.526 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63683 | 0.051585 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.97227 | 0.60625 | 18.3223 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63683 | 0.051585 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97227 | 0.60625 | 18.3223 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63683 | 0.051585 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97227 | 0.60625 | 642 | 606.2485 | 0.97227 | 1.0923 | 0.0051667 | 18.3223
0.643 | 0.69238 | 0.054136 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.62817 | 18.5405 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63783 | 0.051591 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.97229 | 0.60768 | 18.3367 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63783 | 0.051591 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97229 | 0.60768 | 18.3367 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63783 | 0.051591 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97229 | 0.60768 | 643 | 607.6849 | 0.97229 | 1.0923 | 0.0051667 | 18.3367
0.644 | 0.69342 | 0.054141 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.62964 | 18.555 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63883 | 0.051598 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.97231 | 0.60912 | 18.3512 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63883 | 0.051598 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97231 | 0.60912 | 18.3512 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63883 | 0.051598 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97231 | 0.60912 | 644 | 609.1225 | 0.97231 | 1.0923 | 0.0051667 | 18.3512
0.645 | 0.69446 | 0.054147 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.63112 | 18.5695 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63983 | 0.051605 | 1.0925 | 1.0923 | 1.0923 | 1.0923 | 0.97232 | 0.61056 | 18.3656 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63983 | 0.051605 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97232 | 0.61056 | 18.3656 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.63983 | 0.051605 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97232 | 0.61056 | 645 | 610.5612 | 0.97232 | 1.0923 | 0.0051667 | 18.3656
0.646 | 0.6955 | 0.054153 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.63259 | 18.5839 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64083 | 0.051611 | 1.0925 | 1.0924 | 1.0923 | 1.0923 | 0.97234 | 0.612 | 18.38 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64083 | 0.051611 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97234 | 0.612 | 18.38 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64083 | 0.051611 | 1.0923 | 1.0923 | 1.0923 | 1.0923 | 0.97234 | 0.612 | 646 | 612.0011 | 0.97234 | 1.0923 | 0.0051667 | 18.38
0.647 | 0.69654 | 0.054158 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.63407 | 18.5984 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64183 | 0.051618 | 1.0925 | 1.0924 | 1.0924 | 1.0924 | 0.97236 | 0.61344 | 18.3944 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64183 | 0.051618 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97236 | 0.61344 | 18.3944 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64183 | 0.051618 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97236 | 0.61344 | 647 | 613.4421 | 0.97236 | 1.0924 | 0.0051667 | 18.3944
0.648 | 0.69758 | 0.054164 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.63555 | 18.6128 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64283 | 0.051624 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.97238 | 0.61488 | 18.4089 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64283 | 0.051624 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97238 | 0.61488 | 18.4089 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64283 | 0.051624 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97238 | 0.61488 | 648 | 614.8842 | 0.97238 | 1.0924 | 0.0051667 | 18.4089
0.649 | 0.69862 | 0.054169 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.63703 | 18.6272 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64383 | 0.051631 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.9724 | 0.61633 | 18.4232 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64383 | 0.051631 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.9724 | 0.61633 | 18.4232 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64383 | 0.051631 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.9724 | 0.61633 | 649 | 616.3274 | 0.9724 | 1.0924 | 0.0051667 | 18.4232
0.65 | 0.69966 | 0.054174 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.63851 | 18.6416 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64483 | 0.051637 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.97241 | 0.61777 | 18.4376 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64483 | 0.051637 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97241 | 0.61777 | 18.4376 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64483 | 0.051637 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97241 | 0.61777 | 650 | 617.7718 | 0.97241 | 1.0924 | 0.0051667 | 18.4376
0.651 | 0.70071 | 0.05418 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.63999 | 18.656 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64583 | 0.051644 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.97243 | 0.61922 | 18.452 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64583 | 0.051644 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97243 | 0.61922 | 18.452 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64583 | 0.051644 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97243 | 0.61922 | 651 | 619.2173 | 0.97243 | 1.0924 | 0.0051667 | 18.452
0.652 | 0.70175 | 0.054185 | 1.098 | 1.098 | 1.0979 | 1.0979 | 0.64147 | 18.6704 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64683 | 0.05165 | 1.0926 | 1.0924 | 1.0924 | 1.0924 | 0.97245 | 0.62066 | 18.4663 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64683 | 0.05165 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97245 | 0.62066 | 18.4663 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64683 | 0.05165 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97245 | 0.62066 | 652 | 620.6639 | 0.97245 | 1.0924 | 0.0051667 | 18.4663
0.653 | 0.70279 | 0.054191 | 1.098 | 1.098 | 1.098 | 1.098 | 0.64295 | 18.6848 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64783 | 0.051657 | 1.0926 | 1.0925 | 1.0924 | 1.0924 | 0.97247 | 0.62211 | 18.4807 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64783 | 0.051657 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97247 | 0.62211 | 18.4807 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64783 | 0.051657 | 1.0924 | 1.0924 | 1.0924 | 1.0924 | 0.97247 | 0.62211 | 653 | 622.1116 | 0.97247 | 1.0924 | 0.0051667 | 18.4807
0.654 | 0.70383 | 0.054196 | 1.098 | 1.098 | 1.098 | 1.098 | 0.64444 | 18.6992 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64883 | 0.051663 | 1.0926 | 1.0925 | 1.0925 | 1.0925 | 0.97249 | 0.62356 | 18.495 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64883 | 0.051663 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97249 | 0.62356 | 18.495 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64883 | 0.051663 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97249 | 0.62356 | 654 | 623.5605 | 0.97249 | 1.0925 | 0.0051667 | 18.495
0.655 | 0.70487 | 0.054202 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.64592 | 18.7135 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64983 | 0.051669 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.9725 | 0.62501 | 18.5094 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64983 | 0.051669 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.9725 | 0.62501 | 18.5094 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.64983 | 0.051669 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.9725 | 0.62501 | 655 | 625.0105 | 0.9725 | 1.0925 | 0.0051667 | 18.5094
0.656 | 0.70591 | 0.054207 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.64741 | 18.7279 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65083 | 0.051676 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.97252 | 0.62646 | 18.5237 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65083 | 0.051676 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97252 | 0.62646 | 18.5237 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65083 | 0.051676 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97252 | 0.62646 | 656 | 626.4616 | 0.97252 | 1.0925 | 0.0051667 | 18.5237
0.657 | 0.70695 | 0.054212 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.6489 | 18.7422 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65183 | 0.051682 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.97254 | 0.62791 | 18.538 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65183 | 0.051682 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97254 | 0.62791 | 18.538 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65183 | 0.051682 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97254 | 0.62791 | 657 | 627.9139 | 0.97254 | 1.0925 | 0.0051667 | 18.538
0.658 | 0.70799 | 0.054218 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.65039 | 18.7565 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65283 | 0.051688 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.97256 | 0.62937 | 18.5523 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65283 | 0.051688 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97256 | 0.62937 | 18.5523 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65283 | 0.051688 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97256 | 0.62937 | 658 | 629.3672 | 0.97256 | 1.0925 | 0.0051667 | 18.5523
0.659 | 0.70903 | 0.054223 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.65188 | 18.7709 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65383 | 0.051695 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.97257 | 0.63082 | 18.5665 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65383 | 0.051695 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97257 | 0.63082 | 18.5665 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65383 | 0.051695 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97257 | 0.63082 | 659 | 630.8217 | 0.97257 | 1.0925 | 0.0051667 | 18.5665
0.66 | 0.71008 | 0.054228 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.65337 | 18.7852 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65483 | 0.051701 | 1.0927 | 1.0925 | 1.0925 | 1.0925 | 0.97259 | 0.63228 | 18.5808 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65483 | 0.051701 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97259 | 0.63228 | 18.5808 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65483 | 0.051701 | 1.0925 | 1.0925 | 1.0925 | 1.0925 | 0.97259 | 0.63228 | 660 | 632.2773 | 0.97259 | 1.0925 | 0.0051667 | 18.5808
0.661 | 0.71112 | 0.054234 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.65486 | 18.7994 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65583 | 0.051707 | 1.0927 | 1.0926 | 1.0926 | 1.0926 | 0.97261 | 0.63373 | 18.5951 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65583 | 0.051707 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97261 | 0.63373 | 18.5951 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65583 | 0.051707 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97261 | 0.63373 | 661 | 633.7341 | 0.97261 | 1.0926 | 0.0051667 | 18.5951
0.662 | 0.71216 | 0.054239 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.65635 | 18.8137 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65683 | 0.051714 | 1.0927 | 1.0926 | 1.0926 | 1.0926 | 0.97263 | 0.63519 | 18.6093 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65683 | 0.051714 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97263 | 0.63519 | 18.6093 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65683 | 0.051714 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97263 | 0.63519 | 662 | 635.1919 | 0.97263 | 1.0926 | 0.0051667 | 18.6093
0.663 | 0.7132 | 0.054244 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.65785 | 18.828 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65783 | 0.05172 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.97264 | 0.63665 | 18.6236 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65783 | 0.05172 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97264 | 0.63665 | 18.6236 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65783 | 0.05172 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97264 | 0.63665 | 663 | 636.6509 | 0.97264 | 1.0926 | 0.0051667 | 18.6236
0.664 | 0.71424 | 0.054249 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.65934 | 18.8423 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65883 | 0.051726 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.97266 | 0.63811 | 18.6378 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65883 | 0.051726 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97266 | 0.63811 | 18.6378 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65883 | 0.051726 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97266 | 0.63811 | 664 | 638.111 | 0.97266 | 1.0926 | 0.0051667 | 18.6378
0.665 | 0.71528 | 0.054255 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.66084 | 18.8565 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65983 | 0.051732 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.97268 | 0.63957 | 18.652 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65983 | 0.051732 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97268 | 0.63957 | 18.652 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.65983 | 0.051732 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97268 | 0.63957 | 665 | 639.5722 | 0.97268 | 1.0926 | 0.0051667 | 18.652
0.666 | 0.71632 | 0.05426 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.66234 | 18.8707 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66083 | 0.051739 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.9727 | 0.64103 | 18.6662 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66083 | 0.051739 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.9727 | 0.64103 | 18.6662 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66083 | 0.051739 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.9727 | 0.64103 | 666 | 641.0345 | 0.9727 | 1.0926 | 0.0051667 | 18.6662
0.667 | 0.71736 | 0.054265 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.66384 | 18.885 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66183 | 0.051745 | 1.0928 | 1.0926 | 1.0926 | 1.0926 | 0.97271 | 0.6425 | 18.6804 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66183 | 0.051745 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97271 | 0.6425 | 18.6804 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66183 | 0.051745 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97271 | 0.6425 | 667 | 642.4979 | 0.97271 | 1.0926 | 0.0051667 | 18.6804
0.668 | 0.71841 | 0.05427 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.66534 | 18.8992 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66283 | 0.051751 | 1.0928 | 1.0927 | 1.0926 | 1.0926 | 0.97273 | 0.64396 | 18.6946 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66283 | 0.051751 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97273 | 0.64396 | 18.6946 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66283 | 0.051751 | 1.0926 | 1.0926 | 1.0926 | 1.0926 | 0.97273 | 0.64396 | 668 | 643.9625 | 0.97273 | 1.0926 | 0.0051667 | 18.6946
0.669 | 0.71945 | 0.054275 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.66684 | 18.9134 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66383 | 0.051757 | 1.0928 | 1.0927 | 1.0927 | 1.0927 | 0.97275 | 0.64543 | 18.7088 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66383 | 0.051757 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97275 | 0.64543 | 18.7088 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66383 | 0.051757 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97275 | 0.64543 | 669 | 645.4281 | 0.97275 | 1.0927 | 0.0051667 | 18.7088
0.67 | 0.72049 | 0.054281 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.66834 | 18.9276 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66483 | 0.051763 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.97276 | 0.64689 | 18.7229 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66483 | 0.051763 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97276 | 0.64689 | 18.7229 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66483 | 0.051763 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97276 | 0.64689 | 670 | 646.8949 | 0.97276 | 1.0927 | 0.0051667 | 18.7229
0.671 | 0.72153 | 0.054286 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.66985 | 18.9418 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66583 | 0.051769 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.97278 | 0.64836 | 18.7371 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66583 | 0.051769 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97278 | 0.64836 | 18.7371 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66583 | 0.051769 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97278 | 0.64836 | 671 | 648.3628 | 0.97278 | 1.0927 | 0.0051667 | 18.7371
0.672 | 0.72257 | 0.054291 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.67135 | 18.956 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66683 | 0.051775 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.9728 | 0.64983 | 18.7512 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66683 | 0.051775 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.9728 | 0.64983 | 18.7512 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66683 | 0.051775 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.9728 | 0.64983 | 672 | 649.8318 | 0.9728 | 1.0927 | 0.0051667 | 18.7512
0.673 | 0.72361 | 0.054296 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.67286 | 18.9701 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66783 | 0.051781 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.97281 | 0.6513 | 18.7653 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66783 | 0.051781 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97281 | 0.6513 | 18.7653 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66783 | 0.051781 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97281 | 0.6513 | 673 | 651.3019 | 0.97281 | 1.0927 | 0.0051667 | 18.7653
0.674 | 0.72465 | 0.054301 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.67437 | 18.9843 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66883 | 0.051787 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.97283 | 0.65277 | 18.7795 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66883 | 0.051787 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97283 | 0.65277 | 18.7795 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66883 | 0.051787 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97283 | 0.65277 | 674 | 652.7731 | 0.97283 | 1.0927 | 0.0051667 | 18.7795
0.675 | 0.72569 | 0.054306 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.67587 | 18.9984 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66983 | 0.051793 | 1.0929 | 1.0927 | 1.0927 | 1.0927 | 0.97285 | 0.65425 | 18.7936 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66983 | 0.051793 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97285 | 0.65425 | 18.7936 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.66983 | 0.051793 | 1.0927 | 1.0927 | 1.0927 | 1.0927 | 0.97285 | 0.65425 | 675 | 654.2454 | 0.97285 | 1.0927 | 0.0051667 | 18.7936
0.676 | 0.72673 | 0.054311 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.67738 | 19.0125 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67083 | 0.051799 | 1.0929 | 1.0928 | 1.0928 | 1.0928 | 0.97286 | 0.65572 | 18.8077 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67083 | 0.051799 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97286 | 0.65572 | 18.8077 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67083 | 0.051799 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97286 | 0.65572 | 676 | 655.7188 | 0.97286 | 1.0928 | 0.0051667 | 18.8077
0.677 | 0.72778 | 0.054316 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.67889 | 19.0267 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67183 | 0.051805 | 1.0929 | 1.0928 | 1.0928 | 1.0928 | 0.97288 | 0.65719 | 18.8217 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67183 | 0.051805 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97288 | 0.65719 | 18.8217 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67183 | 0.051805 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97288 | 0.65719 | 677 | 657.1934 | 0.97288 | 1.0928 | 0.0051667 | 18.8217
0.678 | 0.72882 | 0.054321 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.6804 | 19.0408 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67283 | 0.051811 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.9729 | 0.65867 | 18.8358 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67283 | 0.051811 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.9729 | 0.65867 | 18.8358 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67283 | 0.051811 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.9729 | 0.65867 | 678 | 658.669 | 0.9729 | 1.0928 | 0.0051667 | 18.8358
0.679 | 0.72986 | 0.054326 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.68192 | 19.0549 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67383 | 0.051817 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.97291 | 0.66015 | 18.8499 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67383 | 0.051817 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97291 | 0.66015 | 18.8499 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67383 | 0.051817 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97291 | 0.66015 | 679 | 660.1457 | 0.97291 | 1.0928 | 0.0051667 | 18.8499
0.68 | 0.7309 | 0.054331 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.68343 | 19.069 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67483 | 0.051823 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.97293 | 0.66162 | 18.8639 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67483 | 0.051823 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97293 | 0.66162 | 18.8639 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67483 | 0.051823 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97293 | 0.66162 | 680 | 661.6236 | 0.97293 | 1.0928 | 0.0051667 | 18.8639
0.681 | 0.73194 | 0.054336 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.68495 | 19.083 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67583 | 0.051829 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.97295 | 0.6631 | 18.878 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67583 | 0.051829 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97295 | 0.6631 | 18.878 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67583 | 0.051829 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97295 | 0.6631 | 681 | 663.1025 | 0.97295 | 1.0928 | 0.0051667 | 18.878
0.682 | 0.73298 | 0.054341 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.68646 | 19.0971 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67683 | 0.051835 | 1.093 | 1.0928 | 1.0928 | 1.0928 | 0.97296 | 0.66458 | 18.892 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67683 | 0.051835 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97296 | 0.66458 | 18.892 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67683 | 0.051835 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97296 | 0.66458 | 682 | 664.5826 | 0.97296 | 1.0928 | 0.0051667 | 18.892
0.683 | 0.73402 | 0.054346 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.68798 | 19.1112 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67783 | 0.051841 | 1.093 | 1.0929 | 1.0928 | 1.0928 | 0.97298 | 0.66606 | 18.9061 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67783 | 0.051841 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97298 | 0.66606 | 18.9061 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67783 | 0.051841 | 1.0928 | 1.0928 | 1.0928 | 1.0928 | 0.97298 | 0.66606 | 683 | 666.0637 | 0.97298 | 1.0928 | 0.0051667 | 18.9061
0.684 | 0.73506 | 0.054351 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.6895 | 19.1252 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67883 | 0.051847 | 1.093 | 1.0929 | 1.0929 | 1.0929 | 0.973 | 0.66755 | 18.9201 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67883 | 0.051847 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.973 | 0.66755 | 18.9201 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67883 | 0.051847 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.973 | 0.66755 | 684 | 667.546 | 0.973 | 1.0929 | 0.0051667 | 18.9201
0.685 | 0.7361 | 0.054356 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.69102 | 19.1393 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67983 | 0.051853 | 1.093 | 1.0929 | 1.0929 | 1.0929 | 0.97301 | 0.66903 | 18.9341 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67983 | 0.051853 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97301 | 0.66903 | 18.9341 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.67983 | 0.051853 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97301 | 0.66903 | 685 | 669.0293 | 0.97301 | 1.0929 | 0.0051667 | 18.9341
0.686 | 0.73715 | 0.054361 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.69254 | 19.1533 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68083 | 0.051859 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.97303 | 0.67051 | 18.9481 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68083 | 0.051859 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97303 | 0.67051 | 18.9481 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68083 | 0.051859 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97303 | 0.67051 | 686 | 670.5138 | 0.97303 | 1.0929 | 0.0051667 | 18.9481
0.687 | 0.73819 | 0.054366 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.69406 | 19.1673 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68183 | 0.051865 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.97304 | 0.672 | 18.962 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68183 | 0.051865 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97304 | 0.672 | 18.962 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68183 | 0.051865 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97304 | 0.672 | 687 | 671.9993 | 0.97304 | 1.0929 | 0.0051667 | 18.962
0.688 | 0.73923 | 0.054371 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.69558 | 19.1813 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68283 | 0.05187 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.97306 | 0.67349 | 18.976 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68283 | 0.05187 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97306 | 0.67349 | 18.976 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68283 | 0.05187 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97306 | 0.67349 | 688 | 673.486 | 0.97306 | 1.0929 | 0.0051667 | 18.976
0.689 | 0.74027 | 0.054376 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.69711 | 19.1953 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68383 | 0.051876 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.97308 | 0.67497 | 18.99 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68383 | 0.051876 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97308 | 0.67497 | 18.99 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68383 | 0.051876 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97308 | 0.67497 | 689 | 674.9737 | 0.97308 | 1.0929 | 0.0051667 | 18.99
0.69 | 0.74131 | 0.054381 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.69863 | 19.2093 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68483 | 0.051882 | 1.0931 | 1.0929 | 1.0929 | 1.0929 | 0.97309 | 0.67646 | 19.0039 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68483 | 0.051882 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97309 | 0.67646 | 19.0039 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68483 | 0.051882 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97309 | 0.67646 | 690 | 676.4625 | 0.97309 | 1.0929 | 0.0051667 | 19.0039
0.691 | 0.74235 | 0.054386 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.70016 | 19.2233 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68583 | 0.051888 | 1.0931 | 1.093 | 1.0929 | 1.0929 | 0.97311 | 0.67795 | 19.0179 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68583 | 0.051888 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97311 | 0.67795 | 19.0179 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68583 | 0.051888 | 1.0929 | 1.0929 | 1.0929 | 1.0929 | 0.97311 | 0.67795 | 691 | 677.9525 | 0.97311 | 1.0929 | 0.0051667 | 19.0179
0.692 | 0.74339 | 0.05439 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.70169 | 19.2372 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68683 | 0.051894 | 1.0931 | 1.093 | 1.093 | 1.093 | 0.97312 | 0.67944 | 19.0318 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68683 | 0.051894 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97312 | 0.67944 | 19.0318 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68683 | 0.051894 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97312 | 0.67944 | 692 | 679.4435 | 0.97312 | 1.093 | 0.0051667 | 19.0318
0.693 | 0.74443 | 0.054395 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.70321 | 19.2512 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68783 | 0.051899 | 1.0931 | 1.093 | 1.093 | 1.093 | 0.97314 | 0.68094 | 19.0457 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68783 | 0.051899 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97314 | 0.68094 | 19.0457 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68783 | 0.051899 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97314 | 0.68094 | 693 | 680.9356 | 0.97314 | 1.093 | 0.0051667 | 19.0457
0.694 | 0.74548 | 0.0544 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.70474 | 19.2652 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68883 | 0.051905 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.97316 | 0.68243 | 19.0596 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68883 | 0.051905 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97316 | 0.68243 | 19.0596 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68883 | 0.051905 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97316 | 0.68243 | 694 | 682.4288 | 0.97316 | 1.093 | 0.0051667 | 19.0596
0.695 | 0.74652 | 0.054405 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.70627 | 19.2791 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68983 | 0.051911 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.97317 | 0.68392 | 19.0735 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68983 | 0.051911 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97317 | 0.68392 | 19.0735 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.68983 | 0.051911 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97317 | 0.68392 | 695 | 683.9231 | 0.97317 | 1.093 | 0.0051667 | 19.0735
0.696 | 0.74756 | 0.05441 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.70781 | 19.293 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69083 | 0.051916 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.97319 | 0.68542 | 19.0874 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69083 | 0.051916 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97319 | 0.68542 | 19.0874 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69083 | 0.051916 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97319 | 0.68542 | 696 | 685.4185 | 0.97319 | 1.093 | 0.0051667 | 19.0874
0.697 | 0.7486 | 0.054414 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.70934 | 19.3069 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69183 | 0.051922 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.9732 | 0.68691 | 19.1013 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69183 | 0.051922 | 1.093 | 1.093 | 1.093 | 1.093 | 0.9732 | 0.68691 | 19.1013 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69183 | 0.051922 | 1.093 | 1.093 | 1.093 | 1.093 | 0.9732 | 0.68691 | 697 | 686.915 | 0.9732 | 1.093 | 0.0051667 | 19.1013
0.698 | 0.74964 | 0.054419 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.71087 | 19.3208 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69283 | 0.051928 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.97322 | 0.68841 | 19.1152 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69283 | 0.051928 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97322 | 0.68841 | 19.1152 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69283 | 0.051928 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97322 | 0.68841 | 698 | 688.4126 | 0.97322 | 1.093 | 0.0051667 | 19.1152
0.699 | 0.75068 | 0.054424 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.71241 | 19.3347 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69383 | 0.051933 | 1.0932 | 1.093 | 1.093 | 1.093 | 0.97323 | 0.68991 | 19.129 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69383 | 0.051933 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97323 | 0.68991 | 19.129 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69383 | 0.051933 | 1.093 | 1.093 | 1.093 | 1.093 | 0.97323 | 0.68991 | 699 | 689.9112 | 0.97323 | 1.093 | 0.0051667 | 19.129
0.7 | 0.75172 | 0.054429 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.71394 | 19.3486 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69483 | 0.051939 | 1.0932 | 1.0931 | 1.0931 | 1.0931 | 0.97325 | 0.69141 | 19.1429 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69483 | 0.051939 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97325 | 0.69141 | 19.1429 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69483 | 0.051939 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97325 | 0.69141 | 700 | 691.411 | 0.97325 | 1.0931 | 0.0051667 | 19.1429
0.701 | 0.75276 | 0.054433 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.71548 | 19.3625 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69583 | 0.051945 | 1.0932 | 1.0931 | 1.0931 | 1.0931 | 0.97326 | 0.69291 | 19.1567 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69583 | 0.051945 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97326 | 0.69291 | 19.1567 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69583 | 0.051945 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97326 | 0.69291 | 701 | 692.9118 | 0.97326 | 1.0931 | 0.0051667 | 19.1567
0.702 | 0.7538 | 0.054438 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.71702 | 19.3764 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69683 | 0.05195 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.97328 | 0.69441 | 19.1706 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69683 | 0.05195 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97328 | 0.69441 | 19.1706 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69683 | 0.05195 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97328 | 0.69441 | 702 | 694.4137 | 0.97328 | 1.0931 | 0.0051667 | 19.1706
0.703 | 0.75485 | 0.054443 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.71856 | 19.3902 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69783 | 0.051956 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.9733 | 0.69592 | 19.1844 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69783 | 0.051956 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.9733 | 0.69592 | 19.1844 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69783 | 0.051956 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.9733 | 0.69592 | 703 | 695.9167 | 0.9733 | 1.0931 | 0.0051667 | 19.1844
0.704 | 0.75589 | 0.054448 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.7201 | 19.4041 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69883 | 0.051961 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.97331 | 0.69742 | 19.1982 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69883 | 0.051961 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97331 | 0.69742 | 19.1982 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69883 | 0.051961 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97331 | 0.69742 | 704 | 697.4208 | 0.97331 | 1.0931 | 0.0051667 | 19.1982
0.705 | 0.75693 | 0.054452 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.72164 | 19.4179 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69983 | 0.051967 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.97333 | 0.69893 | 19.212 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69983 | 0.051967 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97333 | 0.69893 | 19.212 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.69983 | 0.051967 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97333 | 0.69893 | 705 | 698.926 | 0.97333 | 1.0931 | 0.0051667 | 19.212
0.706 | 0.75797 | 0.054457 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.72318 | 19.4317 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70083 | 0.051973 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.97334 | 0.70043 | 19.2258 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70083 | 0.051973 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97334 | 0.70043 | 19.2258 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70083 | 0.051973 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97334 | 0.70043 | 706 | 700.4322 | 0.97334 | 1.0931 | 0.0051667 | 19.2258
0.707 | 0.75901 | 0.054462 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.72473 | 19.4456 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70183 | 0.051978 | 1.0933 | 1.0931 | 1.0931 | 1.0931 | 0.97336 | 0.70194 | 19.2396 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70183 | 0.051978 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97336 | 0.70194 | 19.2396 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70183 | 0.051978 | 1.0931 | 1.0931 | 1.0931 | 1.0931 | 0.97336 | 0.70194 | 707 | 701.9396 | 0.97336 | 1.0931 | 0.0051667 | 19.2396
0.708 | 0.76005 | 0.054466 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.72627 | 19.4594 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70283 | 0.051984 | 1.0933 | 1.0932 | 1.0932 | 1.0932 | 0.97337 | 0.70345 | 19.2533 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70283 | 0.051984 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97337 | 0.70345 | 19.2533 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70283 | 0.051984 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97337 | 0.70345 | 708 | 703.448 | 0.97337 | 1.0932 | 0.0051667 | 19.2533
0.709 | 0.76109 | 0.054471 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.72782 | 19.4732 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70383 | 0.051989 | 1.0933 | 1.0932 | 1.0932 | 1.0932 | 0.97339 | 0.70496 | 19.2671 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70383 | 0.051989 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97339 | 0.70496 | 19.2671 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70383 | 0.051989 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97339 | 0.70496 | 709 | 704.9575 | 0.97339 | 1.0932 | 0.0051667 | 19.2671
0.71 | 0.76213 | 0.054475 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.72936 | 19.4869 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70483 | 0.051995 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.9734 | 0.70647 | 19.2809 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70483 | 0.051995 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.9734 | 0.70647 | 19.2809 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70483 | 0.051995 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.9734 | 0.70647 | 710 | 706.4681 | 0.9734 | 1.0932 | 0.0051667 | 19.2809
0.711 | 0.76318 | 0.05448 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.73091 | 19.5007 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70583 | 0.052 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.97342 | 0.70798 | 19.2946 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70583 | 0.052 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97342 | 0.70798 | 19.2946 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70583 | 0.052 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97342 | 0.70798 | 711 | 707.9797 | 0.97342 | 1.0932 | 0.0051667 | 19.2946
0.712 | 0.76422 | 0.054485 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.73246 | 19.5145 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70683 | 0.052005 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.97343 | 0.70949 | 19.3083 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70683 | 0.052005 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97343 | 0.70949 | 19.3083 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70683 | 0.052005 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97343 | 0.70949 | 712 | 709.4925 | 0.97343 | 1.0932 | 0.0051667 | 19.3083
0.713 | 0.76526 | 0.054489 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.73401 | 19.5283 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70783 | 0.052011 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.97345 | 0.71101 | 19.3221 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70783 | 0.052011 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97345 | 0.71101 | 19.3221 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70783 | 0.052011 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97345 | 0.71101 | 713 | 711.0063 | 0.97345 | 1.0932 | 0.0051667 | 19.3221
0.714 | 0.7663 | 0.054494 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.73556 | 19.542 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70883 | 0.052016 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.97346 | 0.71252 | 19.3358 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70883 | 0.052016 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97346 | 0.71252 | 19.3358 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70883 | 0.052016 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97346 | 0.71252 | 714 | 712.5212 | 0.97346 | 1.0932 | 0.0051667 | 19.3358
0.715 | 0.76734 | 0.054498 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.73712 | 19.5557 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70983 | 0.052022 | 1.0934 | 1.0932 | 1.0932 | 1.0932 | 0.97348 | 0.71404 | 19.3495 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70983 | 0.052022 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97348 | 0.71404 | 19.3495 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.70983 | 0.052022 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97348 | 0.71404 | 715 | 714.0371 | 0.97348 | 1.0932 | 0.0051667 | 19.3495
0.716 | 0.76838 | 0.054503 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.73867 | 19.5695 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71083 | 0.052027 | 1.0934 | 1.0933 | 1.0932 | 1.0932 | 0.97349 | 0.71555 | 19.3632 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71083 | 0.052027 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97349 | 0.71555 | 19.3632 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71083 | 0.052027 | 1.0932 | 1.0932 | 1.0932 | 1.0932 | 0.97349 | 0.71555 | 716 | 715.5542 | 0.97349 | 1.0932 | 0.0051667 | 19.3632
0.717 | 0.76942 | 0.054507 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 0.74023 | 19.5832 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71183 | 0.052033 | 1.0934 | 1.0933 | 1.0933 | 1.0933 | 0.97351 | 0.71707 | 19.3769 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71183 | 0.052033 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97351 | 0.71707 | 19.3769 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71183 | 0.052033 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97351 | 0.71707 | 717 | 717.0723 | 0.97351 | 1.0933 | 0.0051667 | 19.3769
0.718 | 0.77046 | 0.054512 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 0.74178 | 19.5969 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71283 | 0.052038 | 1.0934 | 1.0933 | 1.0933 | 1.0933 | 0.97352 | 0.71859 | 19.3905 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71283 | 0.052038 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97352 | 0.71859 | 19.3905 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71283 | 0.052038 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97352 | 0.71859 | 718 | 718.5915 | 0.97352 | 1.0933 | 0.0051667 | 19.3905
0.719 | 0.7715 | 0.054516 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 0.74334 | 19.6106 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71383 | 0.052043 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.97354 | 0.72011 | 19.4042 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71383 | 0.052043 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97354 | 0.72011 | 19.4042 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71383 | 0.052043 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97354 | 0.72011 | 719 | 720.1117 | 0.97354 | 1.0933 | 0.0051667 | 19.4042
0.72 | 0.77255 | 0.054521 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 0.7449 | 19.6243 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71483 | 0.052049 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.97355 | 0.72163 | 19.4178 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71483 | 0.052049 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97355 | 0.72163 | 19.4178 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71483 | 0.052049 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97355 | 0.72163 | 720 | 721.6331 | 0.97355 | 1.0933 | 0.0051667 | 19.4178
0.721 | 0.77359 | 0.054525 | 1.0987 | 1.0987 | 1.0987 | 1.0987 | 0.74645 | 19.638 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71583 | 0.052054 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.97357 | 0.72316 | 19.4315 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71583 | 0.052054 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97357 | 0.72316 | 19.4315 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71583 | 0.052054 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97357 | 0.72316 | 721 | 723.1555 | 0.97357 | 1.0933 | 0.0051667 | 19.4315
0.722 | 0.77463 | 0.05453 | 1.0988 | 1.0987 | 1.0987 | 1.0987 | 0.74802 | 19.6517 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71683 | 0.052059 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.97358 | 0.72468 | 19.4451 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71683 | 0.052059 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97358 | 0.72468 | 19.4451 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71683 | 0.052059 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97358 | 0.72468 | 722 | 724.6789 | 0.97358 | 1.0933 | 0.0051667 | 19.4451
0.723 | 0.77567 | 0.054534 | 1.0988 | 1.0987 | 1.0987 | 1.0987 | 0.74958 | 19.6653 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71783 | 0.052064 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.97359 | 0.7262 | 19.4588 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71783 | 0.052064 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97359 | 0.7262 | 19.4588 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71783 | 0.052064 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97359 | 0.7262 | 723 | 726.2035 | 0.97359 | 1.0933 | 0.0051667 | 19.4588
0.724 | 0.77671 | 0.054539 | 1.0988 | 1.0987 | 1.0987 | 1.0987 | 0.75114 | 19.679 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71883 | 0.05207 | 1.0935 | 1.0933 | 1.0933 | 1.0933 | 0.97361 | 0.72773 | 19.4724 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71883 | 0.05207 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97361 | 0.72773 | 19.4724 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71883 | 0.05207 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97361 | 0.72773 | 724 | 727.7291 | 0.97361 | 1.0933 | 0.0051667 | 19.4724
0.725 | 0.77775 | 0.054543 | 1.0988 | 1.0987 | 1.0987 | 1.0987 | 0.7527 | 19.6926 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71983 | 0.052075 | 1.0935 | 1.0934 | 1.0933 | 1.0933 | 0.97362 | 0.72926 | 19.486 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71983 | 0.052075 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97362 | 0.72926 | 19.486 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.71983 | 0.052075 | 1.0933 | 1.0933 | 1.0933 | 1.0933 | 0.97362 | 0.72926 | 725 | 729.2558 | 0.97362 | 1.0933 | 0.0051667 | 19.486
0.726 | 0.77879 | 0.054548 | 1.0988 | 1.0987 | 1.0987 | 1.0987 | 0.75427 | 19.7062 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72083 | 0.05208 | 1.0935 | 1.0934 | 1.0934 | 1.0934 | 0.97364 | 0.73078 | 19.4996 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72083 | 0.05208 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97364 | 0.73078 | 19.4996 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72083 | 0.05208 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97364 | 0.73078 | 726 | 730.7835 | 0.97364 | 1.0934 | 0.0051667 | 19.4996
0.727 | 0.77983 | 0.054552 | 1.0988 | 1.0988 | 1.0988 | 1.0988 | 0.75583 | 19.7199 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72183 | 0.052086 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.97365 | 0.73231 | 19.5132 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72183 | 0.052086 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97365 | 0.73231 | 19.5132 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72183 | 0.052086 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97365 | 0.73231 | 727 | 732.3123 | 0.97365 | 1.0934 | 0.0051667 | 19.5132
0.728 | 0.78088 | 0.054557 | 1.0988 | 1.0988 | 1.0988 | 1.0988 | 0.7574 | 19.7335 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72283 | 0.052091 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.97367 | 0.73384 | 19.5267 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72283 | 0.052091 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97367 | 0.73384 | 19.5267 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72283 | 0.052091 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97367 | 0.73384 | 728 | 733.8422 | 0.97367 | 1.0934 | 0.0051667 | 19.5267
0.729 | 0.78192 | 0.054561 | 1.0988 | 1.0988 | 1.0988 | 1.0988 | 0.75897 | 19.7471 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72383 | 0.052096 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.97368 | 0.73537 | 19.5403 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72383 | 0.052096 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97368 | 0.73537 | 19.5403 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72383 | 0.052096 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97368 | 0.73537 | 729 | 735.3732 | 0.97368 | 1.0934 | 0.0051667 | 19.5403
0.73 | 0.78296 | 0.054565 | 1.0988 | 1.0988 | 1.0988 | 1.0988 | 0.76054 | 19.7607 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72483 | 0.052101 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.9737 | 0.73691 | 19.5539 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72483 | 0.052101 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.9737 | 0.73691 | 19.5539 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72483 | 0.052101 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.9737 | 0.73691 | 730 | 736.9052 | 0.9737 | 1.0934 | 0.0051667 | 19.5539
0.731 | 0.784 | 0.05457 | 1.0988 | 1.0988 | 1.0988 | 1.0988 | 0.76211 | 19.7743 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72583 | 0.052106 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.97371 | 0.73844 | 19.5674 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72583 | 0.052106 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97371 | 0.73844 | 19.5674 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72583 | 0.052106 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97371 | 0.73844 | 731 | 738.4383 | 0.97371 | 1.0934 | 0.0051667 | 19.5674
0.732 | 0.78504 | 0.054574 | 1.0988 | 1.0988 | 1.0988 | 1.0988 | 0.76368 | 19.7879 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72683 | 0.052112 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.97372 | 0.73997 | 19.581 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72683 | 0.052112 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97372 | 0.73997 | 19.581 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72683 | 0.052112 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97372 | 0.73997 | 732 | 739.9724 | 0.97372 | 1.0934 | 0.0051667 | 19.581
0.733 | 0.78608 | 0.054578 | 1.0989 | 1.0988 | 1.0988 | 1.0988 | 0.76525 | 19.8014 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72783 | 0.052117 | 1.0936 | 1.0934 | 1.0934 | 1.0934 | 0.97374 | 0.74151 | 19.5945 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72783 | 0.052117 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97374 | 0.74151 | 19.5945 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72783 | 0.052117 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97374 | 0.74151 | 733 | 741.5076 | 0.97374 | 1.0934 | 0.0051667 | 19.5945
0.734 | 0.78712 | 0.054583 | 1.0989 | 1.0988 | 1.0988 | 1.0988 | 0.76682 | 19.815 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72883 | 0.052122 | 1.0936 | 1.0935 | 1.0935 | 1.0934 | 0.97375 | 0.74304 | 19.608 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72883 | 0.052122 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97375 | 0.74304 | 19.608 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72883 | 0.052122 | 1.0934 | 1.0934 | 1.0934 | 1.0934 | 0.97375 | 0.74304 | 734 | 743.0439 | 0.97375 | 1.0934 | 0.0051667 | 19.608
0.735 | 0.78816 | 0.054587 | 1.0989 | 1.0988 | 1.0988 | 1.0988 | 0.7684 | 19.8285 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72983 | 0.052127 | 1.0936 | 1.0935 | 1.0935 | 1.0935 | 0.97377 | 0.74458 | 19.6215 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72983 | 0.052127 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97377 | 0.74458 | 19.6215 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.72983 | 0.052127 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97377 | 0.74458 | 735 | 744.5812 | 0.97377 | 1.0935 | 0.0051667 | 19.6215
0.736 | 0.7892 | 0.054591 | 1.0989 | 1.0988 | 1.0988 | 1.0988 | 0.76997 | 19.8421 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73083 | 0.052132 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97378 | 0.74612 | 19.635 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73083 | 0.052132 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97378 | 0.74612 | 19.635 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73083 | 0.052132 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97378 | 0.74612 | 736 | 746.1196 | 0.97378 | 1.0935 | 0.0051667 | 19.635
0.737 | 0.79025 | 0.054596 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.77155 | 19.8556 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73183 | 0.052137 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97379 | 0.74766 | 19.6485 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73183 | 0.052137 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97379 | 0.74766 | 19.6485 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73183 | 0.052137 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97379 | 0.74766 | 737 | 747.659 | 0.97379 | 1.0935 | 0.0051667 | 19.6485
0.738 | 0.79129 | 0.0546 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.77313 | 19.8691 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73283 | 0.052142 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97381 | 0.7492 | 19.662 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73283 | 0.052142 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97381 | 0.7492 | 19.662 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73283 | 0.052142 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97381 | 0.7492 | 738 | 749.1995 | 0.97381 | 1.0935 | 0.0051667 | 19.662
0.739 | 0.79233 | 0.054604 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.7747 | 19.8826 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73383 | 0.052147 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97382 | 0.75074 | 19.6755 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73383 | 0.052147 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97382 | 0.75074 | 19.6755 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73383 | 0.052147 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97382 | 0.75074 | 739 | 750.7411 | 0.97382 | 1.0935 | 0.0051667 | 19.6755
0.74 | 0.79337 | 0.054608 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.77628 | 19.8962 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73483 | 0.052152 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97384 | 0.75228 | 19.689 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73483 | 0.052152 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97384 | 0.75228 | 19.689 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73483 | 0.052152 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97384 | 0.75228 | 740 | 752.2837 | 0.97384 | 1.0935 | 0.0051667 | 19.689
0.741 | 0.79441 | 0.054613 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.77786 | 19.9096 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73583 | 0.052158 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97385 | 0.75383 | 19.7024 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73583 | 0.052158 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97385 | 0.75383 | 19.7024 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73583 | 0.052158 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97385 | 0.75383 | 741 | 753.8274 | 0.97385 | 1.0935 | 0.0051667 | 19.7024
0.742 | 0.79545 | 0.054617 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.77945 | 19.9231 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73683 | 0.052163 | 1.0937 | 1.0935 | 1.0935 | 1.0935 | 0.97386 | 0.75537 | 19.7159 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73683 | 0.052163 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97386 | 0.75537 | 19.7159 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73683 | 0.052163 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97386 | 0.75537 | 742 | 755.3721 | 0.97386 | 1.0935 | 0.0051667 | 19.7159
0.743 | 0.79649 | 0.054621 | 1.0989 | 1.0989 | 1.0989 | 1.0989 | 0.78103 | 19.9366 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73783 | 0.052168 | 1.0937 | 1.0936 | 1.0935 | 1.0935 | 0.97388 | 0.75692 | 19.7293 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73783 | 0.052168 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97388 | 0.75692 | 19.7293 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73783 | 0.052168 | 1.0935 | 1.0935 | 1.0935 | 1.0935 | 0.97388 | 0.75692 | 743 | 756.9179 | 0.97388 | 1.0935 | 0.0051667 | 19.7293
0.744 | 0.79753 | 0.054625 | 1.099 | 1.0989 | 1.0989 | 1.0989 | 0.78261 | 19.9501 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73883 | 0.052173 | 1.0937 | 1.0936 | 1.0936 | 1.0936 | 0.97389 | 0.75846 | 19.7427 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73883 | 0.052173 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97389 | 0.75846 | 19.7427 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73883 | 0.052173 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97389 | 0.75846 | 744 | 758.4647 | 0.97389 | 1.0936 | 0.0051667 | 19.7427
0.745 | 0.79857 | 0.05463 | 1.099 | 1.0989 | 1.0989 | 1.0989 | 0.7842 | 19.9635 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73983 | 0.052178 | 1.0937 | 1.0936 | 1.0936 | 1.0936 | 0.97391 | 0.76001 | 19.7562 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73983 | 0.052178 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97391 | 0.76001 | 19.7562 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.73983 | 0.052178 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97391 | 0.76001 | 745 | 760.0126 | 0.97391 | 1.0936 | 0.0051667 | 19.7562
0.746 | 0.79962 | 0.054634 | 1.099 | 1.0989 | 1.0989 | 1.0989 | 0.78578 | 19.977 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74083 | 0.052183 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97392 | 0.76156 | 19.7696 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74083 | 0.052183 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97392 | 0.76156 | 19.7696 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74083 | 0.052183 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97392 | 0.76156 | 746 | 761.5616 | 0.97392 | 1.0936 | 0.0051667 | 19.7696
0.747 | 0.80066 | 0.054638 | 1.099 | 1.0989 | 1.0989 | 1.0989 | 0.78737 | 19.9904 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74183 | 0.052188 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97393 | 0.76311 | 19.783 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74183 | 0.052188 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97393 | 0.76311 | 19.783 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74183 | 0.052188 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97393 | 0.76311 | 747 | 763.1116 | 0.97393 | 1.0936 | 0.0051667 | 19.783
0.748 | 0.8017 | 0.054642 | 1.099 | 1.099 | 1.099 | 1.099 | 0.78896 | 20.0039 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7428 | 0.052177 | 1.0937 | 1.0936 | 1.0936 | 1.0936 | 0.97378 | 0.76451 | 19.795 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74283 | 0.052193 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97395 | 0.76466 | 19.7964 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74283 | 0.052193 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97395 | 0.76466 | 748 | 764.6626 | 0.97395 | 1.0936 | 0.0051667 | 19.7964
0.749 | 0.80274 | 0.054646 | 1.099 | 1.099 | 1.099 | 1.099 | 0.79055 | 20.0173 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7438 | 0.052182 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97379 | 0.76606 | 19.8084 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74383 | 0.052197 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97396 | 0.76621 | 19.8098 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74383 | 0.052197 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97396 | 0.76621 | 749 | 766.2147 | 0.97396 | 1.0936 | 0.0051667 | 19.8098
0.75 | 0.80378 | 0.054651 | 1.099 | 1.099 | 1.099 | 1.099 | 0.79214 | 20.0307 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7448 | 0.052187 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97381 | 0.76761 | 19.8218 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74483 | 0.052202 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97397 | 0.76777 | 19.8231 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74483 | 0.052202 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97397 | 0.76777 | 750 | 767.7679 | 0.97397 | 1.0936 | 0.0051667 | 19.8231
0.751 | 0.80482 | 0.054655 | 1.099 | 1.099 | 1.099 | 1.099 | 0.79373 | 20.0441 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7458 | 0.052192 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97382 | 0.76917 | 19.8352 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74583 | 0.052207 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97399 | 0.76932 | 19.8365 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74583 | 0.052207 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.97399 | 0.76932 | 751 | 769.3221 | 0.97399 | 1.0936 | 0.0051667 | 19.8365
0.752 | 0.80586 | 0.054659 | 1.099 | 1.099 | 1.099 | 1.099 | 0.79532 | 20.0575 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7468 | 0.052197 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97383 | 0.77072 | 19.8485 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74683 | 0.052212 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.974 | 0.77088 | 19.8499 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74683 | 0.052212 | 1.0936 | 1.0936 | 1.0936 | 1.0936 | 0.974 | 0.77088 | 752 | 770.8773 | 0.974 | 1.0936 | 0.0051667 | 19.8499
0.753 | 0.8069 | 0.054663 | 1.099 | 1.099 | 1.099 | 1.099 | 0.79692 | 20.0709 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7478 | 0.052202 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97385 | 0.77228 | 19.8619 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74783 | 0.052217 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97401 | 0.77243 | 19.8632 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74783 | 0.052217 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97401 | 0.77243 | 753 | 772.4336 | 0.97401 | 1.0937 | 0.0051667 | 19.8632
0.754 | 0.80795 | 0.054667 | 1.099 | 1.099 | 1.099 | 1.099 | 0.79851 | 20.0843 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7488 | 0.052207 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97386 | 0.77384 | 19.8752 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74883 | 0.052222 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97403 | 0.77399 | 19.8765 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74883 | 0.052222 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97403 | 0.77399 | 754 | 773.991 | 0.97403 | 1.0937 | 0.0051667 | 19.8765
0.755 | 0.80899 | 0.054671 | 1.0991 | 1.099 | 1.099 | 1.099 | 0.80011 | 20.0976 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7498 | 0.052211 | 1.0938 | 1.0936 | 1.0936 | 1.0936 | 0.97387 | 0.77539 | 19.8885 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74983 | 0.052227 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97404 | 0.77555 | 19.8899 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.74983 | 0.052227 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97404 | 0.77555 | 755 | 775.5494 | 0.97404 | 1.0937 | 0.0051667 | 19.8899
0.756 | 0.81003 | 0.054675 | 1.0991 | 1.099 | 1.099 | 1.099 | 0.8017 | 20.111 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7508 | 0.052216 | 1.0938 | 1.0937 | 1.0937 | 1.0937 | 0.97389 | 0.77695 | 19.9019 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75083 | 0.052232 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97405 | 0.77711 | 19.9032 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75083 | 0.052232 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97405 | 0.77711 | 756 | 777.1088 | 0.97405 | 1.0937 | 0.0051667 | 19.9032
0.757 | 0.81107 | 0.054679 | 1.0991 | 1.099 | 1.099 | 1.099 | 0.8033 | 20.1243 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7518 | 0.052221 | 1.0938 | 1.0937 | 1.0937 | 1.0937 | 0.9739 | 0.77851 | 19.9152 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75183 | 0.052237 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97407 | 0.77867 | 19.9165 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75183 | 0.052237 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97407 | 0.77867 | 757 | 778.6693 | 0.97407 | 1.0937 | 0.0051667 | 19.9165
0.758 | 0.81211 | 0.054683 | 1.0991 | 1.099 | 1.099 | 1.099 | 0.8049 | 20.1377 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7528 | 0.052226 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97391 | 0.78007 | 19.9285 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75283 | 0.052241 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97408 | 0.78023 | 19.9298 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75283 | 0.052241 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97408 | 0.78023 | 758 | 780.2308 | 0.97408 | 1.0937 | 0.0051667 | 19.9298
0.759 | 0.81315 | 0.054687 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.8065 | 20.151 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7538 | 0.052231 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97393 | 0.78164 | 19.9418 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75383 | 0.052246 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97409 | 0.78179 | 19.9431 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75383 | 0.052246 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97409 | 0.78179 | 759 | 781.7934 | 0.97409 | 1.0937 | 0.0051667 | 19.9431
0.76 | 0.81419 | 0.054692 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.8081 | 20.1643 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7548 | 0.052236 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97394 | 0.7832 | 19.9551 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75483 | 0.052251 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97411 | 0.78336 | 19.9564 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75483 | 0.052251 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97411 | 0.78336 | 760 | 783.357 | 0.97411 | 1.0937 | 0.0051667 | 19.9564
0.761 | 0.81523 | 0.054696 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.8097 | 20.1777 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7558 | 0.05224 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97395 | 0.78476 | 19.9683 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75583 | 0.052256 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97412 | 0.78492 | 19.9697 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75583 | 0.052256 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97412 | 0.78492 | 761 | 784.9216 | 0.97412 | 1.0937 | 0.0051667 | 19.9697
0.762 | 0.81627 | 0.0547 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.81131 | 20.191 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7568 | 0.052245 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97397 | 0.78633 | 19.9816 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75683 | 0.052261 | 1.0937 | 1.0938 | 1.0938 | 1.0938 | 0.97413 | 0.78649 | 19.9829 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75683 | 0.052261 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97413 | 0.78649 | 762 | 786.4873 | 0.97413 | 1.0938 | 0.0051667 | 19.9829
0.763 | 0.81732 | 0.054704 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.81291 | 20.2043 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7578 | 0.05225 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97398 | 0.7879 | 19.9949 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75783 | 0.052265 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97415 | 0.78805 | 19.9962 | 0.0059 | 0.0048 | 0.0051667 | 0.64058 | 0.75783 | 0.052265 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97415 | 0.78805 | 763 | 788.0541 | 0.97415 | 1.0938 | 0.0051667 | 19.9962
0.764 | 0.81836 | 0.054708 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.81452 | 20.2176 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7588 | 0.052255 | 1.0939 | 1.0937 | 1.0937 | 1.0937 | 0.97399 | 0.78946 | 20.0081 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7588 | 0.052255 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97399 | 0.78946 | 20.0081 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7588 | 0.052255 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97399 | 0.78946 | 764 | 789.4635 | 0.97399 | 1.0937 | 0.0052 | 20.0081
0.765 | 0.8194 | 0.054712 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.81612 | 20.2308 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7598 | 0.05226 | 1.0939 | 1.0938 | 1.0937 | 1.0937 | 0.97401 | 0.79103 | 20.0214 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7598 | 0.05226 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97401 | 0.79103 | 20.0214 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7598 | 0.05226 | 1.0937 | 1.0937 | 1.0937 | 1.0937 | 0.97401 | 0.79103 | 765 | 791.0321 | 0.97401 | 1.0937 | 0.0052 | 20.0214
0.766 | 0.82044 | 0.054716 | 1.0991 | 1.0991 | 1.0991 | 1.0991 | 0.81773 | 20.2441 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7608 | 0.052264 | 1.0939 | 1.0938 | 1.0938 | 1.0938 | 0.97402 | 0.7926 | 20.0346 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7608 | 0.052264 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97402 | 0.7926 | 20.0346 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7608 | 0.052264 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97402 | 0.7926 | 766 | 792.6017 | 0.97402 | 1.0938 | 0.0052 | 20.0346
0.767 | 0.82148 | 0.05472 | 1.0992 | 1.0991 | 1.0991 | 1.0991 | 0.81934 | 20.2574 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7618 | 0.052269 | 1.0939 | 1.0938 | 1.0938 | 1.0938 | 0.97403 | 0.79417 | 20.0478 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7618 | 0.052269 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97403 | 0.79417 | 20.0478 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7618 | 0.052269 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97403 | 0.79417 | 767 | 794.1723 | 0.97403 | 1.0938 | 0.0052 | 20.0478
0.768 | 0.82252 | 0.054724 | 1.0992 | 1.0991 | 1.0991 | 1.0991 | 0.82095 | 20.2706 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7628 | 0.052274 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.97405 | 0.79574 | 20.061 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7628 | 0.052274 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97405 | 0.79574 | 20.061 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7628 | 0.052274 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97405 | 0.79574 | 768 | 795.744 | 0.97405 | 1.0938 | 0.0052 | 20.061
0.769 | 0.82356 | 0.054728 | 1.0992 | 1.0991 | 1.0991 | 1.0991 | 0.82256 | 20.2839 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7638 | 0.052278 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.97406 | 0.79732 | 20.0742 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7638 | 0.052278 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97406 | 0.79732 | 20.0742 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7638 | 0.052278 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97406 | 0.79732 | 769 | 797.3168 | 0.97406 | 1.0938 | 0.0052 | 20.0742
0.77 | 0.8246 | 0.054732 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.82417 | 20.2971 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7648 | 0.052283 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.97407 | 0.79889 | 20.0874 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7648 | 0.052283 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97407 | 0.79889 | 20.0874 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7648 | 0.052283 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97407 | 0.79889 | 770 | 798.8905 | 0.97407 | 1.0938 | 0.0052 | 20.0874
0.771 | 0.82565 | 0.054735 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.82578 | 20.3103 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7658 | 0.052288 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.97408 | 0.80047 | 20.1006 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7658 | 0.052288 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97408 | 0.80047 | 20.1006 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7658 | 0.052288 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97408 | 0.80047 | 771 | 800.4653 | 0.97408 | 1.0938 | 0.0052 | 20.1006
0.772 | 0.82669 | 0.054739 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.8274 | 20.3236 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7668 | 0.052293 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.9741 | 0.80204 | 20.1138 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7668 | 0.052293 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.9741 | 0.80204 | 20.1138 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7668 | 0.052293 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.9741 | 0.80204 | 772 | 802.0412 | 0.9741 | 1.0938 | 0.0052 | 20.1138
0.773 | 0.82773 | 0.054743 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.82901 | 20.3368 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7678 | 0.052297 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.97411 | 0.80362 | 20.127 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7678 | 0.052297 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97411 | 0.80362 | 20.127 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7678 | 0.052297 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97411 | 0.80362 | 773 | 803.618 | 0.97411 | 1.0938 | 0.0052 | 20.127
0.774 | 0.82877 | 0.054747 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.83063 | 20.35 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7688 | 0.052302 | 1.094 | 1.0938 | 1.0938 | 1.0938 | 0.97412 | 0.8052 | 20.1402 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7688 | 0.052302 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97412 | 0.8052 | 20.1402 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7688 | 0.052302 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97412 | 0.8052 | 774 | 805.1959 | 0.97412 | 1.0938 | 0.0052 | 20.1402
0.775 | 0.82981 | 0.054751 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.83224 | 20.3632 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7698 | 0.052307 | 1.094 | 1.0939 | 1.0938 | 1.0938 | 0.97414 | 0.80677 | 20.1533 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7698 | 0.052307 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97414 | 0.80677 | 20.1533 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7698 | 0.052307 | 1.0938 | 1.0938 | 1.0938 | 1.0938 | 0.97414 | 0.80677 | 775 | 806.7749 | 0.97414 | 1.0938 | 0.0052 | 20.1533
0.776 | 0.83085 | 0.054755 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.83386 | 20.3764 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7708 | 0.052311 | 1.094 | 1.0939 | 1.0939 | 1.0939 | 0.97415 | 0.80835 | 20.1665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7708 | 0.052311 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97415 | 0.80835 | 20.1665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7708 | 0.052311 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97415 | 0.80835 | 776 | 808.3548 | 0.97415 | 1.0939 | 0.0052 | 20.1665
0.777 | 0.83189 | 0.054759 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.83548 | 20.3895 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7718 | 0.052316 | 1.094 | 1.0939 | 1.0939 | 1.0939 | 0.97416 | 0.80994 | 20.1796 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7718 | 0.052316 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97416 | 0.80994 | 20.1796 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7718 | 0.052316 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97416 | 0.80994 | 777 | 809.9358 | 0.97416 | 1.0939 | 0.0052 | 20.1796
0.778 | 0.83293 | 0.054763 | 1.0992 | 1.0992 | 1.0992 | 1.0992 | 0.8371 | 20.4027 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7728 | 0.05232 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.97417 | 0.81152 | 20.1927 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7728 | 0.05232 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97417 | 0.81152 | 20.1927 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7728 | 0.05232 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97417 | 0.81152 | 778 | 811.5179 | 0.97417 | 1.0939 | 0.0052 | 20.1927
0.779 | 0.83397 | 0.054767 | 1.0993 | 1.0992 | 1.0992 | 1.0992 | 0.83872 | 20.4159 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7738 | 0.052325 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.97419 | 0.8131 | 20.2058 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7738 | 0.052325 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97419 | 0.8131 | 20.2058 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7738 | 0.052325 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97419 | 0.8131 | 779 | 813.1009 | 0.97419 | 1.0939 | 0.0052 | 20.2058
0.78 | 0.83502 | 0.054771 | 1.0993 | 1.0992 | 1.0992 | 1.0992 | 0.84034 | 20.429 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7748 | 0.05233 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.9742 | 0.81469 | 20.219 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7748 | 0.05233 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.9742 | 0.81469 | 20.219 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7748 | 0.05233 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.9742 | 0.81469 | 780 | 814.685 | 0.9742 | 1.0939 | 0.0052 | 20.219
0.781 | 0.83606 | 0.054774 | 1.0993 | 1.0992 | 1.0992 | 1.0992 | 0.84197 | 20.4422 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7758 | 0.052334 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.97421 | 0.81627 | 20.2321 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7758 | 0.052334 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97421 | 0.81627 | 20.2321 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7758 | 0.052334 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97421 | 0.81627 | 781 | 816.2701 | 0.97421 | 1.0939 | 0.0052 | 20.2321
0.782 | 0.8371 | 0.054778 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.84359 | 20.4553 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7768 | 0.052339 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.97422 | 0.81786 | 20.2452 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7768 | 0.052339 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97422 | 0.81786 | 20.2452 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7768 | 0.052339 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97422 | 0.81786 | 782 | 817.8563 | 0.97422 | 1.0939 | 0.0052 | 20.2452
0.783 | 0.83814 | 0.054782 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.84521 | 20.4684 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7778 | 0.052343 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.97424 | 0.81944 | 20.2582 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7778 | 0.052343 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97424 | 0.81944 | 20.2582 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7778 | 0.052343 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97424 | 0.81944 | 783 | 819.4434 | 0.97424 | 1.0939 | 0.0052 | 20.2582
0.784 | 0.83918 | 0.054786 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.84684 | 20.4816 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7788 | 0.052348 | 1.0941 | 1.0939 | 1.0939 | 1.0939 | 0.97425 | 0.82103 | 20.2713 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7788 | 0.052348 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97425 | 0.82103 | 20.2713 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7788 | 0.052348 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97425 | 0.82103 | 784 | 821.0316 | 0.97425 | 1.0939 | 0.0052 | 20.2713
0.785 | 0.84022 | 0.05479 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.84847 | 20.4947 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7798 | 0.052352 | 1.0941 | 1.094 | 1.0939 | 1.0939 | 0.97426 | 0.82262 | 20.2844 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7798 | 0.052352 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97426 | 0.82262 | 20.2844 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7798 | 0.052352 | 1.0939 | 1.0939 | 1.0939 | 1.0939 | 0.97426 | 0.82262 | 785 | 822.6209 | 0.97426 | 1.0939 | 0.0052 | 20.2844
0.786 | 0.84126 | 0.054793 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.8501 | 20.5078 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7808 | 0.052357 | 1.0941 | 1.094 | 1.094 | 1.094 | 0.97427 | 0.82421 | 20.2975 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7808 | 0.052357 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97427 | 0.82421 | 20.2975 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7808 | 0.052357 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97427 | 0.82421 | 786 | 824.2111 | 0.97427 | 1.094 | 0.0052 | 20.2975
0.787 | 0.8423 | 0.054797 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.85173 | 20.5209 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7818 | 0.052361 | 1.0941 | 1.094 | 1.094 | 1.094 | 0.97429 | 0.8258 | 20.3105 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7818 | 0.052361 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97429 | 0.8258 | 20.3105 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7818 | 0.052361 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97429 | 0.8258 | 787 | 825.8024 | 0.97429 | 1.094 | 0.0052 | 20.3105
0.788 | 0.84335 | 0.054801 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.85336 | 20.5339 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7828 | 0.052366 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.9743 | 0.82739 | 20.3236 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7828 | 0.052366 | 1.094 | 1.094 | 1.094 | 1.094 | 0.9743 | 0.82739 | 20.3236 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7828 | 0.052366 | 1.094 | 1.094 | 1.094 | 1.094 | 0.9743 | 0.82739 | 788 | 827.3947 | 0.9743 | 1.094 | 0.0052 | 20.3236
0.789 | 0.84439 | 0.054805 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.85499 | 20.547 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7838 | 0.05237 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.97431 | 0.82899 | 20.3366 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7838 | 0.05237 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97431 | 0.82899 | 20.3366 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7838 | 0.05237 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97431 | 0.82899 | 789 | 828.988 | 0.97431 | 1.094 | 0.0052 | 20.3366
0.79 | 0.84543 | 0.054809 | 1.0993 | 1.0993 | 1.0993 | 1.0993 | 0.85662 | 20.5601 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7848 | 0.052375 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.97432 | 0.83058 | 20.3496 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7848 | 0.052375 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97432 | 0.83058 | 20.3496 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7848 | 0.052375 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97432 | 0.83058 | 790 | 830.5824 | 0.97432 | 1.094 | 0.0052 | 20.3496
0.791 | 0.84647 | 0.054812 | 1.0994 | 1.0993 | 1.0993 | 1.0993 | 0.85825 | 20.5731 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7858 | 0.052379 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.97434 | 0.83218 | 20.3626 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7858 | 0.052379 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97434 | 0.83218 | 20.3626 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7858 | 0.052379 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97434 | 0.83218 | 791 | 832.1777 | 0.97434 | 1.094 | 0.0052 | 20.3626
0.792 | 0.84751 | 0.054816 | 1.0994 | 1.0993 | 1.0993 | 1.0993 | 0.85989 | 20.5862 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7868 | 0.052384 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.97435 | 0.83377 | 20.3757 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7868 | 0.052384 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97435 | 0.83377 | 20.3757 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7868 | 0.052384 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97435 | 0.83377 | 792 | 833.7741 | 0.97435 | 1.094 | 0.0052 | 20.3757
0.793 | 0.84855 | 0.05482 | 1.0994 | 1.0993 | 1.0993 | 1.0993 | 0.86152 | 20.5992 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7878 | 0.052388 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.97436 | 0.83537 | 20.3887 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7878 | 0.052388 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97436 | 0.83537 | 20.3887 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7878 | 0.052388 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97436 | 0.83537 | 793 | 835.3715 | 0.97436 | 1.094 | 0.0052 | 20.3887
0.794 | 0.84959 | 0.054824 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.86316 | 20.6123 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7888 | 0.052393 | 1.0942 | 1.094 | 1.094 | 1.094 | 0.97437 | 0.83697 | 20.4017 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7888 | 0.052393 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97437 | 0.83697 | 20.4017 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7888 | 0.052393 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97437 | 0.83697 | 794 | 836.97 | 0.97437 | 1.094 | 0.0052 | 20.4017
0.795 | 0.85063 | 0.054827 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.8648 | 20.6253 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7898 | 0.052397 | 1.0942 | 1.0941 | 1.094 | 1.094 | 0.97438 | 0.83857 | 20.4146 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7898 | 0.052397 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97438 | 0.83857 | 20.4146 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7898 | 0.052397 | 1.094 | 1.094 | 1.094 | 1.094 | 0.97438 | 0.83857 | 795 | 838.5694 | 0.97438 | 1.094 | 0.0052 | 20.4146
0.796 | 0.85167 | 0.054831 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.86644 | 20.6383 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7908 | 0.052401 | 1.0942 | 1.0941 | 1.0941 | 1.0941 | 0.9744 | 0.84017 | 20.4276 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7908 | 0.052401 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.9744 | 0.84017 | 20.4276 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7908 | 0.052401 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.9744 | 0.84017 | 796 | 840.1699 | 0.9744 | 1.0941 | 0.0052 | 20.4276
0.797 | 0.85272 | 0.054835 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.86808 | 20.6513 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7918 | 0.052406 | 1.0942 | 1.0941 | 1.0941 | 1.0941 | 0.97441 | 0.84177 | 20.4406 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7918 | 0.052406 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97441 | 0.84177 | 20.4406 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7918 | 0.052406 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97441 | 0.84177 | 797 | 841.7714 | 0.97441 | 1.0941 | 0.0052 | 20.4406
0.798 | 0.85376 | 0.054838 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.86972 | 20.6643 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7928 | 0.05241 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97442 | 0.84337 | 20.4536 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7928 | 0.05241 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97442 | 0.84337 | 20.4536 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7928 | 0.05241 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97442 | 0.84337 | 798 | 843.3739 | 0.97442 | 1.0941 | 0.0052 | 20.4536
0.799 | 0.8548 | 0.054842 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.87136 | 20.6773 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7938 | 0.052415 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97443 | 0.84498 | 20.4665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7938 | 0.052415 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97443 | 0.84498 | 20.4665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7938 | 0.052415 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97443 | 0.84498 | 799 | 844.9774 | 0.97443 | 1.0941 | 0.0052 | 20.4665
0.8 | 0.85584 | 0.054846 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.873 | 20.6903 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7948 | 0.052419 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97444 | 0.84658 | 20.4795 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7948 | 0.052419 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97444 | 0.84658 | 20.4795 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7948 | 0.052419 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97444 | 0.84658 | 800 | 846.5819 | 0.97444 | 1.0941 | 0.0052 | 20.4795
0.801 | 0.85688 | 0.054849 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.87465 | 20.7033 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7958 | 0.052423 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97446 | 0.84819 | 20.4924 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7958 | 0.052423 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97446 | 0.84819 | 20.4924 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7958 | 0.052423 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97446 | 0.84819 | 801 | 848.1875 | 0.97446 | 1.0941 | 0.0052 | 20.4924
0.802 | 0.85792 | 0.054853 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.87629 | 20.7163 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7968 | 0.052428 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97447 | 0.84979 | 20.5053 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7968 | 0.052428 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97447 | 0.84979 | 20.5053 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7968 | 0.052428 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97447 | 0.84979 | 802 | 849.794 | 0.97447 | 1.0941 | 0.0052 | 20.5053
0.803 | 0.85896 | 0.054857 | 1.0994 | 1.0994 | 1.0994 | 1.0994 | 0.87794 | 20.7292 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7978 | 0.052432 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97448 | 0.8514 | 20.5183 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7978 | 0.052432 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97448 | 0.8514 | 20.5183 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7978 | 0.052432 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97448 | 0.8514 | 803 | 851.4016 | 0.97448 | 1.0941 | 0.0052 | 20.5183
0.804 | 0.86 | 0.05486 | 1.0995 | 1.0994 | 1.0994 | 1.0994 | 0.87958 | 20.7422 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7988 | 0.052436 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.97449 | 0.85301 | 20.5312 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7988 | 0.052436 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97449 | 0.85301 | 20.5312 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7988 | 0.052436 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97449 | 0.85301 | 804 | 853.0102 | 0.97449 | 1.0941 | 0.0052 | 20.5312
0.805 | 0.86104 | 0.054864 | 1.0995 | 1.0994 | 1.0994 | 1.0994 | 0.88123 | 20.7551 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7998 | 0.052441 | 1.0943 | 1.0941 | 1.0941 | 1.0941 | 0.9745 | 0.85462 | 20.5441 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7998 | 0.052441 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.9745 | 0.85462 | 20.5441 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.7998 | 0.052441 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.9745 | 0.85462 | 805 | 854.6198 | 0.9745 | 1.0941 | 0.0052 | 20.5441
0.806 | 0.86209 | 0.054868 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.88288 | 20.7681 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8008 | 0.052445 | 1.0943 | 1.0942 | 1.0941 | 1.0941 | 0.97452 | 0.85623 | 20.557 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8008 | 0.052445 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97452 | 0.85623 | 20.557 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8008 | 0.052445 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 0.97452 | 0.85623 | 806 | 856.2304 | 0.97452 | 1.0941 | 0.0052 | 20.557
0.807 | 0.86313 | 0.054871 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.88453 | 20.781 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8018 | 0.052449 | 1.0943 | 1.0942 | 1.0942 | 1.0942 | 0.97453 | 0.85784 | 20.5699 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8018 | 0.052449 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97453 | 0.85784 | 20.5699 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8018 | 0.052449 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97453 | 0.85784 | 807 | 857.842 | 0.97453 | 1.0942 | 0.0052 | 20.5699
0.808 | 0.86417 | 0.054875 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.88618 | 20.7939 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8028 | 0.052454 | 1.0943 | 1.0942 | 1.0942 | 1.0942 | 0.97454 | 0.85945 | 20.5827 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8028 | 0.052454 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97454 | 0.85945 | 20.5827 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8028 | 0.052454 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97454 | 0.85945 | 808 | 859.4547 | 0.97454 | 1.0942 | 0.0052 | 20.5827
0.809 | 0.86521 | 0.054878 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.88783 | 20.8068 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8038 | 0.052458 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97455 | 0.86107 | 20.5956 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8038 | 0.052458 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97455 | 0.86107 | 20.5956 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8038 | 0.052458 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97455 | 0.86107 | 809 | 861.0683 | 0.97455 | 1.0942 | 0.0052 | 20.5956
0.81 | 0.86625 | 0.054882 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.88949 | 20.8197 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8048 | 0.052462 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97456 | 0.86268 | 20.6085 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8048 | 0.052462 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97456 | 0.86268 | 20.6085 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8048 | 0.052462 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97456 | 0.86268 | 810 | 862.683 | 0.97456 | 1.0942 | 0.0052 | 20.6085
0.811 | 0.86729 | 0.054886 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.89114 | 20.8326 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8058 | 0.052466 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97457 | 0.8643 | 20.6213 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8058 | 0.052466 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97457 | 0.8643 | 20.6213 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8058 | 0.052466 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97457 | 0.8643 | 811 | 864.2987 | 0.97457 | 1.0942 | 0.0052 | 20.6213
0.812 | 0.86833 | 0.054889 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.8928 | 20.8455 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8068 | 0.052471 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97459 | 0.86592 | 20.6342 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8068 | 0.052471 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97459 | 0.86592 | 20.6342 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8068 | 0.052471 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97459 | 0.86592 | 812 | 865.9154 | 0.97459 | 1.0942 | 0.0052 | 20.6342
0.813 | 0.86937 | 0.054893 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.89445 | 20.8584 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8078 | 0.052475 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.9746 | 0.86753 | 20.647 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8078 | 0.052475 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.9746 | 0.86753 | 20.647 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8078 | 0.052475 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.9746 | 0.86753 | 813 | 867.533 | 0.9746 | 1.0942 | 0.0052 | 20.647
0.814 | 0.87042 | 0.054896 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.89611 | 20.8713 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8088 | 0.052479 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97461 | 0.86915 | 20.6599 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8088 | 0.052479 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97461 | 0.86915 | 20.6599 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8088 | 0.052479 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97461 | 0.86915 | 814 | 869.1517 | 0.97461 | 1.0942 | 0.0052 | 20.6599
0.815 | 0.87146 | 0.0549 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.89777 | 20.8842 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8098 | 0.052483 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97462 | 0.87077 | 20.6727 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8098 | 0.052483 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97462 | 0.87077 | 20.6727 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8098 | 0.052483 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97462 | 0.87077 | 815 | 870.7714 | 0.97462 | 1.0942 | 0.0052 | 20.6727
0.816 | 0.8725 | 0.054903 | 1.0995 | 1.0995 | 1.0995 | 1.0995 | 0.89943 | 20.897 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8108 | 0.052488 | 1.0944 | 1.0942 | 1.0942 | 1.0942 | 0.97463 | 0.87239 | 20.6855 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8108 | 0.052488 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97463 | 0.87239 | 20.6855 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8108 | 0.052488 | 1.0942 | 1.0942 | 1.0942 | 1.0942 | 0.97463 | 0.87239 | 816 | 872.3921 | 0.97463 | 1.0942 | 0.0052 | 20.6855
0.817 | 0.87354 | 0.054907 | 1.0996 | 1.0995 | 1.0995 | 1.0995 | 0.90109 | 20.9099 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8118 | 0.052492 | 1.0944 | 1.0943 | 1.0943 | 1.0943 | 0.97464 | 0.87401 | 20.6983 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8118 | 0.052492 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97464 | 0.87401 | 20.6983 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8118 | 0.052492 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97464 | 0.87401 | 817 | 874.0139 | 0.97464 | 1.0943 | 0.0052 | 20.6983
0.818 | 0.87458 | 0.05491 | 1.0996 | 1.0995 | 1.0995 | 1.0995 | 0.90275 | 20.9227 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8128 | 0.052496 | 1.0944 | 1.0943 | 1.0943 | 1.0943 | 0.97465 | 0.87564 | 20.7111 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8128 | 0.052496 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97465 | 0.87564 | 20.7111 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8128 | 0.052496 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97465 | 0.87564 | 818 | 875.6366 | 0.97465 | 1.0943 | 0.0052 | 20.7111
0.819 | 0.87562 | 0.054914 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.90441 | 20.9355 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8138 | 0.0525 | 1.0944 | 1.0943 | 1.0943 | 1.0943 | 0.97467 | 0.87726 | 20.7239 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8138 | 0.0525 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97467 | 0.87726 | 20.7239 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8138 | 0.0525 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97467 | 0.87726 | 819 | 877.2603 | 0.97467 | 1.0943 | 0.0052 | 20.7239
0.82 | 0.87666 | 0.054917 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.90607 | 20.9484 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8148 | 0.052504 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97468 | 0.87889 | 20.7367 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8148 | 0.052504 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97468 | 0.87889 | 20.7367 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8148 | 0.052504 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97468 | 0.87889 | 820 | 878.885 | 0.97468 | 1.0943 | 0.0052 | 20.7367
0.821 | 0.8777 | 0.054921 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.90774 | 20.9612 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8158 | 0.052508 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97469 | 0.88051 | 20.7495 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8158 | 0.052508 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97469 | 0.88051 | 20.7495 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8158 | 0.052508 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97469 | 0.88051 | 821 | 880.5107 | 0.97469 | 1.0943 | 0.0052 | 20.7495
0.822 | 0.87874 | 0.054924 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.9094 | 20.974 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8168 | 0.052513 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.9747 | 0.88214 | 20.7622 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8168 | 0.052513 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.9747 | 0.88214 | 20.7622 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8168 | 0.052513 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.9747 | 0.88214 | 822 | 882.1375 | 0.9747 | 1.0943 | 0.0052 | 20.7622
0.823 | 0.87979 | 0.054928 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.91107 | 20.9868 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8178 | 0.052517 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97471 | 0.88377 | 20.775 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8178 | 0.052517 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97471 | 0.88377 | 20.775 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8178 | 0.052517 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97471 | 0.88377 | 823 | 883.7652 | 0.97471 | 1.0943 | 0.0052 | 20.775
0.824 | 0.88083 | 0.054931 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.91274 | 20.9996 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8188 | 0.052521 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97472 | 0.88539 | 20.7878 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8188 | 0.052521 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97472 | 0.88539 | 20.7878 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8188 | 0.052521 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97472 | 0.88539 | 824 | 885.3939 | 0.97472 | 1.0943 | 0.0052 | 20.7878
0.825 | 0.88187 | 0.054935 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.91441 | 21.0124 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8198 | 0.052525 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97473 | 0.88702 | 20.8005 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8198 | 0.052525 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97473 | 0.88702 | 20.8005 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8198 | 0.052525 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97473 | 0.88702 | 825 | 887.0237 | 0.97473 | 1.0943 | 0.0052 | 20.8005
0.826 | 0.88291 | 0.054938 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.91607 | 21.0252 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8208 | 0.052529 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97474 | 0.88865 | 20.8132 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8208 | 0.052529 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97474 | 0.88865 | 20.8132 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8208 | 0.052529 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97474 | 0.88865 | 826 | 888.6544 | 0.97474 | 1.0943 | 0.0052 | 20.8132
0.827 | 0.88395 | 0.054942 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.91775 | 21.0379 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8218 | 0.052533 | 1.0945 | 1.0943 | 1.0943 | 1.0943 | 0.97476 | 0.89029 | 20.826 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8218 | 0.052533 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97476 | 0.89029 | 20.826 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8218 | 0.052533 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97476 | 0.89029 | 827 | 890.2861 | 0.97476 | 1.0943 | 0.0052 | 20.826
0.828 | 0.88499 | 0.054945 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.91942 | 21.0507 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8228 | 0.052537 | 1.0945 | 1.0944 | 1.0943 | 1.0943 | 0.97477 | 0.89192 | 20.8387 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8228 | 0.052537 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97477 | 0.89192 | 20.8387 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8228 | 0.052537 | 1.0943 | 1.0943 | 1.0943 | 1.0943 | 0.97477 | 0.89192 | 828 | 891.9189 | 0.97477 | 1.0943 | 0.0052 | 20.8387
0.829 | 0.88603 | 0.054949 | 1.0996 | 1.0996 | 1.0996 | 1.0996 | 0.92109 | 21.0634 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8238 | 0.052541 | 1.0945 | 1.0944 | 1.0944 | 1.0944 | 0.97478 | 0.89355 | 20.8514 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8238 | 0.052541 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97478 | 0.89355 | 20.8514 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8238 | 0.052541 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97478 | 0.89355 | 829 | 893.5526 | 0.97478 | 1.0944 | 0.0052 | 20.8514
0.83 | 0.88707 | 0.054952 | 1.0997 | 1.0996 | 1.0996 | 1.0996 | 0.92276 | 21.0762 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8248 | 0.052545 | 1.0945 | 1.0944 | 1.0944 | 1.0944 | 0.97479 | 0.89519 | 20.8641 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8248 | 0.052545 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97479 | 0.89519 | 20.8641 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8248 | 0.052545 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97479 | 0.89519 | 830 | 895.1873 | 0.97479 | 1.0944 | 0.0052 | 20.8641
0.831 | 0.88812 | 0.054955 | 1.0997 | 1.0996 | 1.0996 | 1.0996 | 0.92444 | 21.0889 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8258 | 0.052549 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.9748 | 0.89682 | 20.8768 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8258 | 0.052549 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.9748 | 0.89682 | 20.8768 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8258 | 0.052549 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.9748 | 0.89682 | 831 | 896.823 | 0.9748 | 1.0944 | 0.0052 | 20.8768
0.832 | 0.88916 | 0.054959 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.92611 | 21.1017 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8268 | 0.052554 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97481 | 0.89846 | 20.8895 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8268 | 0.052554 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97481 | 0.89846 | 20.8895 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8268 | 0.052554 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97481 | 0.89846 | 832 | 898.4598 | 0.97481 | 1.0944 | 0.0052 | 20.8895
0.833 | 0.8902 | 0.054962 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.92779 | 21.1144 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8278 | 0.052558 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97482 | 0.9001 | 20.9022 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8278 | 0.052558 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97482 | 0.9001 | 20.9022 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8278 | 0.052558 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97482 | 0.9001 | 833 | 900.0975 | 0.97482 | 1.0944 | 0.0052 | 20.9022
0.834 | 0.89124 | 0.054966 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.92947 | 21.1271 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8288 | 0.052562 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97483 | 0.90174 | 20.9149 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8288 | 0.052562 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97483 | 0.90174 | 20.9149 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8288 | 0.052562 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97483 | 0.90174 | 834 | 901.7362 | 0.97483 | 1.0944 | 0.0052 | 20.9149
0.835 | 0.89228 | 0.054969 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.93115 | 21.1398 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8298 | 0.052566 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97484 | 0.90338 | 20.9276 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8298 | 0.052566 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97484 | 0.90338 | 20.9276 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8298 | 0.052566 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97484 | 0.90338 | 835 | 903.3759 | 0.97484 | 1.0944 | 0.0052 | 20.9276
0.836 | 0.89332 | 0.054972 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.93282 | 21.1525 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8308 | 0.05257 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97486 | 0.90502 | 20.9402 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8308 | 0.05257 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97486 | 0.90502 | 20.9402 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8308 | 0.05257 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97486 | 0.90502 | 836 | 905.0166 | 0.97486 | 1.0944 | 0.0052 | 20.9402
0.837 | 0.89436 | 0.054976 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.93451 | 21.1652 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8318 | 0.052574 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97487 | 0.90666 | 20.9529 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8318 | 0.052574 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97487 | 0.90666 | 20.9529 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8318 | 0.052574 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97487 | 0.90666 | 837 | 906.6583 | 0.97487 | 1.0944 | 0.0052 | 20.9529
0.838 | 0.8954 | 0.054979 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.93619 | 21.1779 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8328 | 0.052578 | 1.0946 | 1.0944 | 1.0944 | 1.0944 | 0.97488 | 0.9083 | 20.9655 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8328 | 0.052578 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97488 | 0.9083 | 20.9655 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8328 | 0.052578 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97488 | 0.9083 | 838 | 908.3009 | 0.97488 | 1.0944 | 0.0052 | 20.9655
0.839 | 0.89644 | 0.054982 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.93787 | 21.1906 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8338 | 0.052582 | 1.0946 | 1.0945 | 1.0944 | 1.0944 | 0.97489 | 0.90994 | 20.9782 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8338 | 0.052582 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97489 | 0.90994 | 20.9782 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8338 | 0.052582 | 1.0944 | 1.0944 | 1.0944 | 1.0944 | 0.97489 | 0.90994 | 839 | 909.9446 | 0.97489 | 1.0944 | 0.0052 | 20.9782
0.84 | 0.89749 | 0.054986 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.93955 | 21.2033 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8348 | 0.052586 | 1.0946 | 1.0945 | 1.0945 | 1.0945 | 0.9749 | 0.91159 | 20.9908 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8348 | 0.052586 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.9749 | 0.91159 | 20.9908 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8348 | 0.052586 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.9749 | 0.91159 | 840 | 911.5893 | 0.9749 | 1.0945 | 0.0052 | 20.9908
0.841 | 0.89853 | 0.054989 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.94124 | 21.2159 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8358 | 0.05259 | 1.0946 | 1.0945 | 1.0945 | 1.0945 | 0.97491 | 0.91323 | 21.0034 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8358 | 0.05259 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97491 | 0.91323 | 21.0034 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8358 | 0.05259 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97491 | 0.91323 | 841 | 913.2349 | 0.97491 | 1.0945 | 0.0052 | 21.0034
0.842 | 0.89957 | 0.054992 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.94292 | 21.2286 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8368 | 0.052594 | 1.0946 | 1.0945 | 1.0945 | 1.0945 | 0.97492 | 0.91488 | 21.016 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8368 | 0.052594 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97492 | 0.91488 | 21.016 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8368 | 0.052594 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97492 | 0.91488 | 842 | 914.8816 | 0.97492 | 1.0945 | 0.0052 | 21.016
0.843 | 0.90061 | 0.054996 | 1.0997 | 1.0997 | 1.0997 | 1.0997 | 0.94461 | 21.2412 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8378 | 0.052597 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97493 | 0.91653 | 21.0286 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8378 | 0.052597 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97493 | 0.91653 | 21.0286 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8378 | 0.052597 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97493 | 0.91653 | 843 | 916.5292 | 0.97493 | 1.0945 | 0.0052 | 21.0286
0.844 | 0.90165 | 0.054999 | 1.0998 | 1.0997 | 1.0997 | 1.0997 | 0.9463 | 21.2539 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8388 | 0.052601 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97494 | 0.91818 | 21.0412 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8388 | 0.052601 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97494 | 0.91818 | 21.0412 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8388 | 0.052601 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97494 | 0.91818 | 844 | 918.1778 | 0.97494 | 1.0945 | 0.0052 | 21.0412
0.845 | 0.90269 | 0.055002 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.94799 | 21.2665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8398 | 0.052605 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97495 | 0.91983 | 21.0538 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8398 | 0.052605 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97495 | 0.91983 | 21.0538 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8398 | 0.052605 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97495 | 0.91983 | 845 | 919.8275 | 0.97495 | 1.0945 | 0.0052 | 21.0538
0.846 | 0.90373 | 0.055006 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.94968 | 21.2791 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8408 | 0.052609 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97496 | 0.92148 | 21.0664 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8408 | 0.052609 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97496 | 0.92148 | 21.0664 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8408 | 0.052609 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97496 | 0.92148 | 846 | 921.4781 | 0.97496 | 1.0945 | 0.0052 | 21.0664
0.847 | 0.90477 | 0.055009 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.95137 | 21.2918 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8418 | 0.052613 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97497 | 0.92313 | 21.079 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8418 | 0.052613 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97497 | 0.92313 | 21.079 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8418 | 0.052613 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97497 | 0.92313 | 847 | 923.1296 | 0.97497 | 1.0945 | 0.0052 | 21.079
0.848 | 0.90582 | 0.055012 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.95306 | 21.3044 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8428 | 0.052617 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97499 | 0.92478 | 21.0916 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8428 | 0.052617 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97499 | 0.92478 | 21.0916 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8428 | 0.052617 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97499 | 0.92478 | 848 | 924.7822 | 0.97499 | 1.0945 | 0.0052 | 21.0916
0.849 | 0.90686 | 0.055016 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.95475 | 21.317 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8438 | 0.052621 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.975 | 0.92644 | 21.1041 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8438 | 0.052621 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.975 | 0.92644 | 21.1041 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8438 | 0.052621 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.975 | 0.92644 | 849 | 926.4358 | 0.975 | 1.0945 | 0.0052 | 21.1041
0.85 | 0.9079 | 0.055019 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.95644 | 21.3296 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8448 | 0.052625 | 1.0947 | 1.0945 | 1.0945 | 1.0945 | 0.97501 | 0.92809 | 21.1167 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8448 | 0.052625 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97501 | 0.92809 | 21.1167 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8448 | 0.052625 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97501 | 0.92809 | 850 | 928.0903 | 0.97501 | 1.0945 | 0.0052 | 21.1167
0.851 | 0.90894 | 0.055022 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.95814 | 21.3422 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8458 | 0.052629 | 1.0947 | 1.0946 | 1.0945 | 1.0945 | 0.97502 | 0.92975 | 21.1292 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8458 | 0.052629 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97502 | 0.92975 | 21.1292 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8458 | 0.052629 | 1.0945 | 1.0945 | 1.0945 | 1.0945 | 0.97502 | 0.92975 | 851 | 929.7459 | 0.97502 | 1.0945 | 0.0052 | 21.1292
0.852 | 0.90998 | 0.055025 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.95983 | 21.3547 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8468 | 0.052633 | 1.0947 | 1.0946 | 1.0946 | 1.0946 | 0.97503 | 0.9314 | 21.1418 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8468 | 0.052633 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97503 | 0.9314 | 21.1418 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8468 | 0.052633 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97503 | 0.9314 | 852 | 931.4024 | 0.97503 | 1.0946 | 0.0052 | 21.1418
0.853 | 0.91102 | 0.055029 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.96153 | 21.3673 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8478 | 0.052637 | 1.0947 | 1.0946 | 1.0946 | 1.0946 | 0.97504 | 0.93306 | 21.1543 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8478 | 0.052637 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97504 | 0.93306 | 21.1543 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8478 | 0.052637 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97504 | 0.93306 | 853 | 933.0599 | 0.97504 | 1.0946 | 0.0052 | 21.1543
0.854 | 0.91206 | 0.055032 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.96323 | 21.3799 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8488 | 0.05264 | 1.0947 | 1.0946 | 1.0946 | 1.0946 | 0.97505 | 0.93472 | 21.1668 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8488 | 0.05264 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97505 | 0.93472 | 21.1668 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8488 | 0.05264 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97505 | 0.93472 | 854 | 934.7184 | 0.97505 | 1.0946 | 0.0052 | 21.1668
0.855 | 0.9131 | 0.055035 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.96493 | 21.3924 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8498 | 0.052644 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97506 | 0.93638 | 21.1793 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8498 | 0.052644 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97506 | 0.93638 | 21.1793 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8498 | 0.052644 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97506 | 0.93638 | 855 | 936.3778 | 0.97506 | 1.0946 | 0.0052 | 21.1793
0.856 | 0.91414 | 0.055038 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.96663 | 21.405 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8508 | 0.052648 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97507 | 0.93804 | 21.1919 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8508 | 0.052648 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97507 | 0.93804 | 21.1919 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8508 | 0.052648 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97507 | 0.93804 | 856 | 938.0383 | 0.97507 | 1.0946 | 0.0052 | 21.1919
0.857 | 0.91519 | 0.055042 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.96833 | 21.4175 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8518 | 0.052652 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97508 | 0.9397 | 21.2044 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8518 | 0.052652 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97508 | 0.9397 | 21.2044 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8518 | 0.052652 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97508 | 0.9397 | 857 | 939.6997 | 0.97508 | 1.0946 | 0.0052 | 21.2044
0.858 | 0.91623 | 0.055045 | 1.0998 | 1.0998 | 1.0998 | 1.0998 | 0.97003 | 21.4301 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8528 | 0.052656 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97509 | 0.94136 | 21.2169 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8528 | 0.052656 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97509 | 0.94136 | 21.2169 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8528 | 0.052656 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97509 | 0.94136 | 858 | 941.3621 | 0.97509 | 1.0946 | 0.0052 | 21.2169
0.859 | 0.91727 | 0.055048 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.97173 | 21.4426 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8538 | 0.05266 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.9751 | 0.94303 | 21.2294 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8538 | 0.05266 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.9751 | 0.94303 | 21.2294 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8538 | 0.05266 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.9751 | 0.94303 | 859 | 943.0255 | 0.9751 | 1.0946 | 0.0052 | 21.2294
0.86 | 0.91831 | 0.055051 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.97344 | 21.4551 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8548 | 0.052663 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97511 | 0.94469 | 21.2418 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8548 | 0.052663 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97511 | 0.94469 | 21.2418 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8548 | 0.052663 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97511 | 0.94469 | 860 | 944.6899 | 0.97511 | 1.0946 | 0.0052 | 21.2418
0.861 | 0.91935 | 0.055054 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.97514 | 21.4677 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8558 | 0.052667 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97512 | 0.94636 | 21.2543 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8558 | 0.052667 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97512 | 0.94636 | 21.2543 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8558 | 0.052667 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97512 | 0.94636 | 861 | 946.3552 | 0.97512 | 1.0946 | 0.0052 | 21.2543
0.862 | 0.92039 | 0.055058 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.97685 | 21.4802 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8568 | 0.052671 | 1.0948 | 1.0946 | 1.0946 | 1.0946 | 0.97513 | 0.94802 | 21.2668 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8568 | 0.052671 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97513 | 0.94802 | 21.2668 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8568 | 0.052671 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97513 | 0.94802 | 862 | 948.0215 | 0.97513 | 1.0946 | 0.0052 | 21.2668
0.863 | 0.92143 | 0.055061 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.97855 | 21.4927 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8578 | 0.052675 | 1.0948 | 1.0947 | 1.0946 | 1.0946 | 0.97514 | 0.94969 | 21.2792 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8578 | 0.052675 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97514 | 0.94969 | 21.2792 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8578 | 0.052675 | 1.0946 | 1.0946 | 1.0946 | 1.0946 | 0.97514 | 0.94969 | 863 | 949.6888 | 0.97514 | 1.0946 | 0.0052 | 21.2792
0.864 | 0.92247 | 0.055064 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.98026 | 21.5052 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8588 | 0.052678 | 1.0948 | 1.0947 | 1.0947 | 1.0947 | 0.97515 | 0.95136 | 21.2917 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8588 | 0.052678 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97515 | 0.95136 | 21.2917 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8588 | 0.052678 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97515 | 0.95136 | 864 | 951.3571 | 0.97515 | 1.0947 | 0.0052 | 21.2917
0.865 | 0.92351 | 0.055067 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.98197 | 21.5176 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8598 | 0.052682 | 1.0948 | 1.0947 | 1.0947 | 1.0947 | 0.97516 | 0.95303 | 21.3041 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8598 | 0.052682 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97516 | 0.95303 | 21.3041 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8598 | 0.052682 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97516 | 0.95303 | 865 | 953.0264 | 0.97516 | 1.0947 | 0.0052 | 21.3041
0.866 | 0.92456 | 0.05507 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.98368 | 21.5301 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8608 | 0.052686 | 1.0948 | 1.0947 | 1.0947 | 1.0947 | 0.97517 | 0.9547 | 21.3166 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8608 | 0.052686 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97517 | 0.9547 | 21.3166 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8608 | 0.052686 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97517 | 0.9547 | 866 | 954.6966 | 0.97517 | 1.0947 | 0.0052 | 21.3166
0.867 | 0.9256 | 0.055073 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.98539 | 21.5426 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8618 | 0.05269 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97518 | 0.95637 | 21.329 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8618 | 0.05269 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97518 | 0.95637 | 21.329 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8618 | 0.05269 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97518 | 0.95637 | 867 | 956.3678 | 0.97518 | 1.0947 | 0.0052 | 21.329
0.868 | 0.92664 | 0.055076 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.9871 | 21.5551 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8628 | 0.052693 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97519 | 0.95804 | 21.3414 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8628 | 0.052693 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97519 | 0.95804 | 21.3414 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8628 | 0.052693 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97519 | 0.95804 | 868 | 958.04 | 0.97519 | 1.0947 | 0.0052 | 21.3414
0.869 | 0.92768 | 0.05508 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.98881 | 21.5675 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8638 | 0.052697 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.9752 | 0.95971 | 21.3538 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8638 | 0.052697 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.9752 | 0.95971 | 21.3538 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8638 | 0.052697 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.9752 | 0.95971 | 869 | 959.7132 | 0.9752 | 1.0947 | 0.0052 | 21.3538
0.87 | 0.92872 | 0.055083 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.99053 | 21.58 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8648 | 0.052701 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97521 | 0.96139 | 21.3663 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8648 | 0.052701 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97521 | 0.96139 | 21.3663 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8648 | 0.052701 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97521 | 0.96139 | 870 | 961.3873 | 0.97521 | 1.0947 | 0.0052 | 21.3663
0.871 | 0.92976 | 0.055086 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.99224 | 21.5924 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8658 | 0.052705 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97522 | 0.96306 | 21.3787 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8658 | 0.052705 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97522 | 0.96306 | 21.3787 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8658 | 0.052705 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97522 | 0.96306 | 871 | 963.0624 | 0.97522 | 1.0947 | 0.0052 | 21.3787
0.872 | 0.9308 | 0.055089 | 1.0999 | 1.0999 | 1.0999 | 1.0999 | 0.99396 | 21.6049 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8668 | 0.052708 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97523 | 0.96474 | 21.391 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8668 | 0.052708 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97523 | 0.96474 | 21.391 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8668 | 0.052708 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97523 | 0.96474 | 872 | 964.7385 | 0.97523 | 1.0947 | 0.0052 | 21.391
0.873 | 0.93184 | 0.055092 | 1.1 | 1.0999 | 1.0999 | 1.0999 | 0.99567 | 21.6173 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8678 | 0.052712 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97524 | 0.96642 | 21.4034 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8678 | 0.052712 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97524 | 0.96642 | 21.4034 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8678 | 0.052712 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97524 | 0.96642 | 873 | 966.4155 | 0.97524 | 1.0947 | 0.0052 | 21.4034
0.874 | 0.93289 | 0.055095 | 1.1 | 1.1 | 1.1 | 1.1 | 0.99739 | 21.6297 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8688 | 0.052716 | 1.0949 | 1.0947 | 1.0947 | 1.0947 | 0.97525 | 0.96809 | 21.4158 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8688 | 0.052716 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97525 | 0.96809 | 21.4158 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8688 | 0.052716 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97525 | 0.96809 | 874 | 968.0935 | 0.97525 | 1.0947 | 0.0052 | 21.4158
0.875 | 0.93393 | 0.055098 | 1.1 | 1.1 | 1.1 | 1.1 | 0.99911 | 21.6421 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8698 | 0.052719 | 1.0949 | 1.0948 | 1.0947 | 1.0947 | 0.97526 | 0.96977 | 21.4282 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8698 | 0.052719 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97526 | 0.96977 | 21.4282 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8698 | 0.052719 | 1.0947 | 1.0947 | 1.0947 | 1.0947 | 0.97526 | 0.96977 | 875 | 969.7725 | 0.97526 | 1.0947 | 0.0052 | 21.4282
0.876 | 0.93497 | 0.055101 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0008 | 21.6545 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8708 | 0.052723 | 1.0949 | 1.0948 | 1.0948 | 1.0948 | 0.97527 | 0.97145 | 21.4406 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8708 | 0.052723 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97527 | 0.97145 | 21.4406 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8708 | 0.052723 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97527 | 0.97145 | 876 | 971.4525 | 0.97527 | 1.0948 | 0.0052 | 21.4406
0.877 | 0.93601 | 0.055104 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0025 | 21.6669 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8718 | 0.052727 | 1.0949 | 1.0948 | 1.0948 | 1.0948 | 0.97528 | 0.97313 | 21.4529 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8718 | 0.052727 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97528 | 0.97313 | 21.4529 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8718 | 0.052727 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97528 | 0.97313 | 877 | 973.1334 | 0.97528 | 1.0948 | 0.0052 | 21.4529
0.878 | 0.93705 | 0.055107 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0043 | 21.6793 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8728 | 0.05273 | 1.0949 | 1.0948 | 1.0948 | 1.0948 | 0.97529 | 0.97482 | 21.4653 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8728 | 0.05273 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97529 | 0.97482 | 21.4653 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8728 | 0.05273 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97529 | 0.97482 | 878 | 974.8153 | 0.97529 | 1.0948 | 0.0052 | 21.4653
0.879 | 0.93809 | 0.055111 | 1.1 | 1.1 | 1.1 | 1.1 | 1.006 | 21.6917 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8738 | 0.052734 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.9753 | 0.9765 | 21.4776 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8738 | 0.052734 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.9753 | 0.9765 | 21.4776 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8738 | 0.052734 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.9753 | 0.9765 | 879 | 976.4982 | 0.9753 | 1.0948 | 0.0052 | 21.4776
0.88 | 0.93913 | 0.055114 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0077 | 21.7041 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8748 | 0.052738 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97531 | 0.97818 | 21.49 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8748 | 0.052738 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97531 | 0.97818 | 21.49 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8748 | 0.052738 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97531 | 0.97818 | 880 | 978.182 | 0.97531 | 1.0948 | 0.0052 | 21.49
0.881 | 0.94017 | 0.055117 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0094 | 21.7165 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8758 | 0.052741 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97532 | 0.97987 | 21.5023 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8758 | 0.052741 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97532 | 0.97987 | 21.5023 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8758 | 0.052741 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97532 | 0.97987 | 881 | 979.8668 | 0.97532 | 1.0948 | 0.0052 | 21.5023
0.882 | 0.94121 | 0.05512 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0112 | 21.7288 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8768 | 0.052745 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97533 | 0.98155 | 21.5146 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8768 | 0.052745 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97533 | 0.98155 | 21.5146 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8768 | 0.052745 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97533 | 0.98155 | 882 | 981.5526 | 0.97533 | 1.0948 | 0.0052 | 21.5146
0.883 | 0.94226 | 0.055123 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0129 | 21.7412 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8778 | 0.052749 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97534 | 0.98324 | 21.5269 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8778 | 0.052749 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97534 | 0.98324 | 21.5269 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8778 | 0.052749 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97534 | 0.98324 | 883 | 983.2394 | 0.97534 | 1.0948 | 0.0052 | 21.5269
0.884 | 0.9433 | 0.055126 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0146 | 21.7535 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8788 | 0.052752 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97535 | 0.98493 | 21.5392 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8788 | 0.052752 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97535 | 0.98493 | 21.5392 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8788 | 0.052752 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97535 | 0.98493 | 884 | 984.9271 | 0.97535 | 1.0948 | 0.0052 | 21.5392
0.885 | 0.94434 | 0.055129 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0163 | 21.7659 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8798 | 0.052756 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97536 | 0.98662 | 21.5515 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8798 | 0.052756 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97536 | 0.98662 | 21.5515 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8798 | 0.052756 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97536 | 0.98662 | 885 | 986.6157 | 0.97536 | 1.0948 | 0.0052 | 21.5515
0.886 | 0.94538 | 0.055132 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0181 | 21.7782 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8808 | 0.052759 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97537 | 0.98831 | 21.5638 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8808 | 0.052759 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97537 | 0.98831 | 21.5638 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8808 | 0.052759 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97537 | 0.98831 | 886 | 988.3054 | 0.97537 | 1.0948 | 0.0052 | 21.5638
0.887 | 0.94642 | 0.055135 | 1.1 | 1.1 | 1.1 | 1.1 | 1.0198 | 21.7906 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8818 | 0.052763 | 1.095 | 1.0948 | 1.0948 | 1.0948 | 0.97538 | 0.99 | 21.5761 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8818 | 0.052763 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97538 | 0.99 | 21.5761 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8818 | 0.052763 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97538 | 0.99 | 887 | 989.996 | 0.97538 | 1.0948 | 0.0052 | 21.5761
0.888 | 0.94746 | 0.055138 | 1.1 | 1.1 | 1.1001 | 1.1001 | 1.0215 | 21.8029 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8828 | 0.052767 | 1.095 | 1.0949 | 1.0948 | 1.0948 | 0.97539 | 0.99169 | 21.5884 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8828 | 0.052767 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97539 | 0.99169 | 21.5884 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8828 | 0.052767 | 1.0948 | 1.0948 | 1.0948 | 1.0948 | 0.97539 | 0.99169 | 888 | 991.6875 | 0.97539 | 1.0948 | 0.0052 | 21.5884
0.889 | 0.9485 | 0.055141 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0233 | 21.8152 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8838 | 0.05277 | 1.095 | 1.0949 | 1.0949 | 1.0949 | 0.9754 | 0.99338 | 21.6007 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8838 | 0.05277 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.9754 | 0.99338 | 21.6007 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8838 | 0.05277 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.9754 | 0.99338 | 889 | 993.3801 | 0.9754 | 1.0949 | 0.0052 | 21.6007
0.89 | 0.94954 | 0.055144 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.025 | 21.8275 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8848 | 0.052774 | 1.095 | 1.0949 | 1.0949 | 1.0949 | 0.97541 | 0.99507 | 21.6129 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8848 | 0.052774 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97541 | 0.99507 | 21.6129 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8848 | 0.052774 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97541 | 0.99507 | 890 | 995.0736 | 0.97541 | 1.0949 | 0.0052 | 21.6129
0.891 | 0.95059 | 0.055147 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0267 | 21.8398 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8858 | 0.052777 | 1.095 | 1.0949 | 1.0949 | 1.0949 | 0.97542 | 0.99677 | 21.6252 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8858 | 0.052777 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97542 | 0.99677 | 21.6252 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8858 | 0.052777 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97542 | 0.99677 | 891 | 996.768 | 0.97542 | 1.0949 | 0.0052 | 21.6252
0.892 | 0.95163 | 0.05515 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0285 | 21.8521 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8868 | 0.052781 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97543 | 0.99846 | 21.6375 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8868 | 0.052781 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97543 | 0.99846 | 21.6375 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8868 | 0.052781 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97543 | 0.99846 | 892 | 998.4634 | 0.97543 | 1.0949 | 0.0052 | 21.6375
0.893 | 0.95267 | 0.055153 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0302 | 21.8644 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8878 | 0.052784 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97544 | 1.0002 | 21.6497 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8878 | 0.052784 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97544 | 1.0002 | 21.6497 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8878 | 0.052784 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97544 | 1.0002 | 893 | 1000.1598 | 0.97544 | 1.0949 | 0.0052 | 21.6497
0.894 | 0.95371 | 0.055156 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0319 | 21.8767 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8888 | 0.052788 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97545 | 1.0019 | 21.6619 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8888 | 0.052788 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97545 | 1.0019 | 21.6619 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8888 | 0.052788 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97545 | 1.0019 | 894 | 1001.8571 | 0.97545 | 1.0949 | 0.0052 | 21.6619
0.895 | 0.95475 | 0.055159 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0337 | 21.889 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8898 | 0.052791 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97546 | 1.0036 | 21.6742 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8898 | 0.052791 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97546 | 1.0036 | 21.6742 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8898 | 0.052791 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97546 | 1.0036 | 895 | 1003.5554 | 0.97546 | 1.0949 | 0.0052 | 21.6742
0.896 | 0.95579 | 0.055162 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0354 | 21.9012 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8908 | 0.052795 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97547 | 1.0053 | 21.6864 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8908 | 0.052795 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97547 | 1.0053 | 21.6864 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8908 | 0.052795 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97547 | 1.0053 | 896 | 1005.2547 | 0.97547 | 1.0949 | 0.0052 | 21.6864
0.897 | 0.95683 | 0.055165 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0372 | 21.9135 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8918 | 0.052798 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97548 | 1.007 | 21.6986 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8918 | 0.052798 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97548 | 1.007 | 21.6986 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8918 | 0.052798 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97548 | 1.007 | 897 | 1006.9549 | 0.97548 | 1.0949 | 0.0052 | 21.6986
0.898 | 0.95787 | 0.055168 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0389 | 21.9257 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8928 | 0.052802 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97549 | 1.0087 | 21.7108 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8928 | 0.052802 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97549 | 1.0087 | 21.7108 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8928 | 0.052802 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97549 | 1.0087 | 898 | 1008.6561 | 0.97549 | 1.0949 | 0.0052 | 21.7108
0.899 | 0.95891 | 0.05517 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0406 | 21.938 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8938 | 0.052805 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.9755 | 1.0104 | 21.723 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8938 | 0.052805 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.9755 | 1.0104 | 21.723 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8938 | 0.052805 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.9755 | 1.0104 | 899 | 1010.3582 | 0.9755 | 1.0949 | 0.0052 | 21.723
0.9 | 0.95996 | 0.055173 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0424 | 21.9502 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8948 | 0.052809 | 1.0951 | 1.0949 | 1.0949 | 1.0949 | 0.97551 | 1.0121 | 21.7352 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8948 | 0.052809 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97551 | 1.0121 | 21.7352 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8948 | 0.052809 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97551 | 1.0121 | 900 | 1012.0613 | 0.97551 | 1.0949 | 0.0052 | 21.7352
0.901 | 0.961 | 0.055176 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0441 | 21.9625 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8958 | 0.052812 | 1.0951 | 1.095 | 1.0949 | 1.0949 | 0.97552 | 1.0138 | 21.7474 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8958 | 0.052812 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97552 | 1.0138 | 21.7474 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8958 | 0.052812 | 1.0949 | 1.0949 | 1.0949 | 1.0949 | 0.97552 | 1.0138 | 901 | 1013.7653 | 0.97552 | 1.0949 | 0.0052 | 21.7474
0.902 | 0.96204 | 0.055179 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0459 | 21.9747 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8968 | 0.052816 | 1.0951 | 1.095 | 1.095 | 1.095 | 0.97553 | 1.0155 | 21.7596 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8968 | 0.052816 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97553 | 1.0155 | 21.7596 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8968 | 0.052816 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97553 | 1.0155 | 902 | 1015.4703 | 0.97553 | 1.095 | 0.0052 | 21.7596
0.903 | 0.96308 | 0.055182 | 1.1001 | 1.1001 | 1.1001 | 1.1001 | 1.0476 | 21.9869 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8978 | 0.052819 | 1.0951 | 1.095 | 1.095 | 1.095 | 0.97553 | 1.0172 | 21.7718 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8978 | 0.052819 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97553 | 1.0172 | 21.7718 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8978 | 0.052819 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97553 | 1.0172 | 903 | 1017.1763 | 0.97553 | 1.095 | 0.0052 | 21.7718
0.904 | 0.96412 | 0.055185 | 1.1001 | 1.1002 | 1.1002 | 1.1002 | 1.0494 | 21.9991 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8988 | 0.052823 | 1.0951 | 1.095 | 1.095 | 1.095 | 0.97554 | 1.0189 | 21.784 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8988 | 0.052823 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97554 | 1.0189 | 21.784 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8988 | 0.052823 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97554 | 1.0189 | 904 | 1018.8832 | 0.97554 | 1.095 | 0.0052 | 21.784
0.905 | 0.96516 | 0.055188 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0511 | 22.0113 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8998 | 0.052826 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97555 | 1.0206 | 21.7961 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8998 | 0.052826 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97555 | 1.0206 | 21.7961 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.8998 | 0.052826 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97555 | 1.0206 | 905 | 1020.5911 | 0.97555 | 1.095 | 0.0052 | 21.7961
0.906 | 0.9662 | 0.055191 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0529 | 22.0235 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9008 | 0.05283 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97556 | 1.0223 | 21.8083 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9008 | 0.05283 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97556 | 1.0223 | 21.8083 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9008 | 0.05283 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97556 | 1.0223 | 906 | 1022.2999 | 0.97556 | 1.095 | 0.0052 | 21.8083
0.907 | 0.96724 | 0.055194 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0546 | 22.0357 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9018 | 0.052833 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97557 | 1.024 | 21.8204 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9018 | 0.052833 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97557 | 1.024 | 21.8204 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9018 | 0.052833 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97557 | 1.024 | 907 | 1024.0097 | 0.97557 | 1.095 | 0.0052 | 21.8204
0.908 | 0.96829 | 0.055197 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0564 | 22.0479 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9028 | 0.052836 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97558 | 1.0257 | 21.8326 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9028 | 0.052836 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97558 | 1.0257 | 21.8326 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9028 | 0.052836 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97558 | 1.0257 | 908 | 1025.7204 | 0.97558 | 1.095 | 0.0052 | 21.8326
0.909 | 0.96933 | 0.055199 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0581 | 22.0601 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9038 | 0.05284 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97559 | 1.0274 | 21.8447 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9038 | 0.05284 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97559 | 1.0274 | 21.8447 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9038 | 0.05284 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97559 | 1.0274 | 909 | 1027.4321 | 0.97559 | 1.095 | 0.0052 | 21.8447
0.91 | 0.97037 | 0.055202 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0599 | 22.0723 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9048 | 0.052843 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.9756 | 1.0291 | 21.8569 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9048 | 0.052843 | 1.095 | 1.095 | 1.095 | 1.095 | 0.9756 | 1.0291 | 21.8569 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9048 | 0.052843 | 1.095 | 1.095 | 1.095 | 1.095 | 0.9756 | 1.0291 | 910 | 1029.1447 | 0.9756 | 1.095 | 0.0052 | 21.8569
0.911 | 0.97141 | 0.055205 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0616 | 22.0844 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9058 | 0.052847 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97561 | 1.0309 | 21.869 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9058 | 0.052847 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97561 | 1.0309 | 21.869 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9058 | 0.052847 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97561 | 1.0309 | 911 | 1030.8583 | 0.97561 | 1.095 | 0.0052 | 21.869
0.912 | 0.97245 | 0.055208 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0634 | 22.0966 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9068 | 0.05285 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97562 | 1.0326 | 21.8811 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9068 | 0.05285 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97562 | 1.0326 | 21.8811 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9068 | 0.05285 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97562 | 1.0326 | 912 | 1032.5728 | 0.97562 | 1.095 | 0.0052 | 21.8811
0.913 | 0.97349 | 0.055211 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0651 | 22.1087 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9078 | 0.052853 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97563 | 1.0343 | 21.8932 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9078 | 0.052853 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97563 | 1.0343 | 21.8932 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9078 | 0.052853 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97563 | 1.0343 | 913 | 1034.2883 | 0.97563 | 1.095 | 0.0052 | 21.8932
0.914 | 0.97453 | 0.055214 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0669 | 22.1209 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9088 | 0.052857 | 1.0952 | 1.095 | 1.095 | 1.095 | 0.97564 | 1.036 | 21.9053 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9088 | 0.052857 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97564 | 1.036 | 21.9053 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9088 | 0.052857 | 1.095 | 1.095 | 1.095 | 1.095 | 0.97564 | 1.036 | 914 | 1036.0047 | 0.97564 | 1.095 | 0.0052 | 21.9053
0.915 | 0.97557 | 0.055217 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0687 | 22.133 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9098 | 0.05286 | 1.0952 | 1.0951 | 1.0951 | 1.0951 | 0.97565 | 1.0377 | 21.9174 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9098 | 0.05286 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97565 | 1.0377 | 21.9174 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9098 | 0.05286 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97565 | 1.0377 | 915 | 1037.7221 | 0.97565 | 1.0951 | 0.0052 | 21.9174
0.916 | 0.97661 | 0.055219 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0704 | 22.1452 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9108 | 0.052864 | 1.0952 | 1.0951 | 1.0951 | 1.0951 | 0.97566 | 1.0394 | 21.9295 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9108 | 0.052864 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97566 | 1.0394 | 21.9295 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9108 | 0.052864 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97566 | 1.0394 | 916 | 1039.4405 | 0.97566 | 1.0951 | 0.0052 | 21.9295
0.917 | 0.97766 | 0.055222 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0722 | 22.1573 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9118 | 0.052867 | 1.0952 | 1.0951 | 1.0951 | 1.0951 | 0.97566 | 1.0412 | 21.9416 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9118 | 0.052867 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97566 | 1.0412 | 21.9416 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9118 | 0.052867 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97566 | 1.0412 | 917 | 1041.1597 | 0.97566 | 1.0951 | 0.0052 | 21.9416
0.918 | 0.9787 | 0.055225 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0739 | 22.1694 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9128 | 0.05287 | 1.0952 | 1.0951 | 1.0951 | 1.0951 | 0.97567 | 1.0429 | 21.9537 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9128 | 0.05287 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97567 | 1.0429 | 21.9537 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9128 | 0.05287 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97567 | 1.0429 | 918 | 1042.88 | 0.97567 | 1.0951 | 0.0052 | 21.9537
0.919 | 0.97974 | 0.055228 | 1.1002 | 1.1002 | 1.1002 | 1.1002 | 1.0757 | 22.1815 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9138 | 0.052874 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97568 | 1.0446 | 21.9657 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9138 | 0.052874 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97568 | 1.0446 | 21.9657 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9138 | 0.052874 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97568 | 1.0446 | 919 | 1044.6011 | 0.97568 | 1.0951 | 0.0052 | 21.9657
0.92 | 0.98078 | 0.055231 | 1.1002 | 1.1003 | 1.1003 | 1.1003 | 1.0775 | 22.1936 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9148 | 0.052877 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97569 | 1.0463 | 21.9778 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9148 | 0.052877 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97569 | 1.0463 | 21.9778 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9148 | 0.052877 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97569 | 1.0463 | 920 | 1046.3233 | 0.97569 | 1.0951 | 0.0052 | 21.9778
0.921 | 0.98182 | 0.055233 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0792 | 22.2057 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9158 | 0.05288 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.9757 | 1.048 | 21.9899 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9158 | 0.05288 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.9757 | 1.048 | 21.9899 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9158 | 0.05288 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.9757 | 1.048 | 921 | 1048.0463 | 0.9757 | 1.0951 | 0.0052 | 21.9899
0.922 | 0.98286 | 0.055236 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.081 | 22.2178 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9168 | 0.052884 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97571 | 1.0498 | 22.0019 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9168 | 0.052884 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97571 | 1.0498 | 22.0019 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9168 | 0.052884 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97571 | 1.0498 | 922 | 1049.7703 | 0.97571 | 1.0951 | 0.0052 | 22.0019
0.923 | 0.9839 | 0.055239 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0827 | 22.2299 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9178 | 0.052887 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97572 | 1.0515 | 22.014 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9178 | 0.052887 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97572 | 1.0515 | 22.014 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9178 | 0.052887 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97572 | 1.0515 | 923 | 1051.4953 | 0.97572 | 1.0951 | 0.0052 | 22.014
0.924 | 0.98494 | 0.055242 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0845 | 22.242 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9188 | 0.05289 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97573 | 1.0532 | 22.026 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9188 | 0.05289 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97573 | 1.0532 | 22.026 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9188 | 0.05289 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97573 | 1.0532 | 924 | 1053.2212 | 0.97573 | 1.0951 | 0.0052 | 22.026
0.925 | 0.98598 | 0.055245 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0863 | 22.2541 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9198 | 0.052894 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97574 | 1.0549 | 22.038 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9198 | 0.052894 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97574 | 1.0549 | 22.038 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9198 | 0.052894 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97574 | 1.0549 | 925 | 1054.9481 | 0.97574 | 1.0951 | 0.0052 | 22.038
0.926 | 0.98703 | 0.055247 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.088 | 22.2661 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9208 | 0.052897 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97575 | 1.0567 | 22.05 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9208 | 0.052897 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97575 | 1.0567 | 22.05 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9208 | 0.052897 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97575 | 1.0567 | 926 | 1056.6758 | 0.97575 | 1.0951 | 0.0052 | 22.05
0.927 | 0.98807 | 0.05525 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0898 | 22.2782 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9218 | 0.0529 | 1.0953 | 1.0951 | 1.0951 | 1.0951 | 0.97575 | 1.0584 | 22.0621 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9218 | 0.0529 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97575 | 1.0584 | 22.0621 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9218 | 0.0529 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97575 | 1.0584 | 927 | 1058.4046 | 0.97575 | 1.0951 | 0.0052 | 22.0621
0.928 | 0.98911 | 0.055253 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0916 | 22.2903 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9228 | 0.052904 | 1.0953 | 1.0952 | 1.0951 | 1.0951 | 0.97576 | 1.0601 | 22.0741 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9228 | 0.052904 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97576 | 1.0601 | 22.0741 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9228 | 0.052904 | 1.0951 | 1.0951 | 1.0951 | 1.0951 | 0.97576 | 1.0601 | 928 | 1060.1343 | 0.97576 | 1.0951 | 0.0052 | 22.0741
0.929 | 0.99015 | 0.055256 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0934 | 22.3023 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9238 | 0.052907 | 1.0953 | 1.0952 | 1.0952 | 1.0952 | 0.97577 | 1.0619 | 22.0861 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9238 | 0.052907 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97577 | 1.0619 | 22.0861 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9238 | 0.052907 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97577 | 1.0619 | 929 | 1061.8649 | 0.97577 | 1.0952 | 0.0052 | 22.0861
0.93 | 0.99119 | 0.055258 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0951 | 22.3143 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9248 | 0.05291 | 1.0953 | 1.0952 | 1.0952 | 1.0952 | 0.97578 | 1.0636 | 22.0981 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9248 | 0.05291 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97578 | 1.0636 | 22.0981 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9248 | 0.05291 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97578 | 1.0636 | 930 | 1063.5964 | 0.97578 | 1.0952 | 0.0052 | 22.0981
0.931 | 0.99223 | 0.055261 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0969 | 22.3264 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9258 | 0.052913 | 1.0953 | 1.0952 | 1.0952 | 1.0952 | 0.97579 | 1.0653 | 22.1101 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9258 | 0.052913 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97579 | 1.0653 | 22.1101 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9258 | 0.052913 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97579 | 1.0653 | 931 | 1065.3289 | 0.97579 | 1.0952 | 0.0052 | 22.1101
0.932 | 0.99327 | 0.055264 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.0987 | 22.3384 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9268 | 0.052917 | 1.0953 | 1.0952 | 1.0952 | 1.0952 | 0.9758 | 1.0671 | 22.1221 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9268 | 0.052917 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.9758 | 1.0671 | 22.1221 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9268 | 0.052917 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.9758 | 1.0671 | 932 | 1067.0624 | 0.9758 | 1.0952 | 0.0052 | 22.1221
0.933 | 0.99431 | 0.055267 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.1005 | 22.3504 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9278 | 0.05292 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97581 | 1.0688 | 22.134 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9278 | 0.05292 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97581 | 1.0688 | 22.134 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9278 | 0.05292 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97581 | 1.0688 | 933 | 1068.7968 | 0.97581 | 1.0952 | 0.0052 | 22.134
0.934 | 0.99536 | 0.055269 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.1022 | 22.3624 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9288 | 0.052923 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97582 | 1.0705 | 22.146 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9288 | 0.052923 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97582 | 1.0705 | 22.146 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9288 | 0.052923 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97582 | 1.0705 | 934 | 1070.5321 | 0.97582 | 1.0952 | 0.0052 | 22.146
0.935 | 0.9964 | 0.055272 | 1.1003 | 1.1003 | 1.1003 | 1.1003 | 1.104 | 22.3744 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9298 | 0.052926 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97582 | 1.0723 | 22.158 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9298 | 0.052926 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97582 | 1.0723 | 22.158 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9298 | 0.052926 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97582 | 1.0723 | 935 | 1072.2683 | 0.97582 | 1.0952 | 0.0052 | 22.158
0.936 | 0.99744 | 0.055275 | 1.1003 | 1.1004 | 1.1004 | 1.1004 | 1.1058 | 22.3865 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9308 | 0.05293 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97583 | 1.074 | 22.1699 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9308 | 0.05293 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97583 | 1.074 | 22.1699 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9308 | 0.05293 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97583 | 1.074 | 936 | 1074.0055 | 0.97583 | 1.0952 | 0.0052 | 22.1699
0.937 | 0.99848 | 0.055278 | 1.1003 | 1.1004 | 1.1004 | 1.1004 | 1.1076 | 22.3984 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9318 | 0.052933 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97584 | 1.0757 | 22.1819 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9318 | 0.052933 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97584 | 1.0757 | 22.1819 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9318 | 0.052933 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97584 | 1.0757 | 937 | 1075.7437 | 0.97584 | 1.0952 | 0.0052 | 22.1819
0.938 | 0.99952 | 0.05528 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1093 | 22.4104 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9328 | 0.052936 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97585 | 1.0775 | 22.1938 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9328 | 0.052936 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97585 | 1.0775 | 22.1938 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9328 | 0.052936 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97585 | 1.0775 | 938 | 1077.4827 | 0.97585 | 1.0952 | 0.0052 | 22.1938
0.939 | 1.0006 | 0.055283 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1111 | 22.4224 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9338 | 0.052939 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97586 | 1.0792 | 22.2058 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9338 | 0.052939 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97586 | 1.0792 | 22.2058 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9338 | 0.052939 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97586 | 1.0792 | 939 | 1079.2228 | 0.97586 | 1.0952 | 0.0052 | 22.2058
0.94 | 1.0016 | 0.055286 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1129 | 22.4344 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9348 | 0.052942 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97587 | 1.081 | 22.2177 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9348 | 0.052942 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97587 | 1.081 | 22.2177 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9348 | 0.052942 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97587 | 1.081 | 940 | 1080.9637 | 0.97587 | 1.0952 | 0.0052 | 22.2177
0.941 | 1.0026 | 0.055288 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1147 | 22.4464 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9358 | 0.052946 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97588 | 1.0827 | 22.2296 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9358 | 0.052946 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97588 | 1.0827 | 22.2296 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9358 | 0.052946 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97588 | 1.0827 | 941 | 1082.7056 | 0.97588 | 1.0952 | 0.0052 | 22.2296
0.942 | 1.0037 | 0.055291 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1165 | 22.4583 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9368 | 0.052949 | 1.0954 | 1.0952 | 1.0952 | 1.0952 | 0.97589 | 1.0844 | 22.2416 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9368 | 0.052949 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97589 | 1.0844 | 22.2416 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9368 | 0.052949 | 1.0952 | 1.0952 | 1.0952 | 1.0952 | 0.97589 | 1.0844 | 942 | 1084.4484 | 0.97589 | 1.0952 | 0.0052 | 22.2416
0.943 | 1.0047 | 0.055294 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1183 | 22.4703 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9378 | 0.052952 | 1.0954 | 1.0953 | 1.0953 | 1.0953 | 0.97589 | 1.0862 | 22.2535 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9378 | 0.052952 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97589 | 1.0862 | 22.2535 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9378 | 0.052952 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97589 | 1.0862 | 943 | 1086.1922 | 0.97589 | 1.0953 | 0.0052 | 22.2535
0.944 | 1.0058 | 0.055296 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.12 | 22.4822 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9388 | 0.052955 | 1.0954 | 1.0953 | 1.0953 | 1.0953 | 0.9759 | 1.0879 | 22.2654 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9388 | 0.052955 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.9759 | 1.0879 | 22.2654 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9388 | 0.052955 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.9759 | 1.0879 | 944 | 1087.9368 | 0.9759 | 1.0953 | 0.0052 | 22.2654
0.945 | 1.0068 | 0.055299 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1218 | 22.4942 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9398 | 0.052958 | 1.0954 | 1.0953 | 1.0953 | 1.0953 | 0.97591 | 1.0897 | 22.2773 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9398 | 0.052958 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97591 | 1.0897 | 22.2773 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9398 | 0.052958 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97591 | 1.0897 | 945 | 1089.6825 | 0.97591 | 1.0953 | 0.0052 | 22.2773
0.946 | 1.0078 | 0.055302 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1236 | 22.5061 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9408 | 0.052962 | 1.0954 | 1.0953 | 1.0953 | 1.0953 | 0.97592 | 1.0914 | 22.2892 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9408 | 0.052962 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97592 | 1.0914 | 22.2892 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9408 | 0.052962 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97592 | 1.0914 | 946 | 1091.429 | 0.97592 | 1.0953 | 0.0052 | 22.2892
0.947 | 1.0089 | 0.055304 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1254 | 22.5181 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9418 | 0.052965 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97593 | 1.0932 | 22.3011 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9418 | 0.052965 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97593 | 1.0932 | 22.3011 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9418 | 0.052965 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97593 | 1.0932 | 947 | 1093.1765 | 0.97593 | 1.0953 | 0.0052 | 22.3011
0.948 | 1.0099 | 0.055307 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1272 | 22.53 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9428 | 0.052968 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97594 | 1.0949 | 22.313 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9428 | 0.052968 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97594 | 1.0949 | 22.313 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9428 | 0.052968 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97594 | 1.0949 | 948 | 1094.9249 | 0.97594 | 1.0953 | 0.0052 | 22.313
0.949 | 1.011 | 0.05531 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.129 | 22.5419 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9438 | 0.052971 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97595 | 1.0967 | 22.3248 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9438 | 0.052971 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97595 | 1.0967 | 22.3248 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9438 | 0.052971 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97595 | 1.0967 | 949 | 1096.6743 | 0.97595 | 1.0953 | 0.0052 | 22.3248
0.95 | 1.012 | 0.055312 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1308 | 22.5538 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9448 | 0.052974 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97595 | 1.0984 | 22.3367 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9448 | 0.052974 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97595 | 1.0984 | 22.3367 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9448 | 0.052974 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97595 | 1.0984 | 950 | 1098.4246 | 0.97595 | 1.0953 | 0.0052 | 22.3367
0.951 | 1.0131 | 0.055315 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1326 | 22.5657 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9458 | 0.052977 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97596 | 1.1002 | 22.3486 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9458 | 0.052977 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97596 | 1.1002 | 22.3486 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9458 | 0.052977 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97596 | 1.1002 | 951 | 1100.1758 | 0.97596 | 1.0953 | 0.0052 | 22.3486
0.952 | 1.0141 | 0.055317 | 1.1004 | 1.1004 | 1.1004 | 1.1004 | 1.1344 | 22.5776 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9468 | 0.05298 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97597 | 1.1019 | 22.3604 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9468 | 0.05298 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97597 | 1.1019 | 22.3604 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9468 | 0.05298 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97597 | 1.1019 | 952 | 1101.9279 | 0.97597 | 1.0953 | 0.0052 | 22.3604
0.953 | 1.0151 | 0.05532 | 1.1004 | 1.1005 | 1.1005 | 1.1005 | 1.1361 | 22.5895 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9478 | 0.052984 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97598 | 1.1037 | 22.3723 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9478 | 0.052984 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97598 | 1.1037 | 22.3723 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9478 | 0.052984 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97598 | 1.1037 | 953 | 1103.681 | 0.97598 | 1.0953 | 0.0052 | 22.3723
0.954 | 1.0162 | 0.055323 | 1.1004 | 1.1005 | 1.1005 | 1.1005 | 1.1379 | 22.6014 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9488 | 0.052987 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.97599 | 1.1054 | 22.3841 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9488 | 0.052987 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97599 | 1.1054 | 22.3841 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9488 | 0.052987 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97599 | 1.1054 | 954 | 1105.435 | 0.97599 | 1.0953 | 0.0052 | 22.3841
0.955 | 1.0172 | 0.055325 | 1.1004 | 1.1005 | 1.1005 | 1.1005 | 1.1397 | 22.6133 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9498 | 0.05299 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.976 | 1.1072 | 22.396 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9498 | 0.05299 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.976 | 1.1072 | 22.396 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9498 | 0.05299 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.976 | 1.1072 | 955 | 1107.1899 | 0.976 | 1.0953 | 0.0052 | 22.396
0.956 | 1.0183 | 0.055328 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1415 | 22.6252 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9508 | 0.052993 | 1.0955 | 1.0953 | 1.0953 | 1.0953 | 0.976 | 1.1089 | 22.4078 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9508 | 0.052993 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.976 | 1.1089 | 22.4078 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9508 | 0.052993 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.976 | 1.1089 | 956 | 1108.9458 | 0.976 | 1.0953 | 0.0052 | 22.4078
0.957 | 1.0193 | 0.055331 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1433 | 22.637 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9518 | 0.052996 | 1.0955 | 1.0954 | 1.0953 | 1.0953 | 0.97601 | 1.1107 | 22.4196 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9518 | 0.052996 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97601 | 1.1107 | 22.4196 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9518 | 0.052996 | 1.0953 | 1.0953 | 1.0953 | 1.0953 | 0.97601 | 1.1107 | 957 | 1110.7026 | 0.97601 | 1.0953 | 0.0052 | 22.4196
0.958 | 1.0203 | 0.055333 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1451 | 22.6489 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9528 | 0.052999 | 1.0955 | 1.0954 | 1.0954 | 1.0954 | 0.97602 | 1.1125 | 22.4314 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9528 | 0.052999 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97602 | 1.1125 | 22.4314 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9528 | 0.052999 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97602 | 1.1125 | 958 | 1112.4603 | 0.97602 | 1.0954 | 0.0052 | 22.4314
0.959 | 1.0214 | 0.055336 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1469 | 22.6608 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9538 | 0.053002 | 1.0955 | 1.0954 | 1.0954 | 1.0954 | 0.97603 | 1.1142 | 22.4432 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9538 | 0.053002 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97603 | 1.1142 | 22.4432 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9538 | 0.053002 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97603 | 1.1142 | 959 | 1114.2189 | 0.97603 | 1.0954 | 0.0052 | 22.4432
0.96 | 1.0224 | 0.055338 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1487 | 22.6726 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9548 | 0.053005 | 1.0955 | 1.0954 | 1.0954 | 1.0954 | 0.97604 | 1.116 | 22.4551 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9548 | 0.053005 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97604 | 1.116 | 22.4551 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9548 | 0.053005 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97604 | 1.116 | 960 | 1115.9785 | 0.97604 | 1.0954 | 0.0052 | 22.4551
0.961 | 1.0235 | 0.055341 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1505 | 22.6845 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9558 | 0.053008 | 1.0955 | 1.0954 | 1.0954 | 1.0954 | 0.97605 | 1.1177 | 22.4669 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9558 | 0.053008 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97605 | 1.1177 | 22.4669 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9558 | 0.053008 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97605 | 1.1177 | 961 | 1117.739 | 0.97605 | 1.0954 | 0.0052 | 22.4669
0.962 | 1.0245 | 0.055343 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1523 | 22.6963 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9568 | 0.053011 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97605 | 1.1195 | 22.4787 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9568 | 0.053011 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97605 | 1.1195 | 22.4787 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9568 | 0.053011 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97605 | 1.1195 | 962 | 1119.5004 | 0.97605 | 1.0954 | 0.0052 | 22.4787
0.963 | 1.0255 | 0.055346 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1541 | 22.7081 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9578 | 0.053014 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97606 | 1.1213 | 22.4904 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9578 | 0.053014 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97606 | 1.1213 | 22.4904 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9578 | 0.053014 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97606 | 1.1213 | 963 | 1121.2628 | 0.97606 | 1.0954 | 0.0052 | 22.4904
0.964 | 1.0266 | 0.055349 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1559 | 22.72 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9588 | 0.053017 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97607 | 1.123 | 22.5022 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9588 | 0.053017 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97607 | 1.123 | 22.5022 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9588 | 0.053017 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97607 | 1.123 | 964 | 1123.0261 | 0.97607 | 1.0954 | 0.0052 | 22.5022
0.965 | 1.0276 | 0.055351 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1577 | 22.7318 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9598 | 0.05302 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97608 | 1.1248 | 22.514 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9598 | 0.05302 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97608 | 1.1248 | 22.514 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9598 | 0.05302 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97608 | 1.1248 | 965 | 1124.7903 | 0.97608 | 1.0954 | 0.0052 | 22.514
0.966 | 1.0287 | 0.055354 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1596 | 22.7436 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9608 | 0.053024 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97609 | 1.1266 | 22.5258 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9608 | 0.053024 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97609 | 1.1266 | 22.5258 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9608 | 0.053024 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97609 | 1.1266 | 966 | 1126.5554 | 0.97609 | 1.0954 | 0.0052 | 22.5258
0.967 | 1.0297 | 0.055356 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1614 | 22.7554 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9618 | 0.053027 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.9761 | 1.1283 | 22.5375 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9618 | 0.053027 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.9761 | 1.1283 | 22.5375 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9618 | 0.053027 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.9761 | 1.1283 | 967 | 1128.3214 | 0.9761 | 1.0954 | 0.0052 | 22.5375
0.968 | 1.0308 | 0.055359 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1632 | 22.7672 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9628 | 0.05303 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.9761 | 1.1301 | 22.5493 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9628 | 0.05303 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.9761 | 1.1301 | 22.5493 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9628 | 0.05303 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.9761 | 1.1301 | 968 | 1130.0884 | 0.9761 | 1.0954 | 0.0052 | 22.5493
0.969 | 1.0318 | 0.055361 | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.165 | 22.779 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9638 | 0.053033 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97611 | 1.1319 | 22.5611 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9638 | 0.053033 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97611 | 1.1319 | 22.5611 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9638 | 0.053033 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97611 | 1.1319 | 969 | 1131.8563 | 0.97611 | 1.0954 | 0.0052 | 22.5611
0.97 | 1.0328 | 0.055364 | 1.1005 | 1.1006 | 1.1006 | 1.1006 | 1.1668 | 22.7908 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9648 | 0.053036 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97612 | 1.1336 | 22.5728 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9648 | 0.053036 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97612 | 1.1336 | 22.5728 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9648 | 0.053036 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97612 | 1.1336 | 970 | 1133.6251 | 0.97612 | 1.0954 | 0.0052 | 22.5728
0.971 | 1.0339 | 0.055366 | 1.1005 | 1.1006 | 1.1006 | 1.1006 | 1.1686 | 22.8026 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9658 | 0.053039 | 1.0956 | 1.0954 | 1.0954 | 1.0954 | 0.97613 | 1.1354 | 22.5845 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9658 | 0.053039 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97613 | 1.1354 | 22.5845 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9658 | 0.053039 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97613 | 1.1354 | 971 | 1135.3948 | 0.97613 | 1.0954 | 0.0052 | 22.5845
0.972 | 1.0349 | 0.055369 | 1.1005 | 1.1006 | 1.1006 | 1.1006 | 1.1704 | 22.8143 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9668 | 0.053042 | 1.0956 | 1.0955 | 1.0954 | 1.0954 | 0.97614 | 1.1372 | 22.5963 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9668 | 0.053042 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97614 | 1.1372 | 22.5963 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9668 | 0.053042 | 1.0954 | 1.0954 | 1.0954 | 1.0954 | 0.97614 | 1.1372 | 972 | 1137.1655 | 0.97614 | 1.0954 | 0.0052 | 22.5963
0.973 | 1.036 | 0.055371 | 1.1005 | 1.1006 | 1.1006 | 1.1006 | 1.1722 | 22.8261 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9678 | 0.053045 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97614 | 1.1389 | 22.608 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9678 | 0.053045 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97614 | 1.1389 | 22.608 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9678 | 0.053045 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97614 | 1.1389 | 973 | 1138.937 | 0.97614 | 1.0955 | 0.0052 | 22.608
0.974 | 1.037 | 0.055374 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.174 | 22.8379 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9688 | 0.053048 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97615 | 1.1407 | 22.6197 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9688 | 0.053048 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97615 | 1.1407 | 22.6197 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9688 | 0.053048 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97615 | 1.1407 | 974 | 1140.7095 | 0.97615 | 1.0955 | 0.0052 | 22.6197
0.975 | 1.038 | 0.055376 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1758 | 22.8496 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9698 | 0.053051 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97616 | 1.1425 | 22.6314 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9698 | 0.053051 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97616 | 1.1425 | 22.6314 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9698 | 0.053051 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97616 | 1.1425 | 975 | 1142.4829 | 0.97616 | 1.0955 | 0.0052 | 22.6314
0.976 | 1.0391 | 0.055379 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1777 | 22.8614 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9708 | 0.053054 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97617 | 1.1443 | 22.6431 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9708 | 0.053054 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97617 | 1.1443 | 22.6431 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9708 | 0.053054 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97617 | 1.1443 | 976 | 1144.2573 | 0.97617 | 1.0955 | 0.0052 | 22.6431
0.977 | 1.0401 | 0.055381 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1795 | 22.8731 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9718 | 0.053057 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97618 | 1.146 | 22.6549 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9718 | 0.053057 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97618 | 1.146 | 22.6549 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9718 | 0.053057 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97618 | 1.146 | 977 | 1146.0325 | 0.97618 | 1.0955 | 0.0052 | 22.6549
0.978 | 1.0412 | 0.055384 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1813 | 22.8849 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9728 | 0.05306 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97618 | 1.1478 | 22.6665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9728 | 0.05306 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97618 | 1.1478 | 22.6665 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9728 | 0.05306 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97618 | 1.1478 | 978 | 1147.8087 | 0.97618 | 1.0955 | 0.0052 | 22.6665
0.979 | 1.0422 | 0.055386 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1831 | 22.8966 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9738 | 0.053063 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97619 | 1.1496 | 22.6782 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9738 | 0.053063 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97619 | 1.1496 | 22.6782 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9738 | 0.053063 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97619 | 1.1496 | 979 | 1149.5858 | 0.97619 | 1.0955 | 0.0052 | 22.6782
0.98 | 1.0432 | 0.055389 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1849 | 22.9083 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9748 | 0.053065 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.9762 | 1.1514 | 22.6899 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9748 | 0.053065 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.9762 | 1.1514 | 22.6899 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9748 | 0.053065 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.9762 | 1.1514 | 980 | 1151.3638 | 0.9762 | 1.0955 | 0.0052 | 22.6899
0.981 | 1.0443 | 0.055391 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1868 | 22.9201 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9758 | 0.053068 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97621 | 1.1531 | 22.7016 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9758 | 0.053068 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97621 | 1.1531 | 22.7016 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9758 | 0.053068 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97621 | 1.1531 | 981 | 1153.1427 | 0.97621 | 1.0955 | 0.0052 | 22.7016
0.982 | 1.0453 | 0.055394 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1886 | 22.9318 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9768 | 0.053071 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97622 | 1.1549 | 22.7133 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9768 | 0.053071 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97622 | 1.1549 | 22.7133 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9768 | 0.053071 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97622 | 1.1549 | 982 | 1154.9225 | 0.97622 | 1.0955 | 0.0052 | 22.7133
0.983 | 1.0464 | 0.055396 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1904 | 22.9435 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9778 | 0.053074 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97622 | 1.1567 | 22.7249 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9778 | 0.053074 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97622 | 1.1567 | 22.7249 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9778 | 0.053074 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97622 | 1.1567 | 983 | 1156.7032 | 0.97622 | 1.0955 | 0.0052 | 22.7249
0.984 | 1.0474 | 0.055399 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1922 | 22.9552 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9788 | 0.053077 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97623 | 1.1585 | 22.7366 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9788 | 0.053077 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97623 | 1.1585 | 22.7366 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9788 | 0.053077 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97623 | 1.1585 | 984 | 1158.4849 | 0.97623 | 1.0955 | 0.0052 | 22.7366
0.985 | 1.0485 | 0.055401 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.194 | 22.9669 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9798 | 0.05308 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97624 | 1.1603 | 22.7483 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9798 | 0.05308 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97624 | 1.1603 | 22.7483 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9798 | 0.05308 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97624 | 1.1603 | 985 | 1160.2675 | 0.97624 | 1.0955 | 0.0052 | 22.7483
0.986 | 1.0495 | 0.055404 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1959 | 22.9786 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9808 | 0.053083 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97625 | 1.1621 | 22.7599 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9808 | 0.053083 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97625 | 1.1621 | 22.7599 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9808 | 0.053083 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97625 | 1.1621 | 986 | 1162.051 | 0.97625 | 1.0955 | 0.0052 | 22.7599
0.987 | 1.0505 | 0.055406 | 1.1006 | 1.1006 | 1.1006 | 1.1006 | 1.1977 | 22.9903 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9818 | 0.053086 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97626 | 1.1638 | 22.7716 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9818 | 0.053086 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97626 | 1.1638 | 22.7716 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9818 | 0.053086 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97626 | 1.1638 | 987 | 1163.8354 | 0.97626 | 1.0955 | 0.0052 | 22.7716
0.988 | 1.0516 | 0.055409 | 1.1006 | 1.1007 | 1.1007 | 1.1007 | 1.1995 | 23.002 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9827 | 0.053045 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97581 | 1.165 | 22.779 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9828 | 0.053089 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97626 | 1.1656 | 22.7832 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9828 | 0.053089 | 1.0955 | 1.0955 | 1.0955 | 1.0955 | 0.97626 | 1.1656 | 988 | 1165.6207 | 0.97626 | 1.0955 | 0.0052 | 22.7832
0.989 | 1.0526 | 0.055411 | 1.1006 | 1.1007 | 1.1007 | 1.1007 | 1.2013 | 23.0136 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9837 | 0.053048 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97582 | 1.1668 | 22.7906 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9838 | 0.053092 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97627 | 1.1674 | 22.7948 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9838 | 0.053092 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97627 | 1.1674 | 989 | 1167.4069 | 0.97627 | 1.0956 | 0.0052 | 22.7948
0.99 | 1.0537 | 0.055414 | 1.1006 | 1.1007 | 1.1007 | 1.1007 | 1.2032 | 23.0253 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9847 | 0.053051 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97583 | 1.1685 | 22.8023 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9848 | 0.053095 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97628 | 1.1692 | 22.8065 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9848 | 0.053095 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97628 | 1.1692 | 990 | 1169.1941 | 0.97628 | 1.0956 | 0.0052 | 22.8065
0.991 | 1.0547 | 0.055416 | 1.1006 | 1.1007 | 1.1007 | 1.1007 | 1.205 | 23.037 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9857 | 0.053054 | 1.0956 | 1.0955 | 1.0955 | 1.0955 | 0.97583 | 1.1703 | 22.8139 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9858 | 0.053098 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97629 | 1.171 | 22.8181 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9858 | 0.053098 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97629 | 1.171 | 991 | 1170.9821 | 0.97629 | 1.0956 | 0.0052 | 22.8181
0.992 | 1.0557 | 0.055418 | 1.1006 | 1.1007 | 1.1007 | 1.1007 | 1.2068 | 23.0486 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9867 | 0.053057 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97584 | 1.1721 | 22.8255 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9868 | 0.053101 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.9763 | 1.1728 | 22.8297 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9868 | 0.053101 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.9763 | 1.1728 | 992 | 1172.7711 | 0.9763 | 1.0956 | 0.0052 | 22.8297
0.993 | 1.0568 | 0.055421 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2087 | 23.0603 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9877 | 0.05306 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97585 | 1.1739 | 22.8371 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9878 | 0.053103 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.9763 | 1.1746 | 22.8413 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9878 | 0.053103 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.9763 | 1.1746 | 993 | 1174.561 | 0.9763 | 1.0956 | 0.0052 | 22.8413
0.994 | 1.0578 | 0.055423 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2105 | 23.0719 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9887 | 0.053062 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97586 | 1.1757 | 22.8487 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9888 | 0.053106 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97631 | 1.1764 | 22.8529 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9888 | 0.053106 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97631 | 1.1764 | 994 | 1176.3518 | 0.97631 | 1.0956 | 0.0052 | 22.8529
0.995 | 1.0589 | 0.055426 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2123 | 23.0836 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9897 | 0.053065 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97587 | 1.1775 | 22.8603 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9898 | 0.053109 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97632 | 1.1781 | 22.8645 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9898 | 0.053109 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97632 | 1.1781 | 995 | 1178.1434 | 0.97632 | 1.0956 | 0.0052 | 22.8645
0.996 | 1.0599 | 0.055428 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2142 | 23.0952 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9907 | 0.053068 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97587 | 1.1793 | 22.8719 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9908 | 0.053112 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97633 | 1.1799 | 22.8761 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9908 | 0.053112 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97633 | 1.1799 | 996 | 1179.9361 | 0.97633 | 1.0956 | 0.0052 | 22.8761
0.997 | 1.0609 | 0.05543 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.216 | 23.1068 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9917 | 0.053071 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97588 | 1.1811 | 22.8835 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9918 | 0.053115 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97633 | 1.1817 | 22.8877 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9918 | 0.053115 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97633 | 1.1817 | 997 | 1181.7296 | 0.97633 | 1.0956 | 0.0052 | 22.8877
0.998 | 1.062 | 0.055433 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2178 | 23.1185 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9927 | 0.053074 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97589 | 1.1829 | 22.895 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9928 | 0.053118 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97634 | 1.1835 | 22.8992 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9928 | 0.053118 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97634 | 1.1835 | 998 | 1183.524 | 0.97634 | 1.0956 | 0.0052 | 22.8992
0.999 | 1.063 | 0.055435 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2197 | 23.1301 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9937 | 0.053077 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.9759 | 1.1847 | 22.9066 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9938 | 0.053121 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97635 | 1.1853 | 22.9108 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9938 | 0.053121 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97635 | 1.1853 | 999 | 1185.3193 | 0.97635 | 1.0956 | 0.0052 | 22.9108
1 | 1.0641 | 0.055438 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2215 | 23.1417 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9947 | 0.05308 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97591 | 1.1865 | 22.9182 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9948 | 0.053123 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97636 | 1.1871 | 22.9224 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9948 | 0.053123 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97636 | 1.1871 | 1000 | 1187.1156 | 0.97636 | 1.0956 | 0.0052 | 22.9224
1.001 | 1.0651 | 0.05544 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2234 | 23.1533 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9957 | 0.053082 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97591 | 1.1883 | 22.9297 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9958 | 0.053126 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97636 | 1.1889 | 22.934 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9958 | 0.053126 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97636 | 1.1889 | 1001 | 1188.9127 | 0.97636 | 1.0956 | 0.0052 | 22.934
1.002 | 1.0662 | 0.055442 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2252 | 23.1649 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9967 | 0.053085 | 1.0957 | 1.0955 | 1.0955 | 1.0955 | 0.97592 | 1.1901 | 22.9413 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9968 | 0.053129 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97637 | 1.1907 | 22.9455 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9968 | 0.053129 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97637 | 1.1907 | 1002 | 1190.7108 | 0.97637 | 1.0956 | 0.0052 | 22.9455
1.003 | 1.0672 | 0.055445 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.227 | 23.1765 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9977 | 0.053088 | 1.0957 | 1.0956 | 1.0955 | 1.0955 | 0.97593 | 1.1919 | 22.9528 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9978 | 0.053132 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97638 | 1.1925 | 22.9571 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9978 | 0.053132 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97638 | 1.1925 | 1003 | 1192.5097 | 0.97638 | 1.0956 | 0.0052 | 22.9571
1.004 | 1.0682 | 0.055447 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2289 | 23.1881 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9987 | 0.053091 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 0.97594 | 1.1937 | 22.9644 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9988 | 0.053135 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97639 | 1.1943 | 22.9686 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9988 | 0.053135 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97639 | 1.1943 | 1004 | 1194.3096 | 0.97639 | 1.0956 | 0.0052 | 22.9686
1.005 | 1.0693 | 0.05545 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2307 | 23.1996 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 0.9997 | 0.053094 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 0.97594 | 1.1955 | 22.9759 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9998 | 0.053138 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9764 | 1.1961 | 22.9801 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 0.9998 | 0.053138 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9764 | 1.1961 | 1005 | 1196.1104 | 0.9764 | 1.0957 | 0.0052 | 22.9801
1.006 | 1.0703 | 0.055452 | 1.1007 | 1.1007 | 1.1007 | 1.1007 | 1.2326 | 23.2112 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0007 | 0.053097 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 0.97595 | 1.1973 | 22.9875 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 1.0008 | 0.05314 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9764 | 1.1979 | 22.9917 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 1.0008 | 0.05314 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9764 | 1.1979 | 1006 | 1197.912 | 0.9764 | 1.0957 | 0.0052 | 22.9917
1.007 | 1.0714 | 0.055454 | 1.1007 | 1.1008 | 1.1008 | 1.1008 | 1.2344 | 23.2228 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0017 | 0.053099 | 1.0957 | 1.0956 | 1.0956 | 1.0956 | 0.97596 | 1.1991 | 22.999 | 0.006 | 0.0048 | 0.0052 | 0.64052 | 1.0018 | 0.053143 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97641 | 1.1997 | 23.0032 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0017 | 0.053099 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97596 | 1.1991 | 1007 | 1199.056 | 0.97596 | 1.0956 | 0.0053 | 23.0032
1.008 | 1.0724 | 0.055457 | 1.1007 | 1.1008 | 1.1008 | 1.1008 | 1.2362 | 23.2344 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0027 | 0.053102 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97597 | 1.2009 | 23.0105 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0027 | 0.053102 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97597 | 1.2009 | 23.0105 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0027 | 0.053102 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97597 | 1.2009 | 1008 | 1200.8587 | 0.97597 | 1.0956 | 0.0053 | 23.0105
1.009 | 1.0734 | 0.055459 | 1.1007 | 1.1008 | 1.1008 | 1.1008 | 1.2381 | 23.2459 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0037 | 0.053105 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97597 | 1.2027 | 23.022 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0037 | 0.053105 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97597 | 1.2027 | 23.022 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0037 | 0.053105 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97597 | 1.2027 | 1009 | 1202.6623 | 0.97597 | 1.0956 | 0.0053 | 23.022
1.01 | 1.0745 | 0.055461 | 1.1007 | 1.1008 | 1.1008 | 1.1008 | 1.2399 | 23.2575 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0047 | 0.053108 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97598 | 1.2045 | 23.0335 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0047 | 0.053108 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97598 | 1.2045 | 23.0335 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0047 | 0.053108 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97598 | 1.2045 | 1010 | 1204.4668 | 0.97598 | 1.0956 | 0.0053 | 23.0335
1.011 | 1.0755 | 0.055464 | 1.1007 | 1.1008 | 1.1008 | 1.1008 | 1.2418 | 23.269 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0057 | 0.053111 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97599 | 1.2063 | 23.045 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0057 | 0.053111 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97599 | 1.2063 | 23.045 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0057 | 0.053111 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97599 | 1.2063 | 1011 | 1206.2722 | 0.97599 | 1.0956 | 0.0053 | 23.045
1.012 | 1.0766 | 0.055466 | 1.1007 | 1.1008 | 1.1008 | 1.1008 | 1.2436 | 23.2806 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0067 | 0.053113 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.976 | 1.2081 | 23.0565 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0067 | 0.053113 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.976 | 1.2081 | 23.0565 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0067 | 0.053113 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.976 | 1.2081 | 1012 | 1208.0785 | 0.976 | 1.0956 | 0.0053 | 23.0565
1.013 | 1.0776 | 0.055468 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2455 | 23.2921 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0077 | 0.053116 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97601 | 1.2099 | 23.068 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0077 | 0.053116 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97601 | 1.2099 | 23.068 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0077 | 0.053116 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97601 | 1.2099 | 1013 | 1209.8857 | 0.97601 | 1.0956 | 0.0053 | 23.068
1.014 | 1.0786 | 0.055471 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2473 | 23.3036 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0087 | 0.053119 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97601 | 1.2117 | 23.0795 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0087 | 0.053119 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97601 | 1.2117 | 23.0795 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0087 | 0.053119 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97601 | 1.2117 | 1014 | 1211.6938 | 0.97601 | 1.0956 | 0.0053 | 23.0795
1.015 | 1.0797 | 0.055473 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2492 | 23.3152 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0097 | 0.053122 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97602 | 1.2135 | 23.091 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0097 | 0.053122 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97602 | 1.2135 | 23.091 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0097 | 0.053122 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97602 | 1.2135 | 1015 | 1213.5028 | 0.97602 | 1.0956 | 0.0053 | 23.091
1.016 | 1.0807 | 0.055475 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.251 | 23.3267 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0107 | 0.053125 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97603 | 1.2153 | 23.1025 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0107 | 0.053125 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97603 | 1.2153 | 23.1025 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0107 | 0.053125 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97603 | 1.2153 | 1016 | 1215.3127 | 0.97603 | 1.0956 | 0.0053 | 23.1025
1.017 | 1.0818 | 0.055478 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2529 | 23.3382 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0117 | 0.053127 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97604 | 1.2171 | 23.1139 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0117 | 0.053127 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97604 | 1.2171 | 23.1139 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0117 | 0.053127 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97604 | 1.2171 | 1017 | 1217.1235 | 0.97604 | 1.0956 | 0.0053 | 23.1139
1.018 | 1.0828 | 0.05548 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2547 | 23.3497 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0127 | 0.05313 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97604 | 1.2189 | 23.1254 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0127 | 0.05313 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97604 | 1.2189 | 23.1254 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0127 | 0.05313 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97604 | 1.2189 | 1018 | 1218.9352 | 0.97604 | 1.0956 | 0.0053 | 23.1254
1.019 | 1.0839 | 0.055482 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2566 | 23.3612 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0137 | 0.053133 | 1.0958 | 1.0956 | 1.0956 | 1.0956 | 0.97605 | 1.2207 | 23.1368 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0137 | 0.053133 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97605 | 1.2207 | 23.1368 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0137 | 0.053133 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97605 | 1.2207 | 1019 | 1220.7478 | 0.97605 | 1.0956 | 0.0053 | 23.1368
1.02 | 1.0849 | 0.055484 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2585 | 23.3727 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0147 | 0.053136 | 1.0958 | 1.0957 | 1.0956 | 1.0956 | 0.97606 | 1.2226 | 23.1483 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0147 | 0.053136 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97606 | 1.2226 | 23.1483 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0147 | 0.053136 | 1.0956 | 1.0956 | 1.0956 | 1.0956 | 0.97606 | 1.2226 | 1020 | 1222.5613 | 0.97606 | 1.0956 | 0.0053 | 23.1483
1.021 | 1.0859 | 0.055487 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2603 | 23.3842 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0157 | 0.053138 | 1.0958 | 1.0957 | 1.0957 | 1.0957 | 0.97607 | 1.2244 | 23.1597 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0157 | 0.053138 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97607 | 1.2244 | 23.1597 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0157 | 0.053138 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97607 | 1.2244 | 1021 | 1224.3757 | 0.97607 | 1.0957 | 0.0053 | 23.1597
1.022 | 1.087 | 0.055489 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2622 | 23.3957 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0167 | 0.053141 | 1.0958 | 1.0957 | 1.0957 | 1.0957 | 0.97607 | 1.2262 | 23.1712 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0167 | 0.053141 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97607 | 1.2262 | 23.1712 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0167 | 0.053141 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97607 | 1.2262 | 1022 | 1226.191 | 0.97607 | 1.0957 | 0.0053 | 23.1712
1.023 | 1.088 | 0.055491 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.264 | 23.4071 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0177 | 0.053144 | 1.0958 | 1.0957 | 1.0957 | 1.0957 | 0.97608 | 1.228 | 23.1826 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0177 | 0.053144 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97608 | 1.228 | 23.1826 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0177 | 0.053144 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97608 | 1.228 | 1023 | 1228.0072 | 0.97608 | 1.0957 | 0.0053 | 23.1826
1.024 | 1.0891 | 0.055494 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2659 | 23.4186 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0187 | 0.053146 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97609 | 1.2298 | 23.194 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0187 | 0.053146 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97609 | 1.2298 | 23.194 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0187 | 0.053146 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97609 | 1.2298 | 1024 | 1229.8243 | 0.97609 | 1.0957 | 0.0053 | 23.194
1.025 | 1.0901 | 0.055496 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2678 | 23.4301 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0197 | 0.053149 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.9761 | 1.2316 | 23.2055 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0197 | 0.053149 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9761 | 1.2316 | 23.2055 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0197 | 0.053149 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9761 | 1.2316 | 1025 | 1231.6422 | 0.9761 | 1.0957 | 0.0053 | 23.2055
1.026 | 1.0911 | 0.055498 | 1.1008 | 1.1008 | 1.1008 | 1.1008 | 1.2696 | 23.4415 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0207 | 0.053152 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.9761 | 1.2335 | 23.2169 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0207 | 0.053152 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9761 | 1.2335 | 23.2169 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0207 | 0.053152 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.9761 | 1.2335 | 1026 | 1233.4611 | 0.9761 | 1.0957 | 0.0053 | 23.2169
1.027 | 1.0922 | 0.0555 | 1.1008 | 1.1009 | 1.1009 | 1.1009 | 1.2715 | 23.453 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0217 | 0.053155 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97611 | 1.2353 | 23.2283 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0217 | 0.053155 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97611 | 1.2353 | 23.2283 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0217 | 0.053155 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97611 | 1.2353 | 1027 | 1235.2809 | 0.97611 | 1.0957 | 0.0053 | 23.2283
1.028 | 1.0932 | 0.055503 | 1.1008 | 1.1009 | 1.1009 | 1.1009 | 1.2733 | 23.4645 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0227 | 0.053157 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97612 | 1.2371 | 23.2397 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0227 | 0.053157 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97612 | 1.2371 | 23.2397 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0227 | 0.053157 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97612 | 1.2371 | 1028 | 1237.1016 | 0.97612 | 1.0957 | 0.0053 | 23.2397
1.029 | 1.0943 | 0.055505 | 1.1008 | 1.1009 | 1.1009 | 1.1009 | 1.2752 | 23.4759 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0237 | 0.05316 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97612 | 1.2389 | 23.2511 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0237 | 0.05316 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97612 | 1.2389 | 23.2511 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0237 | 0.05316 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97612 | 1.2389 | 1029 | 1238.9231 | 0.97612 | 1.0957 | 0.0053 | 23.2511
1.03 | 1.0953 | 0.055507 | 1.1008 | 1.1009 | 1.1009 | 1.1009 | 1.2771 | 23.4873 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0247 | 0.053163 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97613 | 1.2407 | 23.2625 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0247 | 0.053163 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97613 | 1.2407 | 23.2625 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0247 | 0.053163 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97613 | 1.2407 | 1030 | 1240.7456 | 0.97613 | 1.0957 | 0.0053 | 23.2625
1.031 | 1.0963 | 0.055509 | 1.1008 | 1.1009 | 1.1009 | 1.1009 | 1.2789 | 23.4988 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0257 | 0.053165 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97614 | 1.2426 | 23.2739 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0257 | 0.053165 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97614 | 1.2426 | 23.2739 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0257 | 0.053165 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97614 | 1.2426 | 1031 | 1242.5689 | 0.97614 | 1.0957 | 0.0053 | 23.2739
1.032 | 1.0974 | 0.055512 | 1.1008 | 1.1009 | 1.1009 | 1.1009 | 1.2808 | 23.5102 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0267 | 0.053168 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97615 | 1.2444 | 23.2853 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0267 | 0.053168 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97615 | 1.2444 | 23.2853 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0267 | 0.053168 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97615 | 1.2444 | 1032 | 1244.3932 | 0.97615 | 1.0957 | 0.0053 | 23.2853
1.033 | 1.0984 | 0.055514 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2827 | 23.5216 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0277 | 0.053171 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97615 | 1.2462 | 23.2967 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0277 | 0.053171 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97615 | 1.2462 | 23.2967 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0277 | 0.053171 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97615 | 1.2462 | 1033 | 1246.2183 | 0.97615 | 1.0957 | 0.0053 | 23.2967
1.034 | 1.0995 | 0.055516 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2845 | 23.533 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0287 | 0.053173 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97616 | 1.248 | 23.308 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0287 | 0.053173 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97616 | 1.248 | 23.308 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0287 | 0.053173 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97616 | 1.248 | 1034 | 1248.0443 | 0.97616 | 1.0957 | 0.0053 | 23.308
1.035 | 1.1005 | 0.055518 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2864 | 23.5445 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0297 | 0.053176 | 1.0959 | 1.0957 | 1.0957 | 1.0957 | 0.97617 | 1.2499 | 23.3194 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0297 | 0.053176 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97617 | 1.2499 | 23.3194 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0297 | 0.053176 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97617 | 1.2499 | 1035 | 1249.8713 | 0.97617 | 1.0957 | 0.0053 | 23.3194
1.036 | 1.1016 | 0.055521 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2883 | 23.5559 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0307 | 0.053179 | 1.0959 | 1.0958 | 1.0957 | 1.0957 | 0.97618 | 1.2517 | 23.3308 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0307 | 0.053179 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97618 | 1.2517 | 23.3308 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0307 | 0.053179 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97618 | 1.2517 | 1036 | 1251.6991 | 0.97618 | 1.0957 | 0.0053 | 23.3308
1.037 | 1.1026 | 0.055523 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2902 | 23.5673 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0317 | 0.053181 | 1.0959 | 1.0958 | 1.0958 | 1.0957 | 0.97618 | 1.2535 | 23.3421 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0317 | 0.053181 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97618 | 1.2535 | 23.3421 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0317 | 0.053181 | 1.0957 | 1.0957 | 1.0957 | 1.0957 | 0.97618 | 1.2535 | 1037 | 1253.5278 | 0.97618 | 1.0957 | 0.0053 | 23.3421
1.038 | 1.1036 | 0.055525 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.292 | 23.5787 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0327 | 0.053184 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.97619 | 1.2554 | 23.3535 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0327 | 0.053184 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97619 | 1.2554 | 23.3535 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0327 | 0.053184 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97619 | 1.2554 | 1038 | 1255.3574 | 0.97619 | 1.0958 | 0.0053 | 23.3535
1.039 | 1.1047 | 0.055527 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2939 | 23.5901 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0337 | 0.053187 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.9762 | 1.2572 | 23.3648 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0337 | 0.053187 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.9762 | 1.2572 | 23.3648 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0337 | 0.053187 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.9762 | 1.2572 | 1039 | 1257.1878 | 0.9762 | 1.0958 | 0.0053 | 23.3648
1.04 | 1.1057 | 0.05553 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2958 | 23.6014 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0347 | 0.053189 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.97621 | 1.259 | 23.3762 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0347 | 0.053189 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97621 | 1.259 | 23.3762 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0347 | 0.053189 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97621 | 1.259 | 1040 | 1259.0192 | 0.97621 | 1.0958 | 0.0053 | 23.3762
1.041 | 1.1068 | 0.055532 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2976 | 23.6128 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0357 | 0.053192 | 1.0959 | 1.0958 | 1.0958 | 1.0958 | 0.97621 | 1.2609 | 23.3875 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0357 | 0.053192 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97621 | 1.2609 | 23.3875 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0357 | 0.053192 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97621 | 1.2609 | 1041 | 1260.8515 | 0.97621 | 1.0958 | 0.0053 | 23.3875
1.042 | 1.1078 | 0.055534 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.2995 | 23.6242 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0367 | 0.053195 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97622 | 1.2627 | 23.3988 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0367 | 0.053195 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97622 | 1.2627 | 23.3988 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0367 | 0.053195 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97622 | 1.2627 | 1042 | 1262.6846 | 0.97622 | 1.0958 | 0.0053 | 23.3988
1.043 | 1.1088 | 0.055536 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.3014 | 23.6356 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0377 | 0.053197 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97623 | 1.2645 | 23.4101 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0377 | 0.053197 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97623 | 1.2645 | 23.4101 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0377 | 0.053197 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97623 | 1.2645 | 1043 | 1264.5187 | 0.97623 | 1.0958 | 0.0053 | 23.4101
1.044 | 1.1099 | 0.055538 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.3033 | 23.6469 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0387 | 0.0532 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97623 | 1.2664 | 23.4215 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0387 | 0.0532 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97623 | 1.2664 | 23.4215 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0387 | 0.0532 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97623 | 1.2664 | 1044 | 1266.3536 | 0.97623 | 1.0958 | 0.0053 | 23.4215
1.045 | 1.1109 | 0.055541 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.3052 | 23.6583 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0397 | 0.053203 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97624 | 1.2682 | 23.4328 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0397 | 0.053203 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97624 | 1.2682 | 23.4328 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0397 | 0.053203 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97624 | 1.2682 | 1045 | 1268.1894 | 0.97624 | 1.0958 | 0.0053 | 23.4328
1.046 | 1.112 | 0.055543 | 1.1009 | 1.1009 | 1.1009 | 1.1009 | 1.307 | 23.6696 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0407 | 0.053205 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97625 | 1.27 | 23.4441 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0407 | 0.053205 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97625 | 1.27 | 23.4441 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0407 | 0.053205 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97625 | 1.27 | 1046 | 1270.0261 | 0.97625 | 1.0958 | 0.0053 | 23.4441
1.047 | 1.113 | 0.055545 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3089 | 23.681 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0417 | 0.053208 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97626 | 1.2719 | 23.4554 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0417 | 0.053208 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97626 | 1.2719 | 23.4554 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0417 | 0.053208 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97626 | 1.2719 | 1047 | 1271.8637 | 0.97626 | 1.0958 | 0.0053 | 23.4554
1.048 | 1.114 | 0.055547 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3108 | 23.6923 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0427 | 0.05321 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97626 | 1.2737 | 23.4667 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0427 | 0.05321 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97626 | 1.2737 | 23.4667 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0427 | 0.05321 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97626 | 1.2737 | 1048 | 1273.7022 | 0.97626 | 1.0958 | 0.0053 | 23.4667
1.049 | 1.1151 | 0.055549 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3127 | 23.7037 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0437 | 0.053213 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97627 | 1.2755 | 23.478 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0437 | 0.053213 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97627 | 1.2755 | 23.478 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0437 | 0.053213 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97627 | 1.2755 | 1049 | 1275.5415 | 0.97627 | 1.0958 | 0.0053 | 23.478
1.05 | 1.1161 | 0.055551 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3146 | 23.715 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0447 | 0.053216 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97628 | 1.2774 | 23.4892 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0447 | 0.053216 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97628 | 1.2774 | 23.4892 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0447 | 0.053216 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97628 | 1.2774 | 1050 | 1277.3817 | 0.97628 | 1.0958 | 0.0053 | 23.4892
1.051 | 1.1172 | 0.055554 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3164 | 23.7263 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0457 | 0.053218 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97628 | 1.2792 | 23.5005 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0457 | 0.053218 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97628 | 1.2792 | 23.5005 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0457 | 0.053218 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97628 | 1.2792 | 1051 | 1279.2229 | 0.97628 | 1.0958 | 0.0053 | 23.5005
1.052 | 1.1182 | 0.055556 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3183 | 23.7376 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0467 | 0.053221 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.97629 | 1.2811 | 23.5118 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0467 | 0.053221 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97629 | 1.2811 | 23.5118 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0467 | 0.053221 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.97629 | 1.2811 | 1052 | 1281.0649 | 0.97629 | 1.0958 | 0.0053 | 23.5118
1.053 | 1.1193 | 0.055558 | 1.1009 | 1.101 | 1.101 | 1.101 | 1.3202 | 23.7489 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0477 | 0.053223 | 1.096 | 1.0958 | 1.0958 | 1.0958 | 0.9763 | 1.2829 | 23.5231 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0477 | 0.053223 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.9763 | 1.2829 | 23.5231 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0477 | 0.053223 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.9763 | 1.2829 | 1053 | 1282.9078 | 0.9763 | 1.0958 | 0.0053 | 23.5231
1.054 | 1.1203 | 0.05556 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3221 | 23.7603 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0487 | 0.053226 | 1.096 | 1.0959 | 1.0958 | 1.0958 | 0.9763 | 1.2848 | 23.5343 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0487 | 0.053226 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.9763 | 1.2848 | 23.5343 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0487 | 0.053226 | 1.0958 | 1.0958 | 1.0958 | 1.0958 | 0.9763 | 1.2848 | 1054 | 1284.7516 | 0.9763 | 1.0958 | 0.0053 | 23.5343
1.055 | 1.1213 | 0.055562 | 1.101 | 1.101 | 1.101 | 1.101 | 1.324 | 23.7716 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0497 | 0.053229 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.97631 | 1.2866 | 23.5456 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0497 | 0.053229 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97631 | 1.2866 | 23.5456 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0497 | 0.053229 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97631 | 1.2866 | 1055 | 1286.5962 | 0.97631 | 1.0959 | 0.0053 | 23.5456
1.056 | 1.1224 | 0.055564 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3259 | 23.7829 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0507 | 0.053231 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.97632 | 1.2884 | 23.5568 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0507 | 0.053231 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97632 | 1.2884 | 23.5568 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0507 | 0.053231 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97632 | 1.2884 | 1056 | 1288.4418 | 0.97632 | 1.0959 | 0.0053 | 23.5568
1.057 | 1.1234 | 0.055567 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3278 | 23.7941 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0517 | 0.053234 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.97633 | 1.2903 | 23.5681 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0517 | 0.053234 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97633 | 1.2903 | 23.5681 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0517 | 0.053234 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97633 | 1.2903 | 1057 | 1290.2882 | 0.97633 | 1.0959 | 0.0053 | 23.5681
1.058 | 1.1245 | 0.055569 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3297 | 23.8054 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0527 | 0.053236 | 1.096 | 1.0959 | 1.0959 | 1.0959 | 0.97633 | 1.2921 | 23.5793 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0527 | 0.053236 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97633 | 1.2921 | 23.5793 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0527 | 0.053236 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97633 | 1.2921 | 1058 | 1292.1355 | 0.97633 | 1.0959 | 0.0053 | 23.5793
1.059 | 1.1255 | 0.055571 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3316 | 23.8167 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0537 | 0.053239 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97634 | 1.294 | 23.5906 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0537 | 0.053239 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97634 | 1.294 | 23.5906 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0537 | 0.053239 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97634 | 1.294 | 1059 | 1293.9837 | 0.97634 | 1.0959 | 0.0053 | 23.5906
1.06 | 1.1265 | 0.055573 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3334 | 23.828 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0547 | 0.053241 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97635 | 1.2958 | 23.6018 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0547 | 0.053241 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97635 | 1.2958 | 23.6018 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0547 | 0.053241 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97635 | 1.2958 | 1060 | 1295.8328 | 0.97635 | 1.0959 | 0.0053 | 23.6018
1.061 | 1.1276 | 0.055575 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3353 | 23.8393 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0557 | 0.053244 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97635 | 1.2977 | 23.613 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0557 | 0.053244 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97635 | 1.2977 | 23.613 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0557 | 0.053244 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97635 | 1.2977 | 1061 | 1297.6827 | 0.97635 | 1.0959 | 0.0053 | 23.613
1.062 | 1.1286 | 0.055577 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3372 | 23.8505 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0567 | 0.053246 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97636 | 1.2995 | 23.6243 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0567 | 0.053246 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97636 | 1.2995 | 23.6243 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0567 | 0.053246 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97636 | 1.2995 | 1062 | 1299.5335 | 0.97636 | 1.0959 | 0.0053 | 23.6243
1.063 | 1.1297 | 0.055579 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3391 | 23.8618 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0577 | 0.053249 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97637 | 1.3014 | 23.6355 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0577 | 0.053249 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97637 | 1.3014 | 23.6355 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0577 | 0.053249 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97637 | 1.3014 | 1063 | 1301.3852 | 0.97637 | 1.0959 | 0.0053 | 23.6355
1.064 | 1.1307 | 0.055581 | 1.101 | 1.101 | 1.101 | 1.101 | 1.341 | 23.873 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0587 | 0.053251 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97637 | 1.3032 | 23.6467 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0587 | 0.053251 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97637 | 1.3032 | 23.6467 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0587 | 0.053251 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97637 | 1.3032 | 1064 | 1303.2378 | 0.97637 | 1.0959 | 0.0053 | 23.6467
1.065 | 1.1317 | 0.055584 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3429 | 23.8843 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0597 | 0.053254 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97638 | 1.3051 | 23.6579 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0597 | 0.053254 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97638 | 1.3051 | 23.6579 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0597 | 0.053254 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97638 | 1.3051 | 1065 | 1305.0913 | 0.97638 | 1.0959 | 0.0053 | 23.6579
1.066 | 1.1328 | 0.055586 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3448 | 23.8955 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0607 | 0.053257 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97639 | 1.3069 | 23.6691 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0607 | 0.053257 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97639 | 1.3069 | 23.6691 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0607 | 0.053257 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97639 | 1.3069 | 1066 | 1306.9457 | 0.97639 | 1.0959 | 0.0053 | 23.6691
1.067 | 1.1338 | 0.055588 | 1.101 | 1.101 | 1.101 | 1.101 | 1.3467 | 23.9068 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0617 | 0.053259 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97639 | 1.3088 | 23.6803 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0617 | 0.053259 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97639 | 1.3088 | 23.6803 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0617 | 0.053259 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97639 | 1.3088 | 1067 | 1308.8009 | 0.97639 | 1.0959 | 0.0053 | 23.6803
1.068 | 1.1349 | 0.05559 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3486 | 23.918 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0627 | 0.053262 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.9764 | 1.3107 | 23.6915 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0627 | 0.053262 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.9764 | 1.3107 | 23.6915 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0627 | 0.053262 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.9764 | 1.3107 | 1068 | 1310.657 | 0.9764 | 1.0959 | 0.0053 | 23.6915
1.069 | 1.1359 | 0.055592 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3505 | 23.9292 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0637 | 0.053264 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97641 | 1.3125 | 23.7026 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0637 | 0.053264 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97641 | 1.3125 | 23.7026 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0637 | 0.053264 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97641 | 1.3125 | 1069 | 1312.514 | 0.97641 | 1.0959 | 0.0053 | 23.7026
1.07 | 1.137 | 0.055594 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3524 | 23.9405 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0647 | 0.053267 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97642 | 1.3144 | 23.7138 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0647 | 0.053267 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97642 | 1.3144 | 23.7138 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0647 | 0.053267 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97642 | 1.3144 | 1070 | 1314.3718 | 0.97642 | 1.0959 | 0.0053 | 23.7138
1.071 | 1.138 | 0.055596 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3543 | 23.9517 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0657 | 0.053269 | 1.0961 | 1.0959 | 1.0959 | 1.0959 | 0.97642 | 1.3162 | 23.725 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0657 | 0.053269 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97642 | 1.3162 | 23.725 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0657 | 0.053269 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97642 | 1.3162 | 1071 | 1316.2305 | 0.97642 | 1.0959 | 0.0053 | 23.725
1.072 | 1.139 | 0.055598 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3562 | 23.9629 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0667 | 0.053272 | 1.0961 | 1.096 | 1.0959 | 1.0959 | 0.97643 | 1.3181 | 23.7362 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0667 | 0.053272 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97643 | 1.3181 | 23.7362 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0667 | 0.053272 | 1.0959 | 1.0959 | 1.0959 | 1.0959 | 0.97643 | 1.3181 | 1072 | 1318.0902 | 0.97643 | 1.0959 | 0.0053 | 23.7362
1.073 | 1.1401 | 0.0556 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3581 | 23.9741 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0677 | 0.053274 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.97644 | 1.32 | 23.7473 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0677 | 0.053274 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97644 | 1.32 | 23.7473 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0677 | 0.053274 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97644 | 1.32 | 1073 | 1319.9506 | 0.97644 | 1.096 | 0.0053 | 23.7473
1.074 | 1.1411 | 0.055602 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.36 | 23.9853 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0687 | 0.053277 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.97644 | 1.3218 | 23.7585 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0687 | 0.053277 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97644 | 1.3218 | 23.7585 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0687 | 0.053277 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97644 | 1.3218 | 1074 | 1321.812 | 0.97644 | 1.096 | 0.0053 | 23.7585
1.075 | 1.1422 | 0.055605 | 1.101 | 1.1011 | 1.1011 | 1.1011 | 1.3619 | 23.9965 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0697 | 0.053279 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.97645 | 1.3237 | 23.7696 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0697 | 0.053279 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97645 | 1.3237 | 23.7696 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0697 | 0.053279 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97645 | 1.3237 | 1075 | 1323.6742 | 0.97645 | 1.096 | 0.0053 | 23.7696
1.076 | 1.1432 | 0.055607 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3638 | 24.0077 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0707 | 0.053281 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.97646 | 1.3255 | 23.7808 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0707 | 0.053281 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97646 | 1.3255 | 23.7808 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0707 | 0.053281 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97646 | 1.3255 | 1076 | 1325.5373 | 0.97646 | 1.096 | 0.0053 | 23.7808
1.077 | 1.1442 | 0.055609 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3658 | 24.0189 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0717 | 0.053284 | 1.0961 | 1.096 | 1.096 | 1.096 | 0.97646 | 1.3274 | 23.7919 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0717 | 0.053284 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97646 | 1.3274 | 23.7919 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0717 | 0.053284 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97646 | 1.3274 | 1077 | 1327.4013 | 0.97646 | 1.096 | 0.0053 | 23.7919
1.078 | 1.1453 | 0.055611 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3677 | 24.0301 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0727 | 0.053286 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97647 | 1.3293 | 23.8031 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0727 | 0.053286 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97647 | 1.3293 | 23.8031 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0727 | 0.053286 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97647 | 1.3293 | 1078 | 1329.2662 | 0.97647 | 1.096 | 0.0053 | 23.8031
1.079 | 1.1463 | 0.055613 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3696 | 24.0412 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0737 | 0.053289 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97648 | 1.3311 | 23.8142 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0737 | 0.053289 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97648 | 1.3311 | 23.8142 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0737 | 0.053289 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97648 | 1.3311 | 1079 | 1331.1319 | 0.97648 | 1.096 | 0.0053 | 23.8142
1.08 | 1.1474 | 0.055615 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3715 | 24.0524 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0747 | 0.053291 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97648 | 1.333 | 23.8253 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0747 | 0.053291 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97648 | 1.333 | 23.8253 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0747 | 0.053291 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97648 | 1.333 | 1080 | 1332.9985 | 0.97648 | 1.096 | 0.0053 | 23.8253
1.081 | 1.1484 | 0.055617 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3734 | 24.0636 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0757 | 0.053294 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97649 | 1.3349 | 23.8364 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0757 | 0.053294 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97649 | 1.3349 | 23.8364 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0757 | 0.053294 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97649 | 1.3349 | 1081 | 1334.866 | 0.97649 | 1.096 | 0.0053 | 23.8364
1.082 | 1.1494 | 0.055619 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3753 | 24.0747 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0767 | 0.053296 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.9765 | 1.3367 | 23.8476 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0767 | 0.053296 | 1.096 | 1.096 | 1.096 | 1.096 | 0.9765 | 1.3367 | 23.8476 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0767 | 0.053296 | 1.096 | 1.096 | 1.096 | 1.096 | 0.9765 | 1.3367 | 1082 | 1336.7343 | 0.9765 | 1.096 | 0.0053 | 23.8476
1.083 | 1.1505 | 0.055621 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3772 | 24.0859 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0777 | 0.053299 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.9765 | 1.3386 | 23.8587 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0777 | 0.053299 | 1.096 | 1.096 | 1.096 | 1.096 | 0.9765 | 1.3386 | 23.8587 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0777 | 0.053299 | 1.096 | 1.096 | 1.096 | 1.096 | 0.9765 | 1.3386 | 1083 | 1338.6035 | 0.9765 | 1.096 | 0.0053 | 23.8587
1.084 | 1.1515 | 0.055623 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3791 | 24.097 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0787 | 0.053301 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97651 | 1.3405 | 23.8698 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0787 | 0.053301 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97651 | 1.3405 | 23.8698 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0787 | 0.053301 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97651 | 1.3405 | 1084 | 1340.4736 | 0.97651 | 1.096 | 0.0053 | 23.8698
1.085 | 1.1526 | 0.055625 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.381 | 24.1082 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0797 | 0.053304 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97652 | 1.3423 | 23.8809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0797 | 0.053304 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97652 | 1.3423 | 23.8809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0797 | 0.053304 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97652 | 1.3423 | 1085 | 1342.3446 | 0.97652 | 1.096 | 0.0053 | 23.8809
1.086 | 1.1536 | 0.055627 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.383 | 24.1193 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0807 | 0.053306 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97652 | 1.3442 | 23.892 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0807 | 0.053306 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97652 | 1.3442 | 23.892 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0807 | 0.053306 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97652 | 1.3442 | 1086 | 1344.2164 | 0.97652 | 1.096 | 0.0053 | 23.892
1.087 | 1.1547 | 0.055629 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3849 | 24.1305 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0817 | 0.053308 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97653 | 1.3461 | 23.9031 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0817 | 0.053308 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97653 | 1.3461 | 23.9031 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0817 | 0.053308 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97653 | 1.3461 | 1087 | 1346.0891 | 0.97653 | 1.096 | 0.0053 | 23.9031
1.088 | 1.1557 | 0.055631 | 1.1011 | 1.1011 | 1.1011 | 1.1011 | 1.3868 | 24.1416 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0827 | 0.053311 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97654 | 1.348 | 23.9141 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0827 | 0.053311 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97654 | 1.348 | 23.9141 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0827 | 0.053311 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97654 | 1.348 | 1088 | 1347.9627 | 0.97654 | 1.096 | 0.0053 | 23.9141
1.089 | 1.1567 | 0.055633 | 1.1011 | 1.1011 | 1.1012 | 1.1012 | 1.3887 | 24.1527 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0837 | 0.053313 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97654 | 1.3498 | 23.9252 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0837 | 0.053313 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97654 | 1.3498 | 23.9252 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0837 | 0.053313 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97654 | 1.3498 | 1089 | 1349.8371 | 0.97654 | 1.096 | 0.0053 | 23.9252
1.09 | 1.1578 | 0.055635 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.3906 | 24.1638 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0847 | 0.053316 | 1.0962 | 1.096 | 1.096 | 1.096 | 0.97655 | 1.3517 | 23.9363 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0847 | 0.053316 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97655 | 1.3517 | 23.9363 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0847 | 0.053316 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97655 | 1.3517 | 1090 | 1351.7124 | 0.97655 | 1.096 | 0.0053 | 23.9363
1.091 | 1.1588 | 0.055637 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.3925 | 24.175 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0857 | 0.053318 | 1.0962 | 1.0961 | 1.096 | 1.096 | 0.97656 | 1.3536 | 23.9474 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0857 | 0.053318 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97656 | 1.3536 | 23.9474 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0857 | 0.053318 | 1.096 | 1.096 | 1.096 | 1.096 | 0.97656 | 1.3536 | 1091 | 1353.5886 | 0.97656 | 1.096 | 0.0053 | 23.9474
1.092 | 1.1599 | 0.055639 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.3945 | 24.1861 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0867 | 0.053321 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.97656 | 1.3555 | 23.9584 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0867 | 0.053321 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97656 | 1.3555 | 23.9584 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0867 | 0.053321 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97656 | 1.3555 | 1092 | 1355.4656 | 0.97656 | 1.0961 | 0.0053 | 23.9584
1.093 | 1.1609 | 0.055641 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.3964 | 24.1972 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0877 | 0.053323 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.97657 | 1.3573 | 23.9695 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0877 | 0.053323 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97657 | 1.3573 | 23.9695 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0877 | 0.053323 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97657 | 1.3573 | 1093 | 1357.3436 | 0.97657 | 1.0961 | 0.0053 | 23.9695
1.094 | 1.1619 | 0.055643 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.3983 | 24.2083 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0887 | 0.053325 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.97658 | 1.3592 | 23.9805 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0887 | 0.053325 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97658 | 1.3592 | 23.9805 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0887 | 0.053325 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97658 | 1.3592 | 1094 | 1359.2223 | 0.97658 | 1.0961 | 0.0053 | 23.9805
1.095 | 1.163 | 0.055645 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.4002 | 24.2194 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0897 | 0.053328 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.97658 | 1.3611 | 23.9916 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0897 | 0.053328 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97658 | 1.3611 | 23.9916 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0897 | 0.053328 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97658 | 1.3611 | 1095 | 1361.102 | 0.97658 | 1.0961 | 0.0053 | 23.9916
1.096 | 1.164 | 0.055647 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.4022 | 24.2305 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0907 | 0.05333 | 1.0962 | 1.0961 | 1.0961 | 1.0961 | 0.97659 | 1.363 | 24.0026 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0907 | 0.05333 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97659 | 1.363 | 24.0026 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0907 | 0.05333 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97659 | 1.363 | 1096 | 1362.9825 | 0.97659 | 1.0961 | 0.0053 | 24.0026
1.097 | 1.1651 | 0.055649 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.4041 | 24.2415 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0917 | 0.053332 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97659 | 1.3649 | 24.0137 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0917 | 0.053332 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97659 | 1.3649 | 24.0137 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0917 | 0.053332 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97659 | 1.3649 | 1097 | 1364.8639 | 0.97659 | 1.0961 | 0.0053 | 24.0137
1.098 | 1.1661 | 0.055651 | 1.1011 | 1.1012 | 1.1012 | 1.1012 | 1.406 | 24.2526 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0927 | 0.053335 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.9766 | 1.3667 | 24.0247 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0927 | 0.053335 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.9766 | 1.3667 | 24.0247 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0927 | 0.053335 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.9766 | 1.3667 | 1098 | 1366.7461 | 0.9766 | 1.0961 | 0.0053 | 24.0247
1.099 | 1.1671 | 0.055653 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4079 | 24.2637 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0937 | 0.053337 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97661 | 1.3686 | 24.0357 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0937 | 0.053337 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97661 | 1.3686 | 24.0357 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0937 | 0.053337 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97661 | 1.3686 | 1099 | 1368.6292 | 0.97661 | 1.0961 | 0.0053 | 24.0357
1.1 | 1.1682 | 0.055655 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4099 | 24.2748 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0947 | 0.05334 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97661 | 1.3705 | 24.0468 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0947 | 0.05334 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97661 | 1.3705 | 24.0468 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0947 | 0.05334 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97661 | 1.3705 | 1100 | 1370.5132 | 0.97661 | 1.0961 | 0.0053 | 24.0468
1.101 | 1.1692 | 0.055657 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4118 | 24.2858 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0957 | 0.053342 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97662 | 1.3724 | 24.0578 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0957 | 0.053342 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97662 | 1.3724 | 24.0578 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0957 | 0.053342 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97662 | 1.3724 | 1101 | 1372.398 | 0.97662 | 1.0961 | 0.0053 | 24.0578
1.102 | 1.1703 | 0.055659 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4137 | 24.2969 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0967 | 0.053344 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97663 | 1.3743 | 24.0688 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0967 | 0.053344 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97663 | 1.3743 | 24.0688 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0967 | 0.053344 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97663 | 1.3743 | 1102 | 1374.2837 | 0.97663 | 1.0961 | 0.0053 | 24.0688
1.103 | 1.1713 | 0.055661 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4157 | 24.3079 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0977 | 0.053347 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97663 | 1.3762 | 24.0798 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0977 | 0.053347 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97663 | 1.3762 | 24.0798 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0977 | 0.053347 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97663 | 1.3762 | 1103 | 1376.1703 | 0.97663 | 1.0961 | 0.0053 | 24.0798
1.104 | 1.1724 | 0.055663 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4176 | 24.319 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0987 | 0.053349 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97664 | 1.3781 | 24.0908 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0987 | 0.053349 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97664 | 1.3781 | 24.0908 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0987 | 0.053349 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97664 | 1.3781 | 1104 | 1378.0577 | 0.97664 | 1.0961 | 0.0053 | 24.0908
1.105 | 1.1734 | 0.055665 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4195 | 24.33 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0997 | 0.053351 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97665 | 1.3799 | 24.1018 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0997 | 0.053351 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97665 | 1.3799 | 24.1018 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.0997 | 0.053351 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97665 | 1.3799 | 1105 | 1379.946 | 0.97665 | 1.0961 | 0.0053 | 24.1018
1.106 | 1.1744 | 0.055667 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4215 | 24.3411 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1007 | 0.053354 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97665 | 1.3818 | 24.1128 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1007 | 0.053354 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97665 | 1.3818 | 24.1128 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1007 | 0.053354 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97665 | 1.3818 | 1106 | 1381.8351 | 0.97665 | 1.0961 | 0.0053 | 24.1128
1.107 | 1.1755 | 0.055669 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4234 | 24.3521 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1017 | 0.053356 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97666 | 1.3837 | 24.1238 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1017 | 0.053356 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97666 | 1.3837 | 24.1238 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1017 | 0.053356 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97666 | 1.3837 | 1107 | 1383.7251 | 0.97666 | 1.0961 | 0.0053 | 24.1238
1.108 | 1.1765 | 0.055671 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4253 | 24.3631 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1027 | 0.053358 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97667 | 1.3856 | 24.1348 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1027 | 0.053358 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97667 | 1.3856 | 24.1348 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1027 | 0.053358 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97667 | 1.3856 | 1108 | 1385.616 | 0.97667 | 1.0961 | 0.0053 | 24.1348
1.109 | 1.1776 | 0.055673 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4273 | 24.3742 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1037 | 0.053361 | 1.0963 | 1.0961 | 1.0961 | 1.0961 | 0.97667 | 1.3875 | 24.1458 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1037 | 0.053361 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97667 | 1.3875 | 24.1457 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1037 | 0.053361 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97667 | 1.3875 | 1109 | 1387.5077 | 0.97667 | 1.0961 | 0.0053 | 24.1457
1.11 | 1.1786 | 0.055675 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4292 | 24.3852 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1047 | 0.053363 | 1.0963 | 1.0962 | 1.0961 | 1.0961 | 0.97668 | 1.3894 | 24.1567 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1047 | 0.053363 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97668 | 1.3894 | 24.1567 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1047 | 0.053363 | 1.0961 | 1.0961 | 1.0961 | 1.0961 | 0.97668 | 1.3894 | 1110 | 1389.4003 | 0.97668 | 1.0961 | 0.0053 | 24.1567
1.111 | 1.1796 | 0.055677 | 1.1012 | 1.1012 | 1.1012 | 1.1012 | 1.4311 | 24.3962 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1057 | 0.053365 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.97668 | 1.3913 | 24.1677 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1057 | 0.053365 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97668 | 1.3913 | 24.1677 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1057 | 0.053365 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97668 | 1.3913 | 1111 | 1391.2938 | 0.97668 | 1.0962 | 0.0053 | 24.1677
1.112 | 1.1807 | 0.055679 | 1.1012 | 1.1012 | 1.1013 | 1.1013 | 1.4331 | 24.4072 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1067 | 0.053368 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.97669 | 1.3932 | 24.1787 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1067 | 0.053368 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97669 | 1.3932 | 24.1787 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1067 | 0.053368 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97669 | 1.3932 | 1112 | 1393.1881 | 0.97669 | 1.0962 | 0.0053 | 24.1787
1.113 | 1.1817 | 0.055681 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.435 | 24.4182 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1077 | 0.05337 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.9767 | 1.3951 | 24.1896 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1077 | 0.05337 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9767 | 1.3951 | 24.1896 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1077 | 0.05337 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9767 | 1.3951 | 1113 | 1395.0833 | 0.9767 | 1.0962 | 0.0053 | 24.1896
1.114 | 1.1828 | 0.055683 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4369 | 24.4292 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1087 | 0.053372 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.9767 | 1.397 | 24.2006 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1087 | 0.053372 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9767 | 1.397 | 24.2006 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1087 | 0.053372 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9767 | 1.397 | 1114 | 1396.9793 | 0.9767 | 1.0962 | 0.0053 | 24.2006
1.115 | 1.1838 | 0.055685 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4389 | 24.4402 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1097 | 0.053375 | 1.0963 | 1.0962 | 1.0962 | 1.0962 | 0.97671 | 1.3989 | 24.2115 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1097 | 0.053375 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97671 | 1.3989 | 24.2115 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1097 | 0.053375 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97671 | 1.3989 | 1115 | 1398.8762 | 0.97671 | 1.0962 | 0.0053 | 24.2115
1.116 | 1.1848 | 0.055687 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4408 | 24.4512 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1107 | 0.053377 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97672 | 1.4008 | 24.2225 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1107 | 0.053377 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97672 | 1.4008 | 24.2225 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1107 | 0.053377 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97672 | 1.4008 | 1116 | 1400.774 | 0.97672 | 1.0962 | 0.0053 | 24.2225
1.117 | 1.1859 | 0.055688 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4428 | 24.4622 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1117 | 0.053379 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97672 | 1.4027 | 24.2334 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1117 | 0.053379 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97672 | 1.4027 | 24.2334 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1117 | 0.053379 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97672 | 1.4027 | 1117 | 1402.6726 | 0.97672 | 1.0962 | 0.0053 | 24.2334
1.118 | 1.1869 | 0.05569 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4447 | 24.4731 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1127 | 0.053382 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97673 | 1.4046 | 24.2443 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1127 | 0.053382 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97673 | 1.4046 | 24.2443 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1127 | 0.053382 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97673 | 1.4046 | 1118 | 1404.572 | 0.97673 | 1.0962 | 0.0053 | 24.2443
1.119 | 1.188 | 0.055692 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4467 | 24.4841 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1137 | 0.053384 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97673 | 1.4065 | 24.2553 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1137 | 0.053384 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97673 | 1.4065 | 24.2553 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1137 | 0.053384 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97673 | 1.4065 | 1119 | 1406.4724 | 0.97673 | 1.0962 | 0.0053 | 24.2553
1.12 | 1.189 | 0.055694 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4486 | 24.4951 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1147 | 0.053386 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97674 | 1.4084 | 24.2662 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1147 | 0.053386 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97674 | 1.4084 | 24.2662 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1147 | 0.053386 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97674 | 1.4084 | 1120 | 1408.3735 | 0.97674 | 1.0962 | 0.0053 | 24.2662
1.121 | 1.1901 | 0.055696 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4506 | 24.506 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1157 | 0.053389 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97675 | 1.4103 | 24.2771 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1157 | 0.053389 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97675 | 1.4103 | 24.2771 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1157 | 0.053389 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97675 | 1.4103 | 1121 | 1410.2756 | 0.97675 | 1.0962 | 0.0053 | 24.2771
1.122 | 1.1911 | 0.055698 | 1.1012 | 1.1013 | 1.1013 | 1.1013 | 1.4525 | 24.517 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1167 | 0.053391 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97675 | 1.4122 | 24.288 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1167 | 0.053391 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97675 | 1.4122 | 24.288 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1167 | 0.053391 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97675 | 1.4122 | 1122 | 1412.1785 | 0.97675 | 1.0962 | 0.0053 | 24.288
1.123 | 1.1921 | 0.0557 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4544 | 24.528 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1177 | 0.053393 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97676 | 1.4141 | 24.2989 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1177 | 0.053393 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97676 | 1.4141 | 24.2989 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1177 | 0.053393 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97676 | 1.4141 | 1123 | 1414.0822 | 0.97676 | 1.0962 | 0.0053 | 24.2989
1.124 | 1.1932 | 0.055702 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4564 | 24.5389 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1187 | 0.053395 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97677 | 1.416 | 24.3098 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1187 | 0.053395 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97677 | 1.416 | 24.3098 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1187 | 0.053395 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97677 | 1.416 | 1124 | 1415.9868 | 0.97677 | 1.0962 | 0.0053 | 24.3098
1.125 | 1.1942 | 0.055704 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4583 | 24.5499 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1197 | 0.053398 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97677 | 1.4179 | 24.3207 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1197 | 0.053398 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97677 | 1.4179 | 24.3207 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1197 | 0.053398 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97677 | 1.4179 | 1125 | 1417.8923 | 0.97677 | 1.0962 | 0.0053 | 24.3207
1.126 | 1.1953 | 0.055706 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4603 | 24.5608 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1207 | 0.0534 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97678 | 1.4198 | 24.3316 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1207 | 0.0534 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97678 | 1.4198 | 24.3316 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1207 | 0.0534 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97678 | 1.4198 | 1126 | 1419.7986 | 0.97678 | 1.0962 | 0.0053 | 24.3316
1.127 | 1.1963 | 0.055708 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4622 | 24.5717 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1217 | 0.053402 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97678 | 1.4217 | 24.3425 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1217 | 0.053402 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97678 | 1.4217 | 24.3425 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1217 | 0.053402 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97678 | 1.4217 | 1127 | 1421.7057 | 0.97678 | 1.0962 | 0.0053 | 24.3425
1.128 | 1.1973 | 0.055709 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4642 | 24.5827 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1227 | 0.053404 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.97679 | 1.4236 | 24.3534 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1227 | 0.053404 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97679 | 1.4236 | 24.3534 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1227 | 0.053404 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.97679 | 1.4236 | 1128 | 1423.6138 | 0.97679 | 1.0962 | 0.0053 | 24.3534
1.129 | 1.1984 | 0.055711 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4662 | 24.5936 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1237 | 0.053407 | 1.0964 | 1.0962 | 1.0962 | 1.0962 | 0.9768 | 1.4255 | 24.3643 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1237 | 0.053407 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9768 | 1.4255 | 24.3643 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1237 | 0.053407 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9768 | 1.4255 | 1129 | 1425.5226 | 0.9768 | 1.0962 | 0.0053 | 24.3643
1.13 | 1.1994 | 0.055713 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4681 | 24.6045 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1247 | 0.053409 | 1.0964 | 1.0963 | 1.0962 | 1.0962 | 0.9768 | 1.4274 | 24.3752 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1247 | 0.053409 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9768 | 1.4274 | 24.3752 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1247 | 0.053409 | 1.0962 | 1.0962 | 1.0962 | 1.0962 | 0.9768 | 1.4274 | 1130 | 1427.4324 | 0.9768 | 1.0962 | 0.0053 | 24.3752
1.131 | 1.2005 | 0.055715 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4701 | 24.6154 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1257 | 0.053411 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.97681 | 1.4293 | 24.386 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1257 | 0.053411 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97681 | 1.4293 | 24.386 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1257 | 0.053411 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97681 | 1.4293 | 1131 | 1429.3429 | 0.97681 | 1.0963 | 0.0053 | 24.386
1.132 | 1.2015 | 0.055717 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.472 | 24.6263 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1267 | 0.053413 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.97681 | 1.4313 | 24.3969 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1267 | 0.053413 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97681 | 1.4313 | 24.3969 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1267 | 0.053413 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97681 | 1.4313 | 1132 | 1431.2544 | 0.97681 | 1.0963 | 0.0053 | 24.3969
1.133 | 1.2025 | 0.055719 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.474 | 24.6372 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1277 | 0.053416 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.97682 | 1.4332 | 24.4078 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1277 | 0.053416 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97682 | 1.4332 | 24.4078 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1277 | 0.053416 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97682 | 1.4332 | 1133 | 1433.1667 | 0.97682 | 1.0963 | 0.0053 | 24.4078
1.134 | 1.2036 | 0.055721 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4759 | 24.6481 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1287 | 0.053418 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.97683 | 1.4351 | 24.4186 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1287 | 0.053418 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97683 | 1.4351 | 24.4186 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1287 | 0.053418 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97683 | 1.4351 | 1134 | 1435.0798 | 0.97683 | 1.0963 | 0.0053 | 24.4186
1.135 | 1.2046 | 0.055723 | 1.1013 | 1.1013 | 1.1013 | 1.1013 | 1.4779 | 24.659 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1297 | 0.05342 | 1.0964 | 1.0963 | 1.0963 | 1.0963 | 0.97683 | 1.437 | 24.4295 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1297 | 0.05342 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97683 | 1.437 | 24.4295 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1297 | 0.05342 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97683 | 1.437 | 1135 | 1436.9938 | 0.97683 | 1.0963 | 0.0053 | 24.4295
1.136 | 1.2057 | 0.055724 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4798 | 24.6699 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1307 | 0.053422 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97684 | 1.4389 | 24.4403 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1307 | 0.053422 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97684 | 1.4389 | 24.4403 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1307 | 0.053422 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97684 | 1.4389 | 1136 | 1438.9086 | 0.97684 | 1.0963 | 0.0053 | 24.4403
1.137 | 1.2067 | 0.055726 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4818 | 24.6808 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1317 | 0.053425 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97685 | 1.4408 | 24.4511 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1317 | 0.053425 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97685 | 1.4408 | 24.4511 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1317 | 0.053425 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97685 | 1.4408 | 1137 | 1440.8243 | 0.97685 | 1.0963 | 0.0053 | 24.4511
1.138 | 1.2078 | 0.055728 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4838 | 24.6917 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1327 | 0.053427 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97685 | 1.4427 | 24.462 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1327 | 0.053427 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97685 | 1.4427 | 24.462 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1327 | 0.053427 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97685 | 1.4427 | 1138 | 1442.7408 | 0.97685 | 1.0963 | 0.0053 | 24.462
1.139 | 1.2088 | 0.05573 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4857 | 24.7026 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1337 | 0.053429 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97686 | 1.4447 | 24.4728 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1337 | 0.053429 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97686 | 1.4447 | 24.4728 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1337 | 0.053429 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97686 | 1.4447 | 1139 | 1444.6582 | 0.97686 | 1.0963 | 0.0053 | 24.4728
1.14 | 1.2098 | 0.055732 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4877 | 24.7135 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1347 | 0.053431 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97686 | 1.4466 | 24.4836 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1347 | 0.053431 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97686 | 1.4466 | 24.4836 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1347 | 0.053431 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97686 | 1.4466 | 1140 | 1446.5764 | 0.97686 | 1.0963 | 0.0053 | 24.4836
1.141 | 1.2109 | 0.055734 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4897 | 24.7243 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1357 | 0.053433 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97687 | 1.4485 | 24.4945 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1357 | 0.053433 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97687 | 1.4485 | 24.4945 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1357 | 0.053433 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97687 | 1.4485 | 1141 | 1448.4955 | 0.97687 | 1.0963 | 0.0053 | 24.4945
1.142 | 1.2119 | 0.055736 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4916 | 24.7352 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1367 | 0.053436 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97688 | 1.4504 | 24.5053 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1367 | 0.053436 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97688 | 1.4504 | 24.5053 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1367 | 0.053436 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97688 | 1.4504 | 1142 | 1450.4155 | 0.97688 | 1.0963 | 0.0053 | 24.5053
1.143 | 1.213 | 0.055737 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4936 | 24.746 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1377 | 0.053438 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97688 | 1.4523 | 24.5161 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1377 | 0.053438 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97688 | 1.4523 | 24.5161 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1377 | 0.053438 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97688 | 1.4523 | 1143 | 1452.3362 | 0.97688 | 1.0963 | 0.0053 | 24.5161
1.144 | 1.214 | 0.055739 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4956 | 24.7569 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1387 | 0.05344 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97689 | 1.4543 | 24.5269 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1387 | 0.05344 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97689 | 1.4543 | 24.5269 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1387 | 0.05344 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97689 | 1.4543 | 1144 | 1454.2579 | 0.97689 | 1.0963 | 0.0053 | 24.5269
1.145 | 1.215 | 0.055741 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4975 | 24.7677 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1397 | 0.053442 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97689 | 1.4562 | 24.5377 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1397 | 0.053442 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97689 | 1.4562 | 24.5377 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1397 | 0.053442 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97689 | 1.4562 | 1145 | 1456.1803 | 0.97689 | 1.0963 | 0.0053 | 24.5377
1.146 | 1.2161 | 0.055743 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.4995 | 24.7786 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1407 | 0.053444 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.9769 | 1.4581 | 24.5485 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1407 | 0.053444 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.9769 | 1.4581 | 24.5485 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1407 | 0.053444 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.9769 | 1.4581 | 1146 | 1458.1037 | 0.9769 | 1.0963 | 0.0053 | 24.5485
1.147 | 1.2171 | 0.055745 | 1.1013 | 1.1014 | 1.1014 | 1.1014 | 1.5015 | 24.7894 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1417 | 0.053447 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.9769 | 1.46 | 24.5593 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1417 | 0.053447 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.9769 | 1.46 | 24.5593 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1417 | 0.053447 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.9769 | 1.46 | 1147 | 1460.0278 | 0.9769 | 1.0963 | 0.0053 | 24.5593
1.148 | 1.2182 | 0.055747 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5034 | 24.8003 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1427 | 0.053449 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97691 | 1.462 | 24.5701 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1427 | 0.053449 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97691 | 1.462 | 24.5701 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1427 | 0.053449 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97691 | 1.462 | 1148 | 1461.9528 | 0.97691 | 1.0963 | 0.0053 | 24.5701
1.149 | 1.2192 | 0.055748 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5054 | 24.8111 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1437 | 0.053451 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97692 | 1.4639 | 24.5809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1437 | 0.053451 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97692 | 1.4639 | 24.5809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1437 | 0.053451 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97692 | 1.4639 | 1149 | 1463.8787 | 0.97692 | 1.0963 | 0.0053 | 24.5809
1.15 | 1.2202 | 0.05575 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5074 | 24.8219 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1447 | 0.053453 | 1.0965 | 1.0963 | 1.0963 | 1.0963 | 0.97692 | 1.4658 | 24.5916 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1447 | 0.053453 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97692 | 1.4658 | 24.5916 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1447 | 0.053453 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97692 | 1.4658 | 1150 | 1465.8054 | 0.97692 | 1.0963 | 0.0053 | 24.5916
1.151 | 1.2213 | 0.055752 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5093 | 24.8327 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1457 | 0.053455 | 1.0965 | 1.0964 | 1.0963 | 1.0963 | 0.97693 | 1.4677 | 24.6024 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1457 | 0.053455 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97693 | 1.4677 | 24.6024 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1457 | 0.053455 | 1.0963 | 1.0963 | 1.0963 | 1.0963 | 0.97693 | 1.4677 | 1151 | 1467.733 | 0.97693 | 1.0963 | 0.0053 | 24.6024
1.152 | 1.2223 | 0.055754 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5113 | 24.8435 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1467 | 0.053458 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.97693 | 1.4697 | 24.6132 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1467 | 0.053458 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97693 | 1.4697 | 24.6132 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1467 | 0.053458 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97693 | 1.4697 | 1152 | 1469.6614 | 0.97693 | 1.0964 | 0.0053 | 24.6132
1.153 | 1.2234 | 0.055756 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5133 | 24.8544 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1477 | 0.05346 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.97694 | 1.4716 | 24.624 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1477 | 0.05346 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97694 | 1.4716 | 24.624 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1477 | 0.05346 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97694 | 1.4716 | 1153 | 1471.5906 | 0.97694 | 1.0964 | 0.0053 | 24.624
1.154 | 1.2244 | 0.055758 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5153 | 24.8652 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1487 | 0.053462 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.97695 | 1.4735 | 24.6347 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1487 | 0.053462 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97695 | 1.4735 | 24.6347 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1487 | 0.053462 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97695 | 1.4735 | 1154 | 1473.5207 | 0.97695 | 1.0964 | 0.0053 | 24.6347
1.155 | 1.2255 | 0.055759 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5172 | 24.876 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1497 | 0.053464 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.97695 | 1.4755 | 24.6455 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1497 | 0.053464 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97695 | 1.4755 | 24.6455 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1497 | 0.053464 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97695 | 1.4755 | 1155 | 1475.4516 | 0.97695 | 1.0964 | 0.0053 | 24.6455
1.156 | 1.2265 | 0.055761 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5192 | 24.8868 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1507 | 0.053466 | 1.0965 | 1.0964 | 1.0964 | 1.0964 | 0.97696 | 1.4774 | 24.6562 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1507 | 0.053466 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97696 | 1.4774 | 24.6562 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1507 | 0.053466 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97696 | 1.4774 | 1156 | 1477.3834 | 0.97696 | 1.0964 | 0.0053 | 24.6562
1.157 | 1.2275 | 0.055763 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5212 | 24.8976 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1517 | 0.053468 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97696 | 1.4793 | 24.667 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1517 | 0.053468 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97696 | 1.4793 | 24.667 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1517 | 0.053468 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97696 | 1.4793 | 1157 | 1479.316 | 0.97696 | 1.0964 | 0.0053 | 24.667
1.158 | 1.2286 | 0.055765 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5232 | 24.9083 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1527 | 0.05347 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97697 | 1.4812 | 24.6777 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1527 | 0.05347 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97697 | 1.4812 | 24.6777 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1527 | 0.05347 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97697 | 1.4812 | 1158 | 1481.2494 | 0.97697 | 1.0964 | 0.0053 | 24.6777
1.159 | 1.2296 | 0.055767 | 1.1014 | 1.1014 | 1.1014 | 1.1014 | 1.5251 | 24.9191 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1537 | 0.053473 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97698 | 1.4832 | 24.6885 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1537 | 0.053473 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97698 | 1.4832 | 24.6885 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1537 | 0.053473 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97698 | 1.4832 | 1159 | 1483.1837 | 0.97698 | 1.0964 | 0.0053 | 24.6885
1.16 | 1.2307 | 0.055768 | 1.1014 | 1.1014 | 1.1015 | 1.1015 | 1.5271 | 24.9299 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1547 | 0.053475 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97698 | 1.4851 | 24.6992 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1547 | 0.053475 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97698 | 1.4851 | 24.6992 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1547 | 0.053475 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97698 | 1.4851 | 1160 | 1485.1189 | 0.97698 | 1.0964 | 0.0053 | 24.6992
1.161 | 1.2317 | 0.05577 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.5291 | 24.9407 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1557 | 0.053477 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97699 | 1.4871 | 24.7099 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1557 | 0.053477 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97699 | 1.4871 | 24.7099 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1557 | 0.053477 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97699 | 1.4871 | 1161 | 1487.0549 | 0.97699 | 1.0964 | 0.0053 | 24.7099
1.162 | 1.2327 | 0.055772 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.5311 | 24.9514 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1567 | 0.053479 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97699 | 1.489 | 24.7206 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1567 | 0.053479 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97699 | 1.489 | 24.7206 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1567 | 0.053479 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97699 | 1.489 | 1162 | 1488.9917 | 0.97699 | 1.0964 | 0.0053 | 24.7206
1.163 | 1.2338 | 0.055774 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.5331 | 24.9622 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1577 | 0.053481 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.977 | 1.4909 | 24.7314 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1577 | 0.053481 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.977 | 1.4909 | 24.7314 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1577 | 0.053481 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.977 | 1.4909 | 1163 | 1490.9293 | 0.977 | 1.0964 | 0.0053 | 24.7314
1.164 | 1.2348 | 0.055775 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.5351 | 24.973 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1587 | 0.053483 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.977 | 1.4929 | 24.7421 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1587 | 0.053483 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.977 | 1.4929 | 24.7421 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1587 | 0.053483 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.977 | 1.4929 | 1164 | 1492.8678 | 0.977 | 1.0964 | 0.0053 | 24.7421
1.165 | 1.2359 | 0.055777 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.537 | 24.9837 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1597 | 0.053485 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97701 | 1.4948 | 24.7528 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1597 | 0.053485 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97701 | 1.4948 | 24.7528 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1597 | 0.053485 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97701 | 1.4948 | 1165 | 1494.8072 | 0.97701 | 1.0964 | 0.0053 | 24.7528
1.166 | 1.2369 | 0.055779 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.539 | 24.9945 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1607 | 0.053488 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97702 | 1.4967 | 24.7635 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1607 | 0.053488 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97702 | 1.4967 | 24.7635 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1607 | 0.053488 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97702 | 1.4967 | 1166 | 1496.7474 | 0.97702 | 1.0964 | 0.0053 | 24.7635
1.167 | 1.2379 | 0.055781 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.541 | 25.0052 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1617 | 0.05349 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97702 | 1.4987 | 24.7742 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1617 | 0.05349 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97702 | 1.4987 | 24.7742 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1617 | 0.05349 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97702 | 1.4987 | 1167 | 1498.6884 | 0.97702 | 1.0964 | 0.0053 | 24.7742
1.168 | 1.239 | 0.055783 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.543 | 25.016 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1627 | 0.053492 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97703 | 1.5006 | 24.7849 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1627 | 0.053492 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97703 | 1.5006 | 24.7849 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1627 | 0.053492 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97703 | 1.5006 | 1168 | 1500.6302 | 0.97703 | 1.0964 | 0.0053 | 24.7849
1.169 | 1.24 | 0.055784 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.545 | 25.0267 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1637 | 0.053494 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97703 | 1.5026 | 24.7956 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1637 | 0.053494 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97703 | 1.5026 | 24.7956 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1637 | 0.053494 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97703 | 1.5026 | 1169 | 1502.5729 | 0.97703 | 1.0964 | 0.0053 | 24.7956
1.17 | 1.2411 | 0.055786 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.547 | 25.0374 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1647 | 0.053496 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97704 | 1.5045 | 24.8063 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1647 | 0.053496 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97704 | 1.5045 | 24.8063 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1647 | 0.053496 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97704 | 1.5045 | 1170 | 1504.5165 | 0.97704 | 1.0964 | 0.0053 | 24.8063
1.171 | 1.2421 | 0.055788 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.549 | 25.0482 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1657 | 0.053498 | 1.0966 | 1.0964 | 1.0964 | 1.0964 | 0.97704 | 1.5065 | 24.8169 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1657 | 0.053498 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97704 | 1.5065 | 24.8169 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1657 | 0.053498 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97704 | 1.5065 | 1171 | 1506.4609 | 0.97704 | 1.0964 | 0.0053 | 24.8169
1.172 | 1.2432 | 0.05579 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.551 | 25.0589 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1667 | 0.0535 | 1.0966 | 1.0965 | 1.0964 | 1.0964 | 0.97705 | 1.5084 | 24.8276 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1667 | 0.0535 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97705 | 1.5084 | 24.8276 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1667 | 0.0535 | 1.0964 | 1.0964 | 1.0964 | 1.0964 | 0.97705 | 1.5084 | 1172 | 1508.4061 | 0.97705 | 1.0964 | 0.0053 | 24.8276
1.173 | 1.2442 | 0.055791 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.5529 | 25.0696 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1677 | 0.053502 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.97706 | 1.5104 | 24.8383 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1677 | 0.053502 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97706 | 1.5104 | 24.8383 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1677 | 0.053502 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97706 | 1.5104 | 1173 | 1510.3521 | 0.97706 | 1.0965 | 0.0053 | 24.8383
1.174 | 1.2452 | 0.055793 | 1.1014 | 1.1015 | 1.1015 | 1.1015 | 1.5549 | 25.0803 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1687 | 0.053504 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.97706 | 1.5123 | 24.849 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1687 | 0.053504 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97706 | 1.5123 | 24.849 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1687 | 0.053504 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97706 | 1.5123 | 1174 | 1512.299 | 0.97706 | 1.0965 | 0.0053 | 24.849
1.175 | 1.2463 | 0.055795 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5569 | 25.091 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1697 | 0.053506 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.97707 | 1.5142 | 24.8596 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1697 | 0.053506 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97707 | 1.5142 | 24.8596 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1697 | 0.053506 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97707 | 1.5142 | 1175 | 1514.2467 | 0.97707 | 1.0965 | 0.0053 | 24.8596
1.176 | 1.2473 | 0.055797 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5589 | 25.1017 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1707 | 0.053509 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.97707 | 1.5162 | 24.8703 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1707 | 0.053509 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97707 | 1.5162 | 24.8703 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1707 | 0.053509 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97707 | 1.5162 | 1176 | 1516.1953 | 0.97707 | 1.0965 | 0.0053 | 24.8703
1.177 | 1.2484 | 0.055798 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5609 | 25.1124 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1717 | 0.053511 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.97708 | 1.5181 | 24.8809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1717 | 0.053511 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97708 | 1.5181 | 24.8809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1717 | 0.053511 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97708 | 1.5181 | 1177 | 1518.1447 | 0.97708 | 1.0965 | 0.0053 | 24.8809
1.178 | 1.2494 | 0.0558 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5629 | 25.1231 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1727 | 0.053513 | 1.0966 | 1.0965 | 1.0965 | 1.0965 | 0.97708 | 1.5201 | 24.8916 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1727 | 0.053513 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97708 | 1.5201 | 24.8916 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1727 | 0.053513 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97708 | 1.5201 | 1178 | 1520.0949 | 0.97708 | 1.0965 | 0.0053 | 24.8916
1.179 | 1.2504 | 0.055802 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5649 | 25.1338 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1737 | 0.053515 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97709 | 1.522 | 24.9022 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1737 | 0.053515 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97709 | 1.522 | 24.9022 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1737 | 0.053515 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97709 | 1.522 | 1179 | 1522.046 | 0.97709 | 1.0965 | 0.0053 | 24.9022
1.18 | 1.2515 | 0.055804 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5669 | 25.1445 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1747 | 0.053517 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.9771 | 1.524 | 24.9129 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1747 | 0.053517 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.9771 | 1.524 | 24.9129 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1747 | 0.053517 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.9771 | 1.524 | 1180 | 1523.9979 | 0.9771 | 1.0965 | 0.0053 | 24.9129
1.181 | 1.2525 | 0.055805 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5689 | 25.1552 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1757 | 0.053519 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.9771 | 1.526 | 24.9235 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1757 | 0.053519 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.9771 | 1.526 | 24.9235 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1757 | 0.053519 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.9771 | 1.526 | 1181 | 1525.9506 | 0.9771 | 1.0965 | 0.0053 | 24.9235
1.182 | 1.2536 | 0.055807 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5709 | 25.1659 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1767 | 0.053521 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97711 | 1.5279 | 24.9341 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1767 | 0.053521 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97711 | 1.5279 | 24.9341 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1767 | 0.053521 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97711 | 1.5279 | 1182 | 1527.9042 | 0.97711 | 1.0965 | 0.0053 | 24.9341
1.183 | 1.2546 | 0.055809 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5729 | 25.1765 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1777 | 0.053523 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97711 | 1.5299 | 24.9448 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1777 | 0.053523 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97711 | 1.5299 | 24.9448 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1777 | 0.053523 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97711 | 1.5299 | 1183 | 1529.8586 | 0.97711 | 1.0965 | 0.0053 | 24.9448
1.184 | 1.2556 | 0.05581 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5749 | 25.1872 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1787 | 0.053525 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97712 | 1.5318 | 24.9554 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1787 | 0.053525 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97712 | 1.5318 | 24.9554 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1787 | 0.053525 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97712 | 1.5318 | 1184 | 1531.8138 | 0.97712 | 1.0965 | 0.0053 | 24.9554
1.185 | 1.2567 | 0.055812 | 1.1015 | 1.1015 | 1.1015 | 1.1015 | 1.5769 | 25.1979 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1797 | 0.053527 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97712 | 1.5338 | 24.966 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1797 | 0.053527 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97712 | 1.5338 | 24.966 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1797 | 0.053527 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97712 | 1.5338 | 1185 | 1533.7698 | 0.97712 | 1.0965 | 0.0053 | 24.966
1.186 | 1.2577 | 0.055814 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5789 | 25.2085 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1807 | 0.053529 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97713 | 1.5357 | 24.9766 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1807 | 0.053529 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97713 | 1.5357 | 24.9766 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1807 | 0.053529 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97713 | 1.5357 | 1186 | 1535.7267 | 0.97713 | 1.0965 | 0.0053 | 24.9766
1.187 | 1.2588 | 0.055816 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5809 | 25.2192 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1817 | 0.053531 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97713 | 1.5377 | 24.9872 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1817 | 0.053531 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97713 | 1.5377 | 24.9872 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1817 | 0.053531 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97713 | 1.5377 | 1187 | 1537.6845 | 0.97713 | 1.0965 | 0.0053 | 24.9872
1.188 | 1.2598 | 0.055817 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5829 | 25.2298 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1827 | 0.053533 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97714 | 1.5396 | 24.9978 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1827 | 0.053533 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97714 | 1.5396 | 24.9978 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1827 | 0.053533 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97714 | 1.5396 | 1188 | 1539.643 | 0.97714 | 1.0965 | 0.0053 | 24.9978
1.189 | 1.2609 | 0.055819 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5849 | 25.2405 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1837 | 0.053535 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97715 | 1.5416 | 25.0084 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1837 | 0.053535 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97715 | 1.5416 | 25.0084 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1837 | 0.053535 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97715 | 1.5416 | 1189 | 1541.6024 | 0.97715 | 1.0965 | 0.0053 | 25.0084
1.19 | 1.2619 | 0.055821 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5869 | 25.2511 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1847 | 0.053537 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97715 | 1.5436 | 25.019 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1847 | 0.053537 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97715 | 1.5436 | 25.019 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1847 | 0.053537 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97715 | 1.5436 | 1190 | 1543.5626 | 0.97715 | 1.0965 | 0.0053 | 25.019
1.191 | 1.2629 | 0.055822 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5889 | 25.2617 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1857 | 0.053539 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97716 | 1.5455 | 25.0296 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1857 | 0.053539 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97716 | 1.5455 | 25.0296 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1857 | 0.053539 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97716 | 1.5455 | 1191 | 1545.5237 | 0.97716 | 1.0965 | 0.0053 | 25.0296
1.192 | 1.264 | 0.055824 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5909 | 25.2724 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1867 | 0.053541 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97716 | 1.5475 | 25.0402 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1867 | 0.053541 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97716 | 1.5475 | 25.0402 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1867 | 0.053541 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97716 | 1.5475 | 1192 | 1547.4856 | 0.97716 | 1.0965 | 0.0053 | 25.0402
1.193 | 1.265 | 0.055826 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5929 | 25.283 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1877 | 0.053543 | 1.0967 | 1.0965 | 1.0965 | 1.0965 | 0.97717 | 1.5494 | 25.0508 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1877 | 0.053543 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97717 | 1.5494 | 25.0508 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1877 | 0.053543 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97717 | 1.5494 | 1193 | 1549.4483 | 0.97717 | 1.0965 | 0.0053 | 25.0508
1.194 | 1.2661 | 0.055827 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.5949 | 25.2936 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1887 | 0.053545 | 1.0967 | 1.0966 | 1.0965 | 1.0965 | 0.97717 | 1.5514 | 25.0614 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1887 | 0.053545 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97717 | 1.5514 | 25.0614 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1887 | 0.053545 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97717 | 1.5514 | 1194 | 1551.4118 | 0.97717 | 1.0965 | 0.0053 | 25.0614
1.195 | 1.2671 | 0.055829 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.597 | 25.3042 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1897 | 0.053547 | 1.0967 | 1.0966 | 1.0965 | 1.0965 | 0.97718 | 1.5534 | 25.0719 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1897 | 0.053547 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97718 | 1.5534 | 25.0719 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1897 | 0.053547 | 1.0965 | 1.0965 | 1.0965 | 1.0965 | 0.97718 | 1.5534 | 1195 | 1553.3762 | 0.97718 | 1.0965 | 0.0053 | 25.0719
1.196 | 1.2681 | 0.055831 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.599 | 25.3149 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1907 | 0.05355 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.97718 | 1.5553 | 25.0825 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1907 | 0.05355 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97718 | 1.5553 | 25.0825 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1907 | 0.05355 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97718 | 1.5553 | 1196 | 1555.3414 | 0.97718 | 1.0966 | 0.0053 | 25.0825
1.197 | 1.2692 | 0.055833 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.601 | 25.3255 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1917 | 0.053552 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.97719 | 1.5573 | 25.0931 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1917 | 0.053552 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97719 | 1.5573 | 25.0931 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1917 | 0.053552 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97719 | 1.5573 | 1197 | 1557.3074 | 0.97719 | 1.0966 | 0.0053 | 25.0931
1.198 | 1.2702 | 0.055834 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.603 | 25.3361 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1927 | 0.053554 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.97719 | 1.5593 | 25.1036 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1927 | 0.053554 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97719 | 1.5593 | 25.1036 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1927 | 0.053554 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97719 | 1.5593 | 1198 | 1559.2743 | 0.97719 | 1.0966 | 0.0053 | 25.1036
1.199 | 1.2713 | 0.055836 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.605 | 25.3467 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1937 | 0.053556 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.9772 | 1.5612 | 25.1142 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1937 | 0.053556 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.9772 | 1.5612 | 25.1142 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1937 | 0.053556 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.9772 | 1.5612 | 1199 | 1561.242 | 0.9772 | 1.0966 | 0.0053 | 25.1142
1.2 | 1.2723 | 0.055838 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.607 | 25.3573 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1947 | 0.053558 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.97721 | 1.5632 | 25.1247 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1947 | 0.053558 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97721 | 1.5632 | 25.1247 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1947 | 0.053558 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97721 | 1.5632 | 1200 | 1563.2105 | 0.97721 | 1.0966 | 0.0053 | 25.1247
1.201 | 1.2733 | 0.055839 | 1.1015 | 1.1016 | 1.1016 | 1.1016 | 1.609 | 25.3679 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1957 | 0.05356 | 1.0967 | 1.0966 | 1.0966 | 1.0966 | 0.97721 | 1.5652 | 25.1353 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1957 | 0.05356 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97721 | 1.5652 | 25.1353 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1957 | 0.05356 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97721 | 1.5652 | 1201 | 1565.1798 | 0.97721 | 1.0966 | 0.0053 | 25.1353
1.202 | 1.2744 | 0.055841 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.611 | 25.3785 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1967 | 0.053562 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97722 | 1.5672 | 25.1458 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1967 | 0.053562 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97722 | 1.5672 | 25.1458 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1967 | 0.053562 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97722 | 1.5672 | 1202 | 1567.15 | 0.97722 | 1.0966 | 0.0053 | 25.1458
1.203 | 1.2754 | 0.055843 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6131 | 25.389 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1977 | 0.053564 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97722 | 1.5691 | 25.1564 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1977 | 0.053564 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97722 | 1.5691 | 25.1564 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1977 | 0.053564 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97722 | 1.5691 | 1203 | 1569.121 | 0.97722 | 1.0966 | 0.0053 | 25.1564
1.204 | 1.2765 | 0.055844 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6151 | 25.3996 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1987 | 0.053566 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97723 | 1.5711 | 25.1669 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1987 | 0.053566 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97723 | 1.5711 | 25.1669 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1987 | 0.053566 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97723 | 1.5711 | 1204 | 1571.0928 | 0.97723 | 1.0966 | 0.0053 | 25.1669
1.205 | 1.2775 | 0.055846 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6171 | 25.4102 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1997 | 0.053568 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97723 | 1.5731 | 25.1774 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1997 | 0.053568 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97723 | 1.5731 | 25.1774 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.1997 | 0.053568 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97723 | 1.5731 | 1205 | 1573.0655 | 0.97723 | 1.0966 | 0.0053 | 25.1774
1.206 | 1.2786 | 0.055848 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6191 | 25.4208 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2007 | 0.05357 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97724 | 1.575 | 25.1879 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2007 | 0.05357 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97724 | 1.575 | 25.1879 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2007 | 0.05357 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97724 | 1.575 | 1206 | 1575.0389 | 0.97724 | 1.0966 | 0.0053 | 25.1879
1.207 | 1.2796 | 0.055849 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6211 | 25.4313 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2017 | 0.053571 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97724 | 1.577 | 25.1985 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2017 | 0.053571 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97724 | 1.577 | 25.1985 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2017 | 0.053571 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97724 | 1.577 | 1207 | 1577.0132 | 0.97724 | 1.0966 | 0.0053 | 25.1985
1.208 | 1.2806 | 0.055851 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6232 | 25.4419 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2027 | 0.053573 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97725 | 1.579 | 25.209 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2027 | 0.053573 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97725 | 1.579 | 25.209 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2027 | 0.053573 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97725 | 1.579 | 1208 | 1578.9883 | 0.97725 | 1.0966 | 0.0053 | 25.209
1.209 | 1.2817 | 0.055853 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6252 | 25.4524 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2037 | 0.053575 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97725 | 1.581 | 25.2195 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2037 | 0.053575 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97725 | 1.581 | 25.2195 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2037 | 0.053575 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97725 | 1.581 | 1209 | 1580.9643 | 0.97725 | 1.0966 | 0.0053 | 25.2195
1.21 | 1.2827 | 0.055854 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6272 | 25.463 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2047 | 0.053577 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97726 | 1.5829 | 25.23 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2047 | 0.053577 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97726 | 1.5829 | 25.23 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2047 | 0.053577 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97726 | 1.5829 | 1210 | 1582.9411 | 0.97726 | 1.0966 | 0.0053 | 25.23
1.211 | 1.2838 | 0.055856 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6292 | 25.4735 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2057 | 0.053579 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97726 | 1.5849 | 25.2405 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2057 | 0.053579 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97726 | 1.5849 | 25.2405 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2057 | 0.053579 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97726 | 1.5849 | 1211 | 1584.9187 | 0.97726 | 1.0966 | 0.0053 | 25.2405
1.212 | 1.2848 | 0.055857 | 1.1016 | 1.1016 | 1.1016 | 1.1016 | 1.6312 | 25.4841 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2067 | 0.053581 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97727 | 1.5869 | 25.251 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2067 | 0.053581 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97727 | 1.5869 | 25.251 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2067 | 0.053581 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97727 | 1.5869 | 1212 | 1586.8971 | 0.97727 | 1.0966 | 0.0053 | 25.251
1.213 | 1.2858 | 0.055859 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6333 | 25.4946 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2077 | 0.053583 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97728 | 1.5889 | 25.2615 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2077 | 0.053583 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97728 | 1.5889 | 25.2615 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2077 | 0.053583 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97728 | 1.5889 | 1213 | 1588.8763 | 0.97728 | 1.0966 | 0.0053 | 25.2615
1.214 | 1.2869 | 0.055861 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6353 | 25.5052 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2087 | 0.053585 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97728 | 1.5909 | 25.272 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2087 | 0.053585 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97728 | 1.5909 | 25.272 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2087 | 0.053585 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97728 | 1.5909 | 1214 | 1590.8564 | 0.97728 | 1.0966 | 0.0053 | 25.272
1.215 | 1.2879 | 0.055862 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6373 | 25.5157 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2097 | 0.053587 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97729 | 1.5928 | 25.2825 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2097 | 0.053587 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97729 | 1.5928 | 25.2825 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2097 | 0.053587 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97729 | 1.5928 | 1215 | 1592.8372 | 0.97729 | 1.0966 | 0.0053 | 25.2825
1.216 | 1.289 | 0.055864 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6394 | 25.5262 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2107 | 0.053589 | 1.0968 | 1.0966 | 1.0966 | 1.0966 | 0.97729 | 1.5948 | 25.2929 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2107 | 0.053589 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97729 | 1.5948 | 25.2929 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2107 | 0.053589 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.97729 | 1.5948 | 1216 | 1594.819 | 0.97729 | 1.0966 | 0.0053 | 25.2929
1.217 | 1.29 | 0.055866 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6414 | 25.5367 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2117 | 0.053591 | 1.0968 | 1.0967 | 1.0966 | 1.0966 | 0.9773 | 1.5968 | 25.3034 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2117 | 0.053591 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.9773 | 1.5968 | 25.3034 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2117 | 0.053591 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.9773 | 1.5968 | 1217 | 1596.8015 | 0.9773 | 1.0966 | 0.0053 | 25.3034
1.218 | 1.291 | 0.055867 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6434 | 25.5473 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2127 | 0.053593 | 1.0968 | 1.0967 | 1.0966 | 1.0966 | 0.9773 | 1.5988 | 25.3139 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2127 | 0.053593 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.9773 | 1.5988 | 25.3139 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2127 | 0.053593 | 1.0966 | 1.0966 | 1.0966 | 1.0966 | 0.9773 | 1.5988 | 1218 | 1598.7848 | 0.9773 | 1.0966 | 0.0053 | 25.3139
1.219 | 1.2921 | 0.055869 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6454 | 25.5578 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2137 | 0.053595 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.97731 | 1.6008 | 25.3244 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2137 | 0.053595 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97731 | 1.6008 | 25.3244 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2137 | 0.053595 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97731 | 1.6008 | 1219 | 1600.769 | 0.97731 | 1.0967 | 0.0053 | 25.3244
1.22 | 1.2931 | 0.055871 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6475 | 25.5683 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2147 | 0.053597 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.97731 | 1.6028 | 25.3348 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2147 | 0.053597 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97731 | 1.6028 | 25.3348 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2147 | 0.053597 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97731 | 1.6028 | 1220 | 1602.754 | 0.97731 | 1.0967 | 0.0053 | 25.3348
1.221 | 1.2942 | 0.055872 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6495 | 25.5788 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2157 | 0.053599 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.97732 | 1.6047 | 25.3453 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2157 | 0.053599 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97732 | 1.6047 | 25.3453 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2157 | 0.053599 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97732 | 1.6047 | 1221 | 1604.7398 | 0.97732 | 1.0967 | 0.0053 | 25.3453
1.222 | 1.2952 | 0.055874 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6515 | 25.5893 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2167 | 0.053601 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.97732 | 1.6067 | 25.3557 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2167 | 0.053601 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97732 | 1.6067 | 25.3557 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2167 | 0.053601 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97732 | 1.6067 | 1222 | 1606.7264 | 0.97732 | 1.0967 | 0.0053 | 25.3557
1.223 | 1.2963 | 0.055875 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6536 | 25.5998 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2177 | 0.053603 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.97733 | 1.6087 | 25.3662 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2177 | 0.053603 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97733 | 1.6087 | 25.3662 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2177 | 0.053603 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97733 | 1.6087 | 1223 | 1608.7139 | 0.97733 | 1.0967 | 0.0053 | 25.3662
1.224 | 1.2973 | 0.055877 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6556 | 25.6103 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2187 | 0.053605 | 1.0968 | 1.0967 | 1.0967 | 1.0967 | 0.97733 | 1.6107 | 25.3766 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2187 | 0.053605 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97733 | 1.6107 | 25.3766 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2187 | 0.053605 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97733 | 1.6107 | 1224 | 1610.7021 | 0.97733 | 1.0967 | 0.0053 | 25.3766
1.225 | 1.2983 | 0.055879 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6576 | 25.6208 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2197 | 0.053607 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97734 | 1.6127 | 25.3871 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2197 | 0.053607 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97734 | 1.6127 | 25.3871 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2197 | 0.053607 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97734 | 1.6127 | 1225 | 1612.6912 | 0.97734 | 1.0967 | 0.0053 | 25.3871
1.226 | 1.2994 | 0.05588 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6597 | 25.6312 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2207 | 0.053609 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97734 | 1.6147 | 25.3975 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2207 | 0.053609 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97734 | 1.6147 | 25.3975 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2207 | 0.053609 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97734 | 1.6147 | 1226 | 1614.6811 | 0.97734 | 1.0967 | 0.0053 | 25.3975
1.227 | 1.3004 | 0.055882 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6617 | 25.6417 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2217 | 0.05361 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97735 | 1.6167 | 25.4079 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2217 | 0.05361 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97735 | 1.6167 | 25.4079 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2217 | 0.05361 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97735 | 1.6167 | 1227 | 1616.6719 | 0.97735 | 1.0967 | 0.0053 | 25.4079
1.228 | 1.3015 | 0.055883 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6637 | 25.6522 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2227 | 0.053612 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97735 | 1.6187 | 25.4184 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2227 | 0.053612 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97735 | 1.6187 | 25.4184 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2227 | 0.053612 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97735 | 1.6187 | 1228 | 1618.6634 | 0.97735 | 1.0967 | 0.0053 | 25.4184
1.229 | 1.3025 | 0.055885 | 1.1016 | 1.1017 | 1.1017 | 1.1017 | 1.6658 | 25.6627 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2237 | 0.053614 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97736 | 1.6207 | 25.4288 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2237 | 0.053614 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97736 | 1.6207 | 25.4288 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2237 | 0.053614 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97736 | 1.6207 | 1229 | 1620.6558 | 0.97736 | 1.0967 | 0.0053 | 25.4288
1.23 | 1.3035 | 0.055887 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6678 | 25.6731 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2247 | 0.053616 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97736 | 1.6226 | 25.4392 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2247 | 0.053616 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97736 | 1.6226 | 25.4392 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2247 | 0.053616 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97736 | 1.6226 | 1230 | 1622.6489 | 0.97736 | 1.0967 | 0.0053 | 25.4392
1.231 | 1.3046 | 0.055888 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6699 | 25.6836 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2257 | 0.053618 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97737 | 1.6246 | 25.4496 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2257 | 0.053618 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97737 | 1.6246 | 25.4496 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2257 | 0.053618 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97737 | 1.6246 | 1231 | 1624.6429 | 0.97737 | 1.0967 | 0.0053 | 25.4496
1.232 | 1.3056 | 0.05589 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6719 | 25.6941 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2267 | 0.05362 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97737 | 1.6266 | 25.46 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2267 | 0.05362 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97737 | 1.6266 | 25.46 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2267 | 0.05362 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97737 | 1.6266 | 1232 | 1626.6377 | 0.97737 | 1.0967 | 0.0053 | 25.46
1.233 | 1.3067 | 0.055891 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6739 | 25.7045 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2277 | 0.053622 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97738 | 1.6286 | 25.4705 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2277 | 0.053622 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97738 | 1.6286 | 25.4705 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2277 | 0.053622 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97738 | 1.6286 | 1233 | 1628.6334 | 0.97738 | 1.0967 | 0.0053 | 25.4705
1.234 | 1.3077 | 0.055893 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.676 | 25.715 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2287 | 0.053624 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97738 | 1.6306 | 25.4809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2287 | 0.053624 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97738 | 1.6306 | 25.4809 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2287 | 0.053624 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97738 | 1.6306 | 1234 | 1630.6298 | 0.97738 | 1.0967 | 0.0053 | 25.4809
1.235 | 1.3087 | 0.055895 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.678 | 25.7254 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2297 | 0.053626 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97739 | 1.6326 | 25.4913 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2297 | 0.053626 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97739 | 1.6326 | 25.4913 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2297 | 0.053626 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97739 | 1.6326 | 1235 | 1632.6271 | 0.97739 | 1.0967 | 0.0053 | 25.4913
1.236 | 1.3098 | 0.055896 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6801 | 25.7358 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2307 | 0.053628 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97739 | 1.6346 | 25.5017 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2307 | 0.053628 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97739 | 1.6346 | 25.5017 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2307 | 0.053628 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97739 | 1.6346 | 1236 | 1634.6251 | 0.97739 | 1.0967 | 0.0053 | 25.5017
1.237 | 1.3108 | 0.055898 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6821 | 25.7463 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2317 | 0.05363 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.9774 | 1.6366 | 25.512 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2317 | 0.05363 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.9774 | 1.6366 | 25.512 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2317 | 0.05363 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.9774 | 1.6366 | 1237 | 1636.624 | 0.9774 | 1.0967 | 0.0053 | 25.512
1.238 | 1.3119 | 0.055899 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6842 | 25.7567 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2327 | 0.053631 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.9774 | 1.6386 | 25.5224 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2327 | 0.053631 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.9774 | 1.6386 | 25.5224 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2327 | 0.053631 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.9774 | 1.6386 | 1238 | 1638.6237 | 0.9774 | 1.0967 | 0.0053 | 25.5224
1.239 | 1.3129 | 0.055901 | 1.1017 | 1.1017 | 1.1017 | 1.1017 | 1.6862 | 25.7671 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2337 | 0.053633 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97741 | 1.6406 | 25.5328 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2337 | 0.053633 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97741 | 1.6406 | 25.5328 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2337 | 0.053633 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97741 | 1.6406 | 1239 | 1640.6242 | 0.97741 | 1.0967 | 0.0053 | 25.5328
1.24 | 1.314 | 0.055902 | 1.1017 | 1.1017 | 1.1018 | 1.1018 | 1.6883 | 25.7776 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2347 | 0.053635 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97742 | 1.6426 | 25.5432 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2347 | 0.053635 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97742 | 1.6426 | 25.5432 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2347 | 0.053635 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97742 | 1.6426 | 1240 | 1642.6256 | 0.97742 | 1.0967 | 0.0053 | 25.5432
1.241 | 1.315 | 0.055904 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.6903 | 25.788 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2357 | 0.053637 | 1.0969 | 1.0968 | 1.0967 | 1.0967 | 0.97742 | 1.6446 | 25.5536 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2357 | 0.053637 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97742 | 1.6446 | 25.5536 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2357 | 0.053637 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97742 | 1.6446 | 1241 | 1644.6277 | 0.97742 | 1.0967 | 0.0053 | 25.5536
1.242 | 1.316 | 0.055906 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.6924 | 25.7984 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2367 | 0.053639 | 1.0969 | 1.0968 | 1.0967 | 1.0967 | 0.97743 | 1.6466 | 25.5639 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2367 | 0.053639 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97743 | 1.6466 | 25.5639 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2367 | 0.053639 | 1.0967 | 1.0967 | 1.0967 | 1.0967 | 0.97743 | 1.6466 | 1242 | 1646.6307 | 0.97743 | 1.0967 | 0.0053 | 25.5639
1.243 | 1.3171 | 0.055907 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.6944 | 25.8088 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2377 | 0.053641 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97743 | 1.6486 | 25.5743 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2377 | 0.053641 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97743 | 1.6486 | 25.5743 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2377 | 0.053641 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97743 | 1.6486 | 1243 | 1648.6344 | 0.97743 | 1.0968 | 0.0053 | 25.5743
1.244 | 1.3181 | 0.055909 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.6965 | 25.8192 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2387 | 0.053643 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97744 | 1.6506 | 25.5847 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2387 | 0.053643 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97744 | 1.6506 | 25.5847 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2387 | 0.053643 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97744 | 1.6506 | 1244 | 1650.639 | 0.97744 | 1.0968 | 0.0053 | 25.5847
1.245 | 1.3192 | 0.05591 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.6985 | 25.8296 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2397 | 0.053645 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97744 | 1.6526 | 25.595 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2397 | 0.053645 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97744 | 1.6526 | 25.595 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2397 | 0.053645 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97744 | 1.6526 | 1245 | 1652.6444 | 0.97744 | 1.0968 | 0.0053 | 25.595
1.246 | 1.3202 | 0.055912 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7006 | 25.84 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2407 | 0.053646 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97745 | 1.6547 | 25.6054 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2407 | 0.053646 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97745 | 1.6547 | 25.6054 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2407 | 0.053646 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97745 | 1.6547 | 1246 | 1654.6506 | 0.97745 | 1.0968 | 0.0053 | 25.6054
1.247 | 1.3212 | 0.055913 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7026 | 25.8504 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2417 | 0.053648 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97745 | 1.6567 | 25.6157 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2417 | 0.053648 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97745 | 1.6567 | 25.6157 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2417 | 0.053648 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97745 | 1.6567 | 1247 | 1656.6576 | 0.97745 | 1.0968 | 0.0053 | 25.6157
1.248 | 1.3223 | 0.055915 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7047 | 25.8608 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2427 | 0.05365 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97746 | 1.6587 | 25.6261 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2427 | 0.05365 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97746 | 1.6587 | 25.6261 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2427 | 0.05365 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97746 | 1.6587 | 1248 | 1658.6655 | 0.97746 | 1.0968 | 0.0053 | 25.6261
1.249 | 1.3233 | 0.055917 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7067 | 25.8712 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2437 | 0.053652 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97746 | 1.6607 | 25.6364 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2437 | 0.053652 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97746 | 1.6607 | 25.6364 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2437 | 0.053652 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97746 | 1.6607 | 1249 | 1660.6741 | 0.97746 | 1.0968 | 0.0053 | 25.6364
1.25 | 1.3244 | 0.055918 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7088 | 25.8816 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2447 | 0.053654 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97747 | 1.6627 | 25.6467 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2447 | 0.053654 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97747 | 1.6627 | 25.6467 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2447 | 0.053654 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97747 | 1.6627 | 1250 | 1662.6836 | 0.97747 | 1.0968 | 0.0053 | 25.6467
1.251 | 1.3254 | 0.05592 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7108 | 25.8919 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2457 | 0.053656 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97747 | 1.6647 | 25.6571 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2457 | 0.053656 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97747 | 1.6647 | 25.6571 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2457 | 0.053656 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97747 | 1.6647 | 1251 | 1664.6938 | 0.97747 | 1.0968 | 0.0053 | 25.6571
1.252 | 1.3264 | 0.055921 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7129 | 25.9023 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2467 | 0.053657 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97748 | 1.6667 | 25.6674 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2467 | 0.053657 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97748 | 1.6667 | 25.6674 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2467 | 0.053657 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97748 | 1.6667 | 1252 | 1666.7049 | 0.97748 | 1.0968 | 0.0053 | 25.6674
1.253 | 1.3275 | 0.055923 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7149 | 25.9127 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2477 | 0.053659 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97748 | 1.6687 | 25.6777 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2477 | 0.053659 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97748 | 1.6687 | 25.6777 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2477 | 0.053659 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97748 | 1.6687 | 1253 | 1668.7168 | 0.97748 | 1.0968 | 0.0053 | 25.6777
1.254 | 1.3285 | 0.055924 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.717 | 25.923 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2487 | 0.053661 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97749 | 1.6707 | 25.688 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2487 | 0.053661 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97749 | 1.6707 | 25.688 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2487 | 0.053661 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97749 | 1.6707 | 1254 | 1670.7295 | 0.97749 | 1.0968 | 0.0053 | 25.688
1.255 | 1.3296 | 0.055926 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7191 | 25.9334 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2497 | 0.053663 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97749 | 1.6727 | 25.6984 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2497 | 0.053663 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97749 | 1.6727 | 25.6984 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2497 | 0.053663 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97749 | 1.6727 | 1255 | 1672.7429 | 0.97749 | 1.0968 | 0.0053 | 25.6984
1.256 | 1.3306 | 0.055927 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7211 | 25.9438 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2507 | 0.053665 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.9775 | 1.6748 | 25.7087 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2507 | 0.053665 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.9775 | 1.6748 | 25.7087 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2507 | 0.053665 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.9775 | 1.6748 | 1256 | 1674.7573 | 0.9775 | 1.0968 | 0.0053 | 25.7087
1.257 | 1.3317 | 0.055929 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7232 | 25.9541 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2517 | 0.053667 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.9775 | 1.6768 | 25.719 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2517 | 0.053667 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.9775 | 1.6768 | 25.719 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2517 | 0.053667 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.9775 | 1.6768 | 1257 | 1676.7724 | 0.9775 | 1.0968 | 0.0053 | 25.719
1.258 | 1.3327 | 0.05593 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7252 | 25.9645 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2527 | 0.053669 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97751 | 1.6788 | 25.7293 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2527 | 0.053669 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97751 | 1.6788 | 25.7293 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2527 | 0.053669 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97751 | 1.6788 | 1258 | 1678.7883 | 0.97751 | 1.0968 | 0.0053 | 25.7293
1.259 | 1.3337 | 0.055932 | 1.1017 | 1.1018 | 1.1018 | 1.1018 | 1.7273 | 25.9748 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2537 | 0.05367 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97751 | 1.6808 | 25.7396 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2537 | 0.05367 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97751 | 1.6808 | 25.7396 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2537 | 0.05367 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97751 | 1.6808 | 1259 | 1680.805 | 0.97751 | 1.0968 | 0.0053 | 25.7396
1.26 | 1.3348 | 0.055933 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7294 | 25.9852 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2547 | 0.053672 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6828 | 25.7499 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2547 | 0.053672 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6828 | 25.7499 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2547 | 0.053672 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6828 | 1260 | 1682.8226 | 0.97752 | 1.0968 | 0.0053 | 25.7499
1.261 | 1.3358 | 0.055935 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7314 | 25.9955 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2557 | 0.053674 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6848 | 25.7602 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2557 | 0.053674 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6848 | 25.7602 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2557 | 0.053674 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6848 | 1261 | 1684.8409 | 0.97752 | 1.0968 | 0.0053 | 25.7602
1.262 | 1.3369 | 0.055936 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7335 | 26.0058 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2566 | 0.053634 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.9771 | 1.686 | 25.766 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2567 | 0.053676 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6869 | 25.7704 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2567 | 0.053676 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97752 | 1.6869 | 1262 | 1686.8601 | 0.97752 | 1.0968 | 0.0053 | 25.7704
1.263 | 1.3379 | 0.055938 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7356 | 26.0161 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2576 | 0.053636 | 1.0969 | 1.0967 | 1.0967 | 1.0967 | 0.97711 | 1.688 | 25.7763 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2577 | 0.053678 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97753 | 1.6889 | 25.7807 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2577 | 0.053678 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97753 | 1.6889 | 1263 | 1688.88 | 0.97753 | 1.0968 | 0.0053 | 25.7807
1.264 | 1.3389 | 0.05594 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7376 | 26.0265 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2586 | 0.053637 | 1.0969 | 1.0968 | 1.0967 | 1.0967 | 0.97711 | 1.69 | 25.7866 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2587 | 0.053679 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97753 | 1.6909 | 25.791 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2587 | 0.053679 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97753 | 1.6909 | 1264 | 1690.9008 | 0.97753 | 1.0968 | 0.0053 | 25.791
1.265 | 1.34 | 0.055941 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7397 | 26.0368 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2596 | 0.053639 | 1.0969 | 1.0968 | 1.0967 | 1.0967 | 0.97712 | 1.6921 | 25.7968 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2597 | 0.053681 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97754 | 1.6929 | 25.8013 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2597 | 0.053681 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97754 | 1.6929 | 1265 | 1692.9224 | 0.97754 | 1.0968 | 0.0053 | 25.8013
1.266 | 1.341 | 0.055943 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7418 | 26.0471 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2606 | 0.053641 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97712 | 1.6941 | 25.8071 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2607 | 0.053683 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97754 | 1.6949 | 25.8115 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2607 | 0.053683 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97754 | 1.6949 | 1266 | 1694.9447 | 0.97754 | 1.0968 | 0.0053 | 25.8115
1.267 | 1.3421 | 0.055944 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7438 | 26.0574 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2616 | 0.053643 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97713 | 1.6961 | 25.8174 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2617 | 0.053685 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97755 | 1.697 | 25.8218 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2617 | 0.053685 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97755 | 1.697 | 1267 | 1696.9679 | 0.97755 | 1.0968 | 0.0053 | 25.8218
1.268 | 1.3431 | 0.055946 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.7459 | 26.0677 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2626 | 0.053645 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97713 | 1.6981 | 25.8276 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2627 | 0.053687 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97755 | 1.699 | 25.8321 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2627 | 0.053687 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97755 | 1.699 | 1268 | 1698.9919 | 0.97755 | 1.0969 | 0.0053 | 25.8321
1.269 | 1.3441 | 0.055947 | 1.1018 | 1.1018 | 1.1018 | 1.1018 | 1.748 | 26.078 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2636 | 0.053646 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97714 | 1.7001 | 25.8379 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2637 | 0.053688 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97756 | 1.701 | 25.8423 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2637 | 0.053688 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97756 | 1.701 | 1269 | 1701.0167 | 0.97756 | 1.0969 | 0.0053 | 25.8423
1.27 | 1.3452 | 0.055949 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7501 | 26.0883 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2646 | 0.053648 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97714 | 1.7022 | 25.8482 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2647 | 0.05369 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97756 | 1.703 | 25.8526 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2647 | 0.05369 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97756 | 1.703 | 1270 | 1703.0423 | 0.97756 | 1.0969 | 0.0053 | 25.8526
1.271 | 1.3462 | 0.05595 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7521 | 26.0986 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2656 | 0.05365 | 1.0969 | 1.0968 | 1.0968 | 1.0968 | 0.97715 | 1.7042 | 25.8584 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2657 | 0.053692 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97757 | 1.7051 | 25.8628 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2657 | 0.053692 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97757 | 1.7051 | 1271 | 1705.0687 | 0.97757 | 1.0969 | 0.0053 | 25.8628
1.272 | 1.3473 | 0.055952 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7542 | 26.1089 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2666 | 0.053652 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97715 | 1.7062 | 25.8686 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2667 | 0.053694 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97757 | 1.7071 | 25.8731 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2667 | 0.053694 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97757 | 1.7071 | 1272 | 1707.0959 | 0.97757 | 1.0969 | 0.0053 | 25.8731
1.273 | 1.3483 | 0.055953 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7563 | 26.1192 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2676 | 0.053654 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97716 | 1.7082 | 25.8789 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2677 | 0.053696 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97758 | 1.7091 | 25.8833 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2677 | 0.053696 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97758 | 1.7091 | 1273 | 1709.1239 | 0.97758 | 1.0969 | 0.0053 | 25.8833
1.274 | 1.3494 | 0.055955 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7584 | 26.1295 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2686 | 0.053655 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97716 | 1.7103 | 25.8891 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2687 | 0.053697 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97758 | 1.7112 | 25.8936 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2687 | 0.053697 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97758 | 1.7112 | 1274 | 1711.1527 | 0.97758 | 1.0969 | 0.0053 | 25.8936
1.275 | 1.3504 | 0.055956 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7604 | 26.1398 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2696 | 0.053657 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97717 | 1.7123 | 25.8994 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2697 | 0.053699 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97759 | 1.7132 | 25.9038 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2697 | 0.053699 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97759 | 1.7132 | 1275 | 1713.1823 | 0.97759 | 1.0969 | 0.0053 | 25.9038
1.276 | 1.3514 | 0.055958 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7625 | 26.15 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2706 | 0.053659 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97717 | 1.7143 | 25.9096 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2707 | 0.053701 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97759 | 1.7152 | 25.914 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2707 | 0.053701 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97759 | 1.7152 | 1276 | 1715.2127 | 0.97759 | 1.0969 | 0.0053 | 25.914
1.277 | 1.3525 | 0.055959 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7646 | 26.1603 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2716 | 0.053661 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97718 | 1.7164 | 25.9198 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2717 | 0.053703 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9776 | 1.7172 | 25.9243 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2717 | 0.053703 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9776 | 1.7172 | 1277 | 1717.2439 | 0.9776 | 1.0969 | 0.0053 | 25.9243
1.278 | 1.3535 | 0.05596 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7667 | 26.1706 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2726 | 0.053663 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97718 | 1.7184 | 25.93 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2727 | 0.053705 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9776 | 1.7193 | 25.9345 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2727 | 0.053705 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9776 | 1.7193 | 1278 | 1719.2759 | 0.9776 | 1.0969 | 0.0053 | 25.9345
1.279 | 1.3546 | 0.055962 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7687 | 26.1808 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2736 | 0.053664 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97719 | 1.7204 | 25.9402 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2737 | 0.053706 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97761 | 1.7213 | 25.9447 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2737 | 0.053706 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97761 | 1.7213 | 1279 | 1721.3087 | 0.97761 | 1.0969 | 0.0053 | 25.9447
1.28 | 1.3556 | 0.055963 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7708 | 26.1911 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2746 | 0.053666 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97719 | 1.7225 | 25.9505 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2747 | 0.053708 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97761 | 1.7233 | 25.9549 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2747 | 0.053708 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97761 | 1.7233 | 1280 | 1723.3424 | 0.97761 | 1.0969 | 0.0053 | 25.9549
1.281 | 1.3566 | 0.055965 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7729 | 26.2014 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2756 | 0.053668 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.9772 | 1.7245 | 25.9607 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2757 | 0.05371 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97762 | 1.7254 | 25.9651 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2757 | 0.05371 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97762 | 1.7254 | 1281 | 1725.3768 | 0.97762 | 1.0969 | 0.0053 | 25.9651
1.282 | 1.3577 | 0.055966 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.775 | 26.2116 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2766 | 0.05367 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.9772 | 1.7265 | 25.9709 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2767 | 0.053712 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97762 | 1.7274 | 25.9753 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2767 | 0.053712 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97762 | 1.7274 | 1282 | 1727.412 | 0.97762 | 1.0969 | 0.0053 | 25.9753
1.283 | 1.3587 | 0.055968 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7771 | 26.2219 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2776 | 0.053671 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97721 | 1.7286 | 25.9811 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2777 | 0.053713 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97763 | 1.7294 | 25.9855 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2777 | 0.053713 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97763 | 1.7294 | 1283 | 1729.448 | 0.97763 | 1.0969 | 0.0053 | 25.9855
1.284 | 1.3598 | 0.055969 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7791 | 26.2321 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2786 | 0.053673 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97721 | 1.7306 | 25.9913 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2787 | 0.053715 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97763 | 1.7315 | 25.9957 | 0.0061 | 0.0049 | 0.0053 | 0.64032 | 1.2787 | 0.053715 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97763 | 1.7315 | 1284 | 1731.4848 | 0.97763 | 1.0969 | 0.0053 | 25.9957
1.285 | 1.3608 | 0.055971 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7812 | 26.2423 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2796 | 0.053675 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97722 | 1.7326 | 26.0015 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2796 | 0.053675 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97722 | 1.7326 | 26.0015 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2796 | 0.053675 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97722 | 1.7326 | 1285 | 1732.6328 | 0.97722 | 1.0968 | 0.0054 | 26.0015
1.286 | 1.3618 | 0.055972 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7833 | 26.2526 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2806 | 0.053677 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97722 | 1.7347 | 26.0116 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2806 | 0.053677 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97722 | 1.7347 | 26.0116 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2806 | 0.053677 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97722 | 1.7347 | 1286 | 1734.6704 | 0.97722 | 1.0968 | 0.0054 | 26.0116
1.287 | 1.3629 | 0.055974 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7854 | 26.2628 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2816 | 0.053678 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7367 | 26.0218 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2816 | 0.053678 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7367 | 26.0218 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2816 | 0.053678 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7367 | 1287 | 1736.7087 | 0.97723 | 1.0968 | 0.0054 | 26.0218
1.288 | 1.3639 | 0.055975 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7875 | 26.273 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2826 | 0.05368 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7387 | 26.032 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2826 | 0.05368 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7387 | 26.032 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2826 | 0.05368 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7387 | 1288 | 1738.7478 | 0.97723 | 1.0968 | 0.0054 | 26.032
1.289 | 1.365 | 0.055977 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7896 | 26.2833 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2836 | 0.053682 | 1.097 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7408 | 26.0422 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2836 | 0.053682 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7408 | 26.0422 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2836 | 0.053682 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97723 | 1.7408 | 1289 | 1740.7878 | 0.97723 | 1.0968 | 0.0054 | 26.0422
1.29 | 1.366 | 0.055978 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7917 | 26.2935 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2846 | 0.053684 | 1.097 | 1.0969 | 1.0968 | 1.0968 | 0.97724 | 1.7428 | 26.0524 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2846 | 0.053684 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97724 | 1.7428 | 26.0524 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2846 | 0.053684 | 1.0968 | 1.0968 | 1.0968 | 1.0968 | 0.97724 | 1.7428 | 1290 | 1742.8285 | 0.97724 | 1.0968 | 0.0054 | 26.0524
1.291 | 1.3671 | 0.05598 | 1.1018 | 1.1019 | 1.1019 | 1.1019 | 1.7938 | 26.3037 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2856 | 0.053685 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97724 | 1.7449 | 26.0625 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2856 | 0.053685 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97724 | 1.7449 | 26.0625 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2856 | 0.053685 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97724 | 1.7449 | 1291 | 1744.87 | 0.97724 | 1.0969 | 0.0054 | 26.0625
1.292 | 1.3681 | 0.055981 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.7958 | 26.3139 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2866 | 0.053687 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97725 | 1.7469 | 26.0727 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2866 | 0.053687 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97725 | 1.7469 | 26.0727 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2866 | 0.053687 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97725 | 1.7469 | 1292 | 1746.9124 | 0.97725 | 1.0969 | 0.0054 | 26.0727
1.293 | 1.3691 | 0.055982 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.7979 | 26.3241 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2876 | 0.053689 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97725 | 1.749 | 26.0829 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2876 | 0.053689 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97725 | 1.749 | 26.0829 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2876 | 0.053689 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97725 | 1.749 | 1293 | 1748.9555 | 0.97725 | 1.0969 | 0.0054 | 26.0829
1.294 | 1.3702 | 0.055984 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.8 | 26.3343 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2886 | 0.053691 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97726 | 1.751 | 26.093 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2886 | 0.053691 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97726 | 1.751 | 26.093 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2886 | 0.053691 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97726 | 1.751 | 1294 | 1750.9994 | 0.97726 | 1.0969 | 0.0054 | 26.093
1.295 | 1.3712 | 0.055985 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.8021 | 26.3445 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2896 | 0.053692 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97726 | 1.753 | 26.1032 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2896 | 0.053692 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97726 | 1.753 | 26.1032 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2896 | 0.053692 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97726 | 1.753 | 1295 | 1753.0442 | 0.97726 | 1.0969 | 0.0054 | 26.1032
1.296 | 1.3723 | 0.055987 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.8042 | 26.3547 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2906 | 0.053694 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97727 | 1.7551 | 26.1133 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2906 | 0.053694 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97727 | 1.7551 | 26.1133 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2906 | 0.053694 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97727 | 1.7551 | 1296 | 1755.0897 | 0.97727 | 1.0969 | 0.0054 | 26.1133
1.297 | 1.3733 | 0.055988 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.8063 | 26.3649 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2916 | 0.053696 | 1.097 | 1.0969 | 1.0969 | 1.0969 | 0.97727 | 1.7571 | 26.1235 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2916 | 0.053696 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97727 | 1.7571 | 26.1235 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2916 | 0.053696 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97727 | 1.7571 | 1297 | 1757.136 | 0.97727 | 1.0969 | 0.0054 | 26.1235
1.298 | 1.3743 | 0.05599 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.8084 | 26.3751 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2926 | 0.053698 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97728 | 1.7592 | 26.1336 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2926 | 0.053698 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97728 | 1.7592 | 26.1336 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2926 | 0.053698 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97728 | 1.7592 | 1298 | 1759.1831 | 0.97728 | 1.0969 | 0.0054 | 26.1336
1.299 | 1.3754 | 0.055991 | 1.1019 | 1.1019 | 1.1019 | 1.1019 | 1.8105 | 26.3853 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2936 | 0.053699 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97728 | 1.7612 | 26.1437 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2936 | 0.053699 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97728 | 1.7612 | 26.1437 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2936 | 0.053699 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97728 | 1.7612 | 1299 | 1761.231 | 0.97728 | 1.0969 | 0.0054 | 26.1437
1.3 | 1.3764 | 0.055993 | 1.1019 | 1.1019 | 1.102 | 1.102 | 1.8126 | 26.3954 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2946 | 0.053701 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97729 | 1.7633 | 26.1539 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2946 | 0.053701 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97729 | 1.7633 | 26.1539 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2946 | 0.053701 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97729 | 1.7633 | 1300 | 1763.2797 | 0.97729 | 1.0969 | 0.0054 | 26.1539
1.301 | 1.3775 | 0.055994 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8147 | 26.4056 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2956 | 0.053703 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97729 | 1.7653 | 26.164 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2956 | 0.053703 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97729 | 1.7653 | 26.164 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2956 | 0.053703 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97729 | 1.7653 | 1301 | 1765.3292 | 0.97729 | 1.0969 | 0.0054 | 26.164
1.302 | 1.3785 | 0.055995 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8168 | 26.4158 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2966 | 0.053704 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.9773 | 1.7674 | 26.1741 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2966 | 0.053704 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9773 | 1.7674 | 26.1741 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2966 | 0.053704 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9773 | 1.7674 | 1302 | 1767.3795 | 0.9773 | 1.0969 | 0.0054 | 26.1741
1.303 | 1.3795 | 0.055997 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8189 | 26.426 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2976 | 0.053706 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.9773 | 1.7694 | 26.1842 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2976 | 0.053706 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9773 | 1.7694 | 26.1842 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2976 | 0.053706 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.9773 | 1.7694 | 1303 | 1769.4305 | 0.9773 | 1.0969 | 0.0054 | 26.1842
1.304 | 1.3806 | 0.055998 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.821 | 26.4361 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2986 | 0.053708 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97731 | 1.7715 | 26.1944 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2986 | 0.053708 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97731 | 1.7715 | 26.1944 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2986 | 0.053708 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97731 | 1.7715 | 1304 | 1771.4824 | 0.97731 | 1.0969 | 0.0054 | 26.1944
1.305 | 1.3816 | 0.056 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8231 | 26.4463 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2996 | 0.05371 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97731 | 1.7735 | 26.2045 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2996 | 0.05371 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97731 | 1.7735 | 26.2045 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.2996 | 0.05371 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97731 | 1.7735 | 1305 | 1773.5351 | 0.97731 | 1.0969 | 0.0054 | 26.2045
1.306 | 1.3827 | 0.056001 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8252 | 26.4564 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3006 | 0.053711 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7756 | 26.2146 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3006 | 0.053711 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7756 | 26.2146 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3006 | 0.053711 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7756 | 1306 | 1775.5885 | 0.97732 | 1.0969 | 0.0054 | 26.2146
1.307 | 1.3837 | 0.056003 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8273 | 26.4666 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3016 | 0.053713 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7776 | 26.2247 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3016 | 0.053713 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7776 | 26.2247 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3016 | 0.053713 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7776 | 1307 | 1777.6428 | 0.97732 | 1.0969 | 0.0054 | 26.2247
1.308 | 1.3848 | 0.056004 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8294 | 26.4767 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3026 | 0.053715 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7797 | 26.2348 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3026 | 0.053715 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7797 | 26.2348 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3026 | 0.053715 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97732 | 1.7797 | 1308 | 1779.6978 | 0.97732 | 1.0969 | 0.0054 | 26.2348
1.309 | 1.3858 | 0.056005 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8315 | 26.4869 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3036 | 0.053716 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97733 | 1.7818 | 26.2449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3036 | 0.053716 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97733 | 1.7818 | 26.2449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3036 | 0.053716 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97733 | 1.7818 | 1309 | 1781.7536 | 0.97733 | 1.0969 | 0.0054 | 26.2449
1.31 | 1.3868 | 0.056007 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8336 | 26.497 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3046 | 0.053718 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97733 | 1.7838 | 26.255 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3046 | 0.053718 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97733 | 1.7838 | 26.255 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3046 | 0.053718 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97733 | 1.7838 | 1310 | 1783.8103 | 0.97733 | 1.0969 | 0.0054 | 26.255
1.311 | 1.3879 | 0.056008 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8357 | 26.5072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3056 | 0.05372 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97734 | 1.7859 | 26.2651 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3056 | 0.05372 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97734 | 1.7859 | 26.2651 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3056 | 0.05372 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97734 | 1.7859 | 1311 | 1785.8677 | 0.97734 | 1.0969 | 0.0054 | 26.2651
1.312 | 1.3889 | 0.05601 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8378 | 26.5173 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3066 | 0.053721 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97734 | 1.7879 | 26.2752 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3066 | 0.053721 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97734 | 1.7879 | 26.2752 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3066 | 0.053721 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97734 | 1.7879 | 1312 | 1787.9259 | 0.97734 | 1.0969 | 0.0054 | 26.2752
1.313 | 1.39 | 0.056011 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8399 | 26.5274 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3076 | 0.053723 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97735 | 1.79 | 26.2852 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3076 | 0.053723 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97735 | 1.79 | 26.2852 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3076 | 0.053723 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97735 | 1.79 | 1313 | 1789.9849 | 0.97735 | 1.0969 | 0.0054 | 26.2852
1.314 | 1.391 | 0.056012 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.842 | 26.5376 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3086 | 0.053725 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97735 | 1.792 | 26.2953 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3086 | 0.053725 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97735 | 1.792 | 26.2953 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3086 | 0.053725 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97735 | 1.792 | 1314 | 1792.0447 | 0.97735 | 1.0969 | 0.0054 | 26.2953
1.315 | 1.392 | 0.056014 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8441 | 26.5477 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3096 | 0.053726 | 1.0971 | 1.0969 | 1.0969 | 1.0969 | 0.97736 | 1.7941 | 26.3054 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3096 | 0.053726 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97736 | 1.7941 | 26.3054 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3096 | 0.053726 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97736 | 1.7941 | 1315 | 1794.1052 | 0.97736 | 1.0969 | 0.0054 | 26.3054
1.316 | 1.3931 | 0.056015 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8462 | 26.5578 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3106 | 0.053728 | 1.0971 | 1.097 | 1.0969 | 1.0969 | 0.97736 | 1.7962 | 26.3155 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3106 | 0.053728 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97736 | 1.7962 | 26.3155 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3106 | 0.053728 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97736 | 1.7962 | 1316 | 1796.1666 | 0.97736 | 1.0969 | 0.0054 | 26.3155
1.317 | 1.3941 | 0.056017 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8484 | 26.5679 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3116 | 0.05373 | 1.0971 | 1.097 | 1.0969 | 1.0969 | 0.97737 | 1.7982 | 26.3255 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3116 | 0.05373 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97737 | 1.7982 | 26.3255 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3116 | 0.05373 | 1.0969 | 1.0969 | 1.0969 | 1.0969 | 0.97737 | 1.7982 | 1317 | 1798.2287 | 0.97737 | 1.0969 | 0.0054 | 26.3255
1.318 | 1.3952 | 0.056018 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8505 | 26.578 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3126 | 0.053732 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.97737 | 1.8003 | 26.3356 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3126 | 0.053732 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97737 | 1.8003 | 26.3356 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3126 | 0.053732 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97737 | 1.8003 | 1318 | 1800.2917 | 0.97737 | 1.097 | 0.0054 | 26.3356
1.319 | 1.3962 | 0.056019 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8526 | 26.5881 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3136 | 0.053733 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8024 | 26.3457 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3136 | 0.053733 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8024 | 26.3457 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3136 | 0.053733 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8024 | 1319 | 1802.3554 | 0.97738 | 1.097 | 0.0054 | 26.3457
1.32 | 1.3972 | 0.056021 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8547 | 26.5982 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3146 | 0.053735 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8044 | 26.3557 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3146 | 0.053735 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8044 | 26.3557 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3146 | 0.053735 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8044 | 1320 | 1804.4199 | 0.97738 | 1.097 | 0.0054 | 26.3557
1.321 | 1.3983 | 0.056022 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8568 | 26.6083 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3156 | 0.053737 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8065 | 26.3658 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3156 | 0.053737 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8065 | 26.3658 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3156 | 0.053737 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97738 | 1.8065 | 1321 | 1806.4852 | 0.97738 | 1.097 | 0.0054 | 26.3658
1.322 | 1.3993 | 0.056024 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8589 | 26.6184 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3166 | 0.053738 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.97739 | 1.8086 | 26.3758 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3166 | 0.053738 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97739 | 1.8086 | 26.3758 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3166 | 0.053738 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97739 | 1.8086 | 1322 | 1808.5513 | 0.97739 | 1.097 | 0.0054 | 26.3758
1.323 | 1.4004 | 0.056025 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.861 | 26.6285 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3176 | 0.05374 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.97739 | 1.8106 | 26.3859 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3176 | 0.05374 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97739 | 1.8106 | 26.3859 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3176 | 0.05374 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97739 | 1.8106 | 1323 | 1810.6182 | 0.97739 | 1.097 | 0.0054 | 26.3859
1.324 | 1.4014 | 0.056026 | 1.1019 | 1.102 | 1.102 | 1.102 | 1.8631 | 26.6386 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3186 | 0.053742 | 1.0971 | 1.097 | 1.097 | 1.097 | 0.9774 | 1.8127 | 26.3959 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3186 | 0.053742 | 1.097 | 1.097 | 1.097 | 1.097 | 0.9774 | 1.8127 | 26.3959 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3186 | 0.053742 | 1.097 | 1.097 | 1.097 | 1.097 | 0.9774 | 1.8127 | 1324 | 1812.6859 | 0.9774 | 1.097 | 0.0054 | 26.3959
1.325 | 1.4025 | 0.056028 | 1.102 | 1.102 | 1.102 | 1.102 | 1.8653 | 26.6487 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3196 | 0.053743 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.9774 | 1.8148 | 26.4059 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3196 | 0.053743 | 1.097 | 1.097 | 1.097 | 1.097 | 0.9774 | 1.8148 | 26.4059 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3196 | 0.053743 | 1.097 | 1.097 | 1.097 | 1.097 | 0.9774 | 1.8148 | 1325 | 1814.7544 | 0.9774 | 1.097 | 0.0054 | 26.4059
1.326 | 1.4035 | 0.056029 | 1.102 | 1.102 | 1.102 | 1.102 | 1.8674 | 26.6588 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3206 | 0.053745 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97741 | 1.8168 | 26.416 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3206 | 0.053745 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97741 | 1.8168 | 26.416 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3206 | 0.053745 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97741 | 1.8168 | 1326 | 1816.8236 | 0.97741 | 1.097 | 0.0054 | 26.416
1.327 | 1.4045 | 0.05603 | 1.102 | 1.102 | 1.102 | 1.102 | 1.8695 | 26.6688 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3216 | 0.053746 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97741 | 1.8189 | 26.426 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3216 | 0.053746 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97741 | 1.8189 | 26.426 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3216 | 0.053746 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97741 | 1.8189 | 1327 | 1818.8936 | 0.97741 | 1.097 | 0.0054 | 26.426
1.328 | 1.4056 | 0.056032 | 1.102 | 1.102 | 1.102 | 1.102 | 1.8716 | 26.6789 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3226 | 0.053748 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.821 | 26.436 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3226 | 0.053748 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.821 | 26.436 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3226 | 0.053748 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.821 | 1328 | 1820.9644 | 0.97742 | 1.097 | 0.0054 | 26.436
1.329 | 1.4066 | 0.056033 | 1.102 | 1.102 | 1.102 | 1.102 | 1.8737 | 26.689 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3236 | 0.05375 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.823 | 26.446 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3236 | 0.05375 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.823 | 26.446 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3236 | 0.05375 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.823 | 1329 | 1823.036 | 0.97742 | 1.097 | 0.0054 | 26.446
1.33 | 1.4077 | 0.056035 | 1.102 | 1.102 | 1.102 | 1.102 | 1.8759 | 26.699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3246 | 0.053751 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.8251 | 26.4561 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3246 | 0.053751 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.8251 | 26.4561 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3246 | 0.053751 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97742 | 1.8251 | 1330 | 1825.1084 | 0.97742 | 1.097 | 0.0054 | 26.4561
1.331 | 1.4087 | 0.056036 | 1.102 | 1.102 | 1.102 | 1.102 | 1.878 | 26.7091 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3256 | 0.053753 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97743 | 1.8272 | 26.4661 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3256 | 0.053753 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97743 | 1.8272 | 26.4661 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3256 | 0.053753 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97743 | 1.8272 | 1331 | 1827.1816 | 0.97743 | 1.097 | 0.0054 | 26.4661
1.332 | 1.4097 | 0.056037 | 1.102 | 1.102 | 1.1021 | 1.1021 | 1.8801 | 26.7191 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3266 | 0.053755 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97743 | 1.8293 | 26.4761 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3266 | 0.053755 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97743 | 1.8293 | 26.4761 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3266 | 0.053755 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97743 | 1.8293 | 1332 | 1829.2556 | 0.97743 | 1.097 | 0.0054 | 26.4761
1.333 | 1.4108 | 0.056039 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8822 | 26.7292 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3276 | 0.053756 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97744 | 1.8313 | 26.4861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3276 | 0.053756 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97744 | 1.8313 | 26.4861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3276 | 0.053756 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97744 | 1.8313 | 1333 | 1831.3303 | 0.97744 | 1.097 | 0.0054 | 26.4861
1.334 | 1.4118 | 0.05604 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8843 | 26.7392 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3286 | 0.053758 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97744 | 1.8334 | 26.4961 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3286 | 0.053758 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97744 | 1.8334 | 26.4961 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3286 | 0.053758 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97744 | 1.8334 | 1334 | 1833.4058 | 0.97744 | 1.097 | 0.0054 | 26.4961
1.335 | 1.4129 | 0.056041 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8865 | 26.7493 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3296 | 0.05376 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97745 | 1.8355 | 26.5061 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3296 | 0.05376 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97745 | 1.8355 | 26.5061 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3296 | 0.05376 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97745 | 1.8355 | 1335 | 1835.4821 | 0.97745 | 1.097 | 0.0054 | 26.5061
1.336 | 1.4139 | 0.056043 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8886 | 26.7593 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3306 | 0.053761 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97745 | 1.8376 | 26.5161 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3306 | 0.053761 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97745 | 1.8376 | 26.5161 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3306 | 0.053761 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97745 | 1.8376 | 1336 | 1837.5592 | 0.97745 | 1.097 | 0.0054 | 26.5161
1.337 | 1.4149 | 0.056044 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8907 | 26.7694 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3316 | 0.053763 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97746 | 1.8396 | 26.5261 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3316 | 0.053763 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97746 | 1.8396 | 26.5261 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3316 | 0.053763 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97746 | 1.8396 | 1337 | 1839.6371 | 0.97746 | 1.097 | 0.0054 | 26.5261
1.338 | 1.416 | 0.056046 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8928 | 26.7794 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3326 | 0.053765 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97746 | 1.8417 | 26.5361 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3326 | 0.053765 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97746 | 1.8417 | 26.5361 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3326 | 0.053765 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97746 | 1.8417 | 1338 | 1841.7158 | 0.97746 | 1.097 | 0.0054 | 26.5361
1.339 | 1.417 | 0.056047 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.895 | 26.7894 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3336 | 0.053766 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.8438 | 26.546 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3336 | 0.053766 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.8438 | 26.546 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3336 | 0.053766 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.8438 | 1339 | 1843.7952 | 0.97747 | 1.097 | 0.0054 | 26.546
1.34 | 1.4181 | 0.056048 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8971 | 26.7995 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3346 | 0.053768 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.8459 | 26.556 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3346 | 0.053768 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.8459 | 26.556 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3346 | 0.053768 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.8459 | 1340 | 1845.8754 | 0.97747 | 1.097 | 0.0054 | 26.556
1.341 | 1.4191 | 0.05605 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.8992 | 26.8095 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3356 | 0.053769 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.848 | 26.566 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3356 | 0.053769 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.848 | 26.566 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3356 | 0.053769 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97747 | 1.848 | 1341 | 1847.9564 | 0.97747 | 1.097 | 0.0054 | 26.566
1.342 | 1.4202 | 0.056051 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9014 | 26.8195 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3366 | 0.053771 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97748 | 1.85 | 26.576 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3366 | 0.053771 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97748 | 1.85 | 26.576 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3366 | 0.053771 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97748 | 1.85 | 1342 | 1850.0382 | 0.97748 | 1.097 | 0.0054 | 26.576
1.343 | 1.4212 | 0.056052 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9035 | 26.8295 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3376 | 0.053773 | 1.0972 | 1.097 | 1.097 | 1.097 | 0.97748 | 1.8521 | 26.5859 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3376 | 0.053773 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97748 | 1.8521 | 26.5859 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3376 | 0.053773 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97748 | 1.8521 | 1343 | 1852.1208 | 0.97748 | 1.097 | 0.0054 | 26.5859
1.344 | 1.4222 | 0.056054 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9056 | 26.8395 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3386 | 0.053774 | 1.0972 | 1.0971 | 1.097 | 1.097 | 0.97749 | 1.8542 | 26.5959 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3386 | 0.053774 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97749 | 1.8542 | 26.5959 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3386 | 0.053774 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97749 | 1.8542 | 1344 | 1854.2041 | 0.97749 | 1.097 | 0.0054 | 26.5959
1.345 | 1.4233 | 0.056055 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9078 | 26.8495 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3396 | 0.053776 | 1.0972 | 1.0971 | 1.097 | 1.097 | 0.97749 | 1.8563 | 26.6059 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3396 | 0.053776 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97749 | 1.8563 | 26.6059 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3396 | 0.053776 | 1.097 | 1.097 | 1.097 | 1.097 | 0.97749 | 1.8563 | 1345 | 1856.2883 | 0.97749 | 1.097 | 0.0054 | 26.6059
1.346 | 1.4243 | 0.056056 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9099 | 26.8595 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3406 | 0.053777 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8584 | 26.6158 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3406 | 0.053777 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8584 | 26.6158 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3406 | 0.053777 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8584 | 1346 | 1858.3732 | 0.9775 | 1.0971 | 0.0054 | 26.6158
1.347 | 1.4254 | 0.056058 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.912 | 26.8695 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3416 | 0.053779 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8605 | 26.6258 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3416 | 0.053779 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8605 | 26.6258 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3416 | 0.053779 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8605 | 1347 | 1860.4589 | 0.9775 | 1.0971 | 0.0054 | 26.6258
1.348 | 1.4264 | 0.056059 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9142 | 26.8795 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3426 | 0.053781 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8625 | 26.6357 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3426 | 0.053781 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8625 | 26.6357 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3426 | 0.053781 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9775 | 1.8625 | 1348 | 1862.5453 | 0.9775 | 1.0971 | 0.0054 | 26.6357
1.349 | 1.4274 | 0.05606 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9163 | 26.8895 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3436 | 0.053782 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.97751 | 1.8646 | 26.6457 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3436 | 0.053782 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97751 | 1.8646 | 26.6457 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3436 | 0.053782 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97751 | 1.8646 | 1349 | 1864.6326 | 0.97751 | 1.0971 | 0.0054 | 26.6457
1.35 | 1.4285 | 0.056062 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9184 | 26.8995 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3446 | 0.053784 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.97751 | 1.8667 | 26.6556 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3446 | 0.053784 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97751 | 1.8667 | 26.6556 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3446 | 0.053784 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97751 | 1.8667 | 1350 | 1866.7206 | 0.97751 | 1.0971 | 0.0054 | 26.6556
1.351 | 1.4295 | 0.056063 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9206 | 26.9095 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3456 | 0.053785 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.97752 | 1.8688 | 26.6656 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3456 | 0.053785 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97752 | 1.8688 | 26.6656 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3456 | 0.053785 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97752 | 1.8688 | 1351 | 1868.8094 | 0.97752 | 1.0971 | 0.0054 | 26.6656
1.352 | 1.4306 | 0.056064 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9227 | 26.9195 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3466 | 0.053787 | 1.0972 | 1.0971 | 1.0971 | 1.0971 | 0.97752 | 1.8709 | 26.6755 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3466 | 0.053787 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97752 | 1.8709 | 26.6755 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3466 | 0.053787 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97752 | 1.8709 | 1352 | 1870.899 | 0.97752 | 1.0971 | 0.0054 | 26.6755
1.353 | 1.4316 | 0.056066 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9248 | 26.9295 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3476 | 0.053789 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97753 | 1.873 | 26.6854 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3476 | 0.053789 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97753 | 1.873 | 26.6854 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3476 | 0.053789 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97753 | 1.873 | 1353 | 1872.9894 | 0.97753 | 1.0971 | 0.0054 | 26.6854
1.354 | 1.4326 | 0.056067 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.927 | 26.9394 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3486 | 0.05379 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97753 | 1.8751 | 26.6953 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3486 | 0.05379 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97753 | 1.8751 | 26.6953 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3486 | 0.05379 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97753 | 1.8751 | 1354 | 1875.0805 | 0.97753 | 1.0971 | 0.0054 | 26.6953
1.355 | 1.4337 | 0.056068 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9291 | 26.9494 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3496 | 0.053792 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8772 | 26.7053 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3496 | 0.053792 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8772 | 26.7053 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3496 | 0.053792 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8772 | 1355 | 1877.1725 | 0.97754 | 1.0971 | 0.0054 | 26.7053
1.356 | 1.4347 | 0.05607 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9313 | 26.9594 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3506 | 0.053793 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8793 | 26.7152 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3506 | 0.053793 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8793 | 26.7152 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3506 | 0.053793 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8793 | 1356 | 1879.2652 | 0.97754 | 1.0971 | 0.0054 | 26.7152
1.357 | 1.4358 | 0.056071 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9334 | 26.9693 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3516 | 0.053795 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8814 | 26.7251 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3516 | 0.053795 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8814 | 26.7251 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3516 | 0.053795 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97754 | 1.8814 | 1357 | 1881.3586 | 0.97754 | 1.0971 | 0.0054 | 26.7251
1.358 | 1.4368 | 0.056072 | 1.102 | 1.1021 | 1.1021 | 1.1021 | 1.9356 | 26.9793 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3526 | 0.053797 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97755 | 1.8835 | 26.735 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3526 | 0.053797 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97755 | 1.8835 | 26.735 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3526 | 0.053797 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97755 | 1.8835 | 1358 | 1883.4529 | 0.97755 | 1.0971 | 0.0054 | 26.735
1.359 | 1.4379 | 0.056074 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.9377 | 26.9893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3536 | 0.053798 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97755 | 1.8855 | 26.7449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3536 | 0.053798 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97755 | 1.8855 | 26.7449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3536 | 0.053798 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97755 | 1.8855 | 1359 | 1885.5479 | 0.97755 | 1.0971 | 0.0054 | 26.7449
1.36 | 1.4389 | 0.056075 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.9398 | 26.9992 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3546 | 0.0538 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97756 | 1.8876 | 26.7548 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3546 | 0.0538 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97756 | 1.8876 | 26.7548 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3546 | 0.0538 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97756 | 1.8876 | 1360 | 1887.6437 | 0.97756 | 1.0971 | 0.0054 | 26.7548
1.361 | 1.4399 | 0.056076 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.942 | 27.0092 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3556 | 0.053801 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97756 | 1.8897 | 26.7647 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3556 | 0.053801 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97756 | 1.8897 | 26.7647 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3556 | 0.053801 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97756 | 1.8897 | 1361 | 1889.7403 | 0.97756 | 1.0971 | 0.0054 | 26.7647
1.362 | 1.441 | 0.056077 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.9441 | 27.0191 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3566 | 0.053803 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.8918 | 26.7746 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3566 | 0.053803 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.8918 | 26.7746 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3566 | 0.053803 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.8918 | 1362 | 1891.8377 | 0.97757 | 1.0971 | 0.0054 | 26.7746
1.363 | 1.442 | 0.056079 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.9463 | 27.029 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3576 | 0.053804 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.8939 | 26.7845 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3576 | 0.053804 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.8939 | 26.7845 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3576 | 0.053804 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.8939 | 1363 | 1893.9358 | 0.97757 | 1.0971 | 0.0054 | 26.7845
1.364 | 1.4431 | 0.05608 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.9484 | 27.039 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3586 | 0.053806 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.896 | 26.7944 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3586 | 0.053806 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.896 | 26.7944 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3586 | 0.053806 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97757 | 1.896 | 1364 | 1896.0347 | 0.97757 | 1.0971 | 0.0054 | 26.7944
1.365 | 1.4441 | 0.056081 | 1.1021 | 1.1021 | 1.1021 | 1.1021 | 1.9506 | 27.0489 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3596 | 0.053808 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97758 | 1.8981 | 26.8043 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3596 | 0.053808 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97758 | 1.8981 | 26.8043 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3596 | 0.053808 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97758 | 1.8981 | 1365 | 1898.1344 | 0.97758 | 1.0971 | 0.0054 | 26.8043
1.366 | 1.4451 | 0.056083 | 1.1021 | 1.1021 | 1.1022 | 1.1022 | 1.9527 | 27.0588 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3606 | 0.053809 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97758 | 1.9002 | 26.8142 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3606 | 0.053809 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97758 | 1.9002 | 26.8142 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3606 | 0.053809 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97758 | 1.9002 | 1366 | 1900.2349 | 0.97758 | 1.0971 | 0.0054 | 26.8142
1.367 | 1.4462 | 0.056084 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9549 | 27.0688 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3616 | 0.053811 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97759 | 1.9023 | 26.8241 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3616 | 0.053811 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97759 | 1.9023 | 26.8241 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3616 | 0.053811 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97759 | 1.9023 | 1367 | 1902.3361 | 0.97759 | 1.0971 | 0.0054 | 26.8241
1.368 | 1.4472 | 0.056085 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.957 | 27.0787 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3626 | 0.053812 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97759 | 1.9044 | 26.8339 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3626 | 0.053812 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97759 | 1.9044 | 26.8339 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3626 | 0.053812 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97759 | 1.9044 | 1368 | 1904.4381 | 0.97759 | 1.0971 | 0.0054 | 26.8339
1.369 | 1.4483 | 0.056087 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9592 | 27.0886 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3636 | 0.053814 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9065 | 26.8438 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3636 | 0.053814 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9065 | 26.8438 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3636 | 0.053814 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9065 | 1369 | 1906.5409 | 0.9776 | 1.0971 | 0.0054 | 26.8438
1.37 | 1.4493 | 0.056088 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9613 | 27.0985 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3646 | 0.053815 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9086 | 26.8537 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3646 | 0.053815 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9086 | 26.8537 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3646 | 0.053815 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9086 | 1370 | 1908.6445 | 0.9776 | 1.0971 | 0.0054 | 26.8537
1.371 | 1.4503 | 0.056089 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9635 | 27.1084 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3656 | 0.053817 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9107 | 26.8636 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3656 | 0.053817 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9107 | 26.8636 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3656 | 0.053817 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.9776 | 1.9107 | 1371 | 1910.7488 | 0.9776 | 1.0971 | 0.0054 | 26.8636
1.372 | 1.4514 | 0.05609 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9656 | 27.1183 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3666 | 0.053818 | 1.0973 | 1.0971 | 1.0971 | 1.0971 | 0.97761 | 1.9129 | 26.8734 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3666 | 0.053818 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97761 | 1.9129 | 26.8734 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3666 | 0.053818 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97761 | 1.9129 | 1372 | 1912.8539 | 0.97761 | 1.0971 | 0.0054 | 26.8734
1.373 | 1.4524 | 0.056092 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9678 | 27.1282 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3676 | 0.05382 | 1.0973 | 1.0972 | 1.0971 | 1.0971 | 0.97761 | 1.915 | 26.8833 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3676 | 0.05382 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97761 | 1.915 | 26.8833 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3676 | 0.05382 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97761 | 1.915 | 1373 | 1914.9598 | 0.97761 | 1.0971 | 0.0054 | 26.8833
1.374 | 1.4535 | 0.056093 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9699 | 27.1381 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3686 | 0.053822 | 1.0973 | 1.0972 | 1.0971 | 1.0971 | 0.97762 | 1.9171 | 26.8931 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3686 | 0.053822 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97762 | 1.9171 | 26.8931 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3686 | 0.053822 | 1.0971 | 1.0971 | 1.0971 | 1.0971 | 0.97762 | 1.9171 | 1374 | 1917.0664 | 0.97762 | 1.0971 | 0.0054 | 26.8931
1.375 | 1.4545 | 0.056094 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9721 | 27.148 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3696 | 0.053823 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97762 | 1.9192 | 26.903 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3696 | 0.053823 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97762 | 1.9192 | 26.903 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3696 | 0.053823 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97762 | 1.9192 | 1375 | 1919.1739 | 0.97762 | 1.0972 | 0.0054 | 26.903
1.376 | 1.4556 | 0.056096 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9743 | 27.1579 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3706 | 0.053825 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97762 | 1.9213 | 26.9128 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3706 | 0.053825 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97762 | 1.9213 | 26.9128 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3706 | 0.053825 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97762 | 1.9213 | 1376 | 1921.2821 | 0.97762 | 1.0972 | 0.0054 | 26.9128
1.377 | 1.4566 | 0.056097 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9764 | 27.1678 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3716 | 0.053826 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97763 | 1.9234 | 26.9227 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3716 | 0.053826 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97763 | 1.9234 | 26.9227 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3716 | 0.053826 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97763 | 1.9234 | 1377 | 1923.391 | 0.97763 | 1.0972 | 0.0054 | 26.9227
1.378 | 1.4576 | 0.056098 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9786 | 27.1777 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3726 | 0.053828 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97763 | 1.9255 | 26.9325 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3726 | 0.053828 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97763 | 1.9255 | 26.9325 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3726 | 0.053828 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97763 | 1.9255 | 1378 | 1925.5008 | 0.97763 | 1.0972 | 0.0054 | 26.9325
1.379 | 1.4587 | 0.056099 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9807 | 27.1876 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3736 | 0.053829 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97764 | 1.9276 | 26.9423 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3736 | 0.053829 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97764 | 1.9276 | 26.9423 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3736 | 0.053829 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97764 | 1.9276 | 1379 | 1927.6113 | 0.97764 | 1.0972 | 0.0054 | 26.9423
1.38 | 1.4597 | 0.056101 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9829 | 27.1975 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3746 | 0.053831 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97764 | 1.9297 | 26.9522 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3746 | 0.053831 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97764 | 1.9297 | 26.9522 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3746 | 0.053831 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97764 | 1.9297 | 1380 | 1929.7226 | 0.97764 | 1.0972 | 0.0054 | 26.9522
1.381 | 1.4608 | 0.056102 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9851 | 27.2074 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3756 | 0.053832 | 1.0973 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9318 | 26.962 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3756 | 0.053832 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9318 | 26.962 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3756 | 0.053832 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9318 | 1381 | 1931.8346 | 0.97765 | 1.0972 | 0.0054 | 26.962
1.382 | 1.4618 | 0.056103 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9872 | 27.2172 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3766 | 0.053834 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9339 | 26.9718 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3766 | 0.053834 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9339 | 26.9718 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3766 | 0.053834 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9339 | 1382 | 1933.9474 | 0.97765 | 1.0972 | 0.0054 | 26.9718
1.383 | 1.4628 | 0.056105 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9894 | 27.2271 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3776 | 0.053835 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9361 | 26.9817 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3776 | 0.053835 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9361 | 26.9817 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3776 | 0.053835 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97765 | 1.9361 | 1383 | 1936.061 | 0.97765 | 1.0972 | 0.0054 | 26.9817
1.384 | 1.4639 | 0.056106 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9915 | 27.237 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3786 | 0.053837 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97766 | 1.9382 | 26.9915 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3786 | 0.053837 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97766 | 1.9382 | 26.9915 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3786 | 0.053837 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97766 | 1.9382 | 1384 | 1938.1754 | 0.97766 | 1.0972 | 0.0054 | 26.9915
1.385 | 1.4649 | 0.056107 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9937 | 27.2468 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3796 | 0.053838 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97766 | 1.9403 | 27.0013 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3796 | 0.053838 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97766 | 1.9403 | 27.0013 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3796 | 0.053838 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97766 | 1.9403 | 1385 | 1940.2905 | 0.97766 | 1.0972 | 0.0054 | 27.0013
1.386 | 1.466 | 0.056108 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.9959 | 27.2567 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3806 | 0.05384 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9424 | 27.0111 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3806 | 0.05384 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9424 | 27.0111 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3806 | 0.05384 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9424 | 1386 | 1942.4064 | 0.97767 | 1.0972 | 0.0054 | 27.0111
1.387 | 1.467 | 0.05611 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 1.998 | 27.2665 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3816 | 0.053841 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9445 | 27.0209 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3816 | 0.053841 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9445 | 27.0209 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3816 | 0.053841 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9445 | 1387 | 1944.5231 | 0.97767 | 1.0972 | 0.0054 | 27.0209
1.388 | 1.468 | 0.056111 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.0002 | 27.2764 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3826 | 0.053843 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9466 | 27.0307 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3826 | 0.053843 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9466 | 27.0307 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3826 | 0.053843 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97767 | 1.9466 | 1388 | 1946.6405 | 0.97767 | 1.0972 | 0.0054 | 27.0307
1.389 | 1.4691 | 0.056112 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.0024 | 27.2862 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3836 | 0.053844 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97768 | 1.9488 | 27.0405 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3836 | 0.053844 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97768 | 1.9488 | 27.0405 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3836 | 0.053844 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97768 | 1.9488 | 1389 | 1948.7587 | 0.97768 | 1.0972 | 0.0054 | 27.0405
1.39 | 1.4701 | 0.056113 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.0045 | 27.2961 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3846 | 0.053846 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97768 | 1.9509 | 27.0503 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3846 | 0.053846 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97768 | 1.9509 | 27.0503 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3846 | 0.053846 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97768 | 1.9509 | 1390 | 1950.8777 | 0.97768 | 1.0972 | 0.0054 | 27.0503
1.391 | 1.4712 | 0.056115 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.0067 | 27.3059 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3856 | 0.053847 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97769 | 1.953 | 27.0601 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3856 | 0.053847 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97769 | 1.953 | 27.0601 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3856 | 0.053847 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97769 | 1.953 | 1391 | 1952.9974 | 0.97769 | 1.0972 | 0.0054 | 27.0601
1.392 | 1.4722 | 0.056116 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.0089 | 27.3158 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3866 | 0.053849 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97769 | 1.9551 | 27.0699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3866 | 0.053849 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97769 | 1.9551 | 27.0699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3866 | 0.053849 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97769 | 1.9551 | 1392 | 1955.1179 | 0.97769 | 1.0972 | 0.0054 | 27.0699
1.393 | 1.4733 | 0.056117 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.011 | 27.3256 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3876 | 0.05385 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9572 | 27.0797 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3876 | 0.05385 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9572 | 27.0797 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3876 | 0.05385 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9572 | 1393 | 1957.2392 | 0.9777 | 1.0972 | 0.0054 | 27.0797
1.394 | 1.4743 | 0.056118 | 1.1021 | 1.1022 | 1.1022 | 1.1022 | 2.0132 | 27.3354 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3886 | 0.053852 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9594 | 27.0895 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3886 | 0.053852 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9594 | 27.0895 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3886 | 0.053852 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9594 | 1394 | 1959.3613 | 0.9777 | 1.0972 | 0.0054 | 27.0895
1.395 | 1.4753 | 0.05612 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0154 | 27.3452 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3896 | 0.053853 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9615 | 27.0992 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3896 | 0.053853 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9615 | 27.0992 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3896 | 0.053853 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.9777 | 1.9615 | 1395 | 1961.4841 | 0.9777 | 1.0972 | 0.0054 | 27.0992
1.396 | 1.4764 | 0.056121 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0176 | 27.3551 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3906 | 0.053855 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97771 | 1.9636 | 27.109 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3906 | 0.053855 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97771 | 1.9636 | 27.109 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3906 | 0.053855 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97771 | 1.9636 | 1396 | 1963.6076 | 0.97771 | 1.0972 | 0.0054 | 27.109
1.397 | 1.4774 | 0.056122 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0197 | 27.3649 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3916 | 0.053856 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97771 | 1.9657 | 27.1188 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3916 | 0.053856 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97771 | 1.9657 | 27.1188 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3916 | 0.053856 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97771 | 1.9657 | 1397 | 1965.732 | 0.97771 | 1.0972 | 0.0054 | 27.1188
1.398 | 1.4785 | 0.056123 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0219 | 27.3747 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3926 | 0.053858 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.9679 | 27.1286 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3926 | 0.053858 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.9679 | 27.1286 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3926 | 0.053858 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.9679 | 1398 | 1967.8571 | 0.97772 | 1.0972 | 0.0054 | 27.1286
1.399 | 1.4795 | 0.056125 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0241 | 27.3845 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3936 | 0.053859 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.97 | 27.1383 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3936 | 0.053859 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.97 | 27.1383 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3936 | 0.053859 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.97 | 1399 | 1969.983 | 0.97772 | 1.0972 | 0.0054 | 27.1383
1.4 | 1.4805 | 0.056126 | 1.1022 | 1.1022 | 1.1022 | 1.1022 | 2.0263 | 27.3943 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3946 | 0.053861 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.9721 | 27.1481 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3946 | 0.053861 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.9721 | 27.1481 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3946 | 0.053861 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97772 | 1.9721 | 1400 | 1972.1096 | 0.97772 | 1.0972 | 0.0054 | 27.1481
1.401 | 1.4816 | 0.056127 | 1.1022 | 1.1022 | 1.1023 | 1.1023 | 2.0284 | 27.4041 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3956 | 0.053862 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97773 | 1.9742 | 27.1578 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3956 | 0.053862 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97773 | 1.9742 | 27.1578 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3956 | 0.053862 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97773 | 1.9742 | 1401 | 1974.237 | 0.97773 | 1.0972 | 0.0054 | 27.1578
1.402 | 1.4826 | 0.056128 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0306 | 27.4139 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3966 | 0.053864 | 1.0974 | 1.0972 | 1.0972 | 1.0972 | 0.97773 | 1.9764 | 27.1676 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3966 | 0.053864 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97773 | 1.9764 | 27.1676 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3966 | 0.053864 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97773 | 1.9764 | 1402 | 1976.3652 | 0.97773 | 1.0972 | 0.0054 | 27.1676
1.403 | 1.4837 | 0.05613 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0328 | 27.4237 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3976 | 0.053865 | 1.0974 | 1.0973 | 1.0972 | 1.0972 | 0.97774 | 1.9785 | 27.1774 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3976 | 0.053865 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97774 | 1.9785 | 27.1774 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3976 | 0.053865 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97774 | 1.9785 | 1403 | 1978.4941 | 0.97774 | 1.0972 | 0.0054 | 27.1774
1.404 | 1.4847 | 0.056131 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.035 | 27.4335 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3986 | 0.053867 | 1.0974 | 1.0973 | 1.0972 | 1.0972 | 0.97774 | 1.9806 | 27.1871 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3986 | 0.053867 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97774 | 1.9806 | 27.1871 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3986 | 0.053867 | 1.0972 | 1.0972 | 1.0972 | 1.0972 | 0.97774 | 1.9806 | 1404 | 1980.6238 | 0.97774 | 1.0972 | 0.0054 | 27.1871
1.405 | 1.4857 | 0.056132 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0371 | 27.4433 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3996 | 0.053868 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97774 | 1.9828 | 27.1968 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3996 | 0.053868 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97774 | 1.9828 | 27.1968 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.3996 | 0.053868 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97774 | 1.9828 | 1405 | 1982.7543 | 0.97774 | 1.0973 | 0.0054 | 27.1968
1.406 | 1.4868 | 0.056133 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0393 | 27.4531 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4006 | 0.05387 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97775 | 1.9849 | 27.2066 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4006 | 0.05387 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97775 | 1.9849 | 27.2066 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4006 | 0.05387 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97775 | 1.9849 | 1406 | 1984.8855 | 0.97775 | 1.0973 | 0.0054 | 27.2066
1.407 | 1.4878 | 0.056135 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0415 | 27.4629 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4016 | 0.053871 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97775 | 1.987 | 27.2163 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4016 | 0.053871 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97775 | 1.987 | 27.2163 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4016 | 0.053871 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97775 | 1.987 | 1407 | 1987.0175 | 0.97775 | 1.0973 | 0.0054 | 27.2163
1.408 | 1.4889 | 0.056136 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0437 | 27.4727 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4026 | 0.053873 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9892 | 27.2261 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4026 | 0.053873 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9892 | 27.2261 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4026 | 0.053873 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9892 | 1408 | 1989.1502 | 0.97776 | 1.0973 | 0.0054 | 27.2261
1.409 | 1.4899 | 0.056137 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0459 | 27.4824 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4036 | 0.053874 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9913 | 27.2358 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4036 | 0.053874 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9913 | 27.2358 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4036 | 0.053874 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9913 | 1409 | 1991.2837 | 0.97776 | 1.0973 | 0.0054 | 27.2358
1.41 | 1.491 | 0.056138 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0481 | 27.4922 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4046 | 0.053876 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9934 | 27.2455 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4046 | 0.053876 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9934 | 27.2455 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4046 | 0.053876 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97776 | 1.9934 | 1410 | 1993.418 | 0.97776 | 1.0973 | 0.0054 | 27.2455
1.411 | 1.492 | 0.056139 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0502 | 27.502 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4056 | 0.053877 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97777 | 1.9956 | 27.2552 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4056 | 0.053877 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97777 | 1.9956 | 27.2552 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4056 | 0.053877 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97777 | 1.9956 | 1411 | 1995.5531 | 0.97777 | 1.0973 | 0.0054 | 27.2552
1.412 | 1.493 | 0.056141 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0524 | 27.5117 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4066 | 0.053879 | 1.0974 | 1.0973 | 1.0973 | 1.0973 | 0.97777 | 1.9977 | 27.265 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4066 | 0.053879 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97777 | 1.9977 | 27.265 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4066 | 0.053879 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97777 | 1.9977 | 1412 | 1997.6889 | 0.97777 | 1.0973 | 0.0054 | 27.265
1.413 | 1.4941 | 0.056142 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0546 | 27.5215 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4076 | 0.05388 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 1.9998 | 27.2747 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4076 | 0.05388 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 1.9998 | 27.2747 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4076 | 0.05388 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 1.9998 | 1413 | 1999.8254 | 0.97778 | 1.0973 | 0.0054 | 27.2747
1.414 | 1.4951 | 0.056143 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0568 | 27.5313 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4086 | 0.053882 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 2.002 | 27.2844 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4086 | 0.053882 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 2.002 | 27.2844 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4086 | 0.053882 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 2.002 | 1414 | 2001.9628 | 0.97778 | 1.0973 | 0.0054 | 27.2844
1.415 | 1.4962 | 0.056144 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.059 | 27.541 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4096 | 0.053883 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 2.0041 | 27.2941 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4096 | 0.053883 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 2.0041 | 27.2941 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4096 | 0.053883 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97778 | 2.0041 | 1415 | 2004.1008 | 0.97778 | 1.0973 | 0.0054 | 27.2941
1.416 | 1.4972 | 0.056146 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0612 | 27.5508 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4106 | 0.053885 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97779 | 2.0062 | 27.3038 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4106 | 0.053885 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97779 | 2.0062 | 27.3038 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4106 | 0.053885 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97779 | 2.0062 | 1416 | 2006.2397 | 0.97779 | 1.0973 | 0.0054 | 27.3038
1.417 | 1.4982 | 0.056147 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0634 | 27.5605 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4116 | 0.053886 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97779 | 2.0084 | 27.3135 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4116 | 0.053886 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97779 | 2.0084 | 27.3135 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4116 | 0.053886 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97779 | 2.0084 | 1417 | 2008.3793 | 0.97779 | 1.0973 | 0.0054 | 27.3135
1.418 | 1.4993 | 0.056148 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0656 | 27.5703 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4126 | 0.053887 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0105 | 27.3232 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4126 | 0.053887 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0105 | 27.3232 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4126 | 0.053887 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0105 | 1418 | 2010.5197 | 0.9778 | 1.0973 | 0.0054 | 27.3232
1.419 | 1.5003 | 0.056149 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0677 | 27.58 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4136 | 0.053889 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0127 | 27.3329 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4136 | 0.053889 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0127 | 27.3329 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4136 | 0.053889 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0127 | 1419 | 2012.6608 | 0.9778 | 1.0973 | 0.0054 | 27.3329
1.42 | 1.5014 | 0.05615 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0699 | 27.5898 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4146 | 0.05389 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0148 | 27.3426 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4146 | 0.05389 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0148 | 27.3426 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4146 | 0.05389 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.9778 | 2.0148 | 1420 | 2014.8027 | 0.9778 | 1.0973 | 0.0054 | 27.3426
1.421 | 1.5024 | 0.056152 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0721 | 27.5995 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4156 | 0.053892 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97781 | 2.0169 | 27.3523 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4156 | 0.053892 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97781 | 2.0169 | 27.3523 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4156 | 0.053892 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97781 | 2.0169 | 1421 | 2016.9453 | 0.97781 | 1.0973 | 0.0054 | 27.3523
1.422 | 1.5034 | 0.056153 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0743 | 27.6092 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4166 | 0.053893 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97781 | 2.0191 | 27.362 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4166 | 0.053893 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97781 | 2.0191 | 27.362 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4166 | 0.053893 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97781 | 2.0191 | 1422 | 2019.0887 | 0.97781 | 1.0973 | 0.0054 | 27.362
1.423 | 1.5045 | 0.056154 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0765 | 27.6189 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4176 | 0.053895 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0212 | 27.3717 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4176 | 0.053895 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0212 | 27.3717 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4176 | 0.053895 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0212 | 1423 | 2021.2329 | 0.97782 | 1.0973 | 0.0054 | 27.3717
1.424 | 1.5055 | 0.056155 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0787 | 27.6287 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4186 | 0.053896 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0234 | 27.3813 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4186 | 0.053896 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0234 | 27.3813 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4186 | 0.053896 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0234 | 1424 | 2023.3778 | 0.97782 | 1.0973 | 0.0054 | 27.3813
1.425 | 1.5066 | 0.056156 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0809 | 27.6384 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4196 | 0.053898 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0255 | 27.391 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4196 | 0.053898 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0255 | 27.391 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4196 | 0.053898 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97782 | 2.0255 | 1425 | 2025.5235 | 0.97782 | 1.0973 | 0.0054 | 27.391
1.426 | 1.5076 | 0.056158 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0831 | 27.6481 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4206 | 0.053899 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97783 | 2.0277 | 27.4007 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4206 | 0.053899 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97783 | 2.0277 | 27.4007 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4206 | 0.053899 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97783 | 2.0277 | 1426 | 2027.6699 | 0.97783 | 1.0973 | 0.0054 | 27.4007
1.427 | 1.5087 | 0.056159 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0853 | 27.6578 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4216 | 0.0539 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97783 | 2.0298 | 27.4103 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4216 | 0.0539 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97783 | 2.0298 | 27.4103 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4216 | 0.0539 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97783 | 2.0298 | 1427 | 2029.8171 | 0.97783 | 1.0973 | 0.0054 | 27.4103
1.428 | 1.5097 | 0.05616 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0875 | 27.6675 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4226 | 0.053902 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.032 | 27.42 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4226 | 0.053902 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.032 | 27.42 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4226 | 0.053902 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.032 | 1428 | 2031.9651 | 0.97784 | 1.0973 | 0.0054 | 27.42
1.429 | 1.5107 | 0.056161 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0897 | 27.6772 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4236 | 0.053903 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.0341 | 27.4297 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4236 | 0.053903 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.0341 | 27.4297 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4236 | 0.053903 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.0341 | 1429 | 2034.1138 | 0.97784 | 1.0973 | 0.0054 | 27.4297
1.43 | 1.5118 | 0.056162 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0919 | 27.687 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4246 | 0.053905 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.0363 | 27.4393 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4246 | 0.053905 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.0363 | 27.4393 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4246 | 0.053905 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97784 | 2.0363 | 1430 | 2036.2633 | 0.97784 | 1.0973 | 0.0054 | 27.4393
1.431 | 1.5128 | 0.056164 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0941 | 27.6967 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4256 | 0.053906 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0384 | 27.449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4256 | 0.053906 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0384 | 27.449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4256 | 0.053906 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0384 | 1431 | 2038.4135 | 0.97785 | 1.0973 | 0.0054 | 27.449
1.432 | 1.5139 | 0.056165 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0963 | 27.7064 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4266 | 0.053908 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0406 | 27.4586 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4266 | 0.053908 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0406 | 27.4586 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4266 | 0.053908 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0406 | 1432 | 2040.5645 | 0.97785 | 1.0973 | 0.0054 | 27.4586
1.433 | 1.5149 | 0.056166 | 1.1022 | 1.1023 | 1.1023 | 1.1023 | 2.0985 | 27.716 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4276 | 0.053909 | 1.0975 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0427 | 27.4683 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4276 | 0.053909 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0427 | 27.4683 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4276 | 0.053909 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97785 | 2.0427 | 1433 | 2042.7162 | 0.97785 | 1.0973 | 0.0054 | 27.4683
1.434 | 1.5159 | 0.056167 | 1.1023 | 1.1023 | 1.1023 | 1.1023 | 2.1007 | 27.7257 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4286 | 0.05391 | 1.0975 | 1.0974 | 1.0973 | 1.0973 | 0.97786 | 2.0449 | 27.4779 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4286 | 0.05391 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97786 | 2.0449 | 27.4779 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4286 | 0.05391 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97786 | 2.0449 | 1434 | 2044.8687 | 0.97786 | 1.0973 | 0.0054 | 27.4779
1.435 | 1.517 | 0.056168 | 1.1023 | 1.1023 | 1.1023 | 1.1023 | 2.1029 | 27.7354 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4296 | 0.053912 | 1.0975 | 1.0974 | 1.0973 | 1.0973 | 0.97786 | 2.047 | 27.4876 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4296 | 0.053912 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97786 | 2.047 | 27.4876 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4296 | 0.053912 | 1.0973 | 1.0973 | 1.0973 | 1.0973 | 0.97786 | 2.047 | 1435 | 2047.022 | 0.97786 | 1.0973 | 0.0054 | 27.4876
1.436 | 1.518 | 0.056169 | 1.1023 | 1.1023 | 1.1023 | 1.1023 | 2.1051 | 27.7451 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4306 | 0.053913 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0492 | 27.4972 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4306 | 0.053913 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0492 | 27.4972 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4306 | 0.053913 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0492 | 1436 | 2049.176 | 0.97787 | 1.0974 | 0.0054 | 27.4972
1.437 | 1.5191 | 0.056171 | 1.1023 | 1.1023 | 1.1023 | 1.1023 | 2.1073 | 27.7548 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4316 | 0.053915 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0513 | 27.5068 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4316 | 0.053915 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0513 | 27.5068 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4316 | 0.053915 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0513 | 1437 | 2051.3307 | 0.97787 | 1.0974 | 0.0054 | 27.5068
1.438 | 1.5201 | 0.056172 | 1.1023 | 1.1023 | 1.1024 | 1.1024 | 2.1095 | 27.7645 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4326 | 0.053916 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0535 | 27.5165 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4326 | 0.053916 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0535 | 27.5165 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4326 | 0.053916 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97787 | 2.0535 | 1438 | 2053.4863 | 0.97787 | 1.0974 | 0.0054 | 27.5165
1.439 | 1.5211 | 0.056173 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1117 | 27.7741 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4336 | 0.053917 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97788 | 2.0556 | 27.5261 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4336 | 0.053917 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97788 | 2.0556 | 27.5261 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4336 | 0.053917 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97788 | 2.0556 | 1439 | 2055.6425 | 0.97788 | 1.0974 | 0.0054 | 27.5261
1.44 | 1.5222 | 0.056174 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1139 | 27.7838 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4346 | 0.053919 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97788 | 2.0578 | 27.5357 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4346 | 0.053919 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97788 | 2.0578 | 27.5357 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4346 | 0.053919 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97788 | 2.0578 | 1440 | 2057.7996 | 0.97788 | 1.0974 | 0.0054 | 27.5357
1.441 | 1.5232 | 0.056175 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1161 | 27.7935 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4356 | 0.05392 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.06 | 27.5454 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4356 | 0.05392 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.06 | 27.5454 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4356 | 0.05392 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.06 | 1441 | 2059.9573 | 0.97789 | 1.0974 | 0.0054 | 27.5454
1.442 | 1.5243 | 0.056177 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1183 | 27.8031 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4366 | 0.053922 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.0621 | 27.555 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4366 | 0.053922 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.0621 | 27.555 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4366 | 0.053922 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.0621 | 1442 | 2062.1159 | 0.97789 | 1.0974 | 0.0054 | 27.555
1.443 | 1.5253 | 0.056178 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1205 | 27.8128 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4376 | 0.053923 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.0643 | 27.5646 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4376 | 0.053923 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.0643 | 27.5646 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4376 | 0.053923 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97789 | 2.0643 | 1443 | 2064.2752 | 0.97789 | 1.0974 | 0.0054 | 27.5646
1.444 | 1.5264 | 0.056179 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1228 | 27.8225 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4386 | 0.053925 | 1.0975 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0664 | 27.5742 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4386 | 0.053925 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0664 | 27.5742 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4386 | 0.053925 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0664 | 1444 | 2066.4352 | 0.9779 | 1.0974 | 0.0054 | 27.5742
1.445 | 1.5274 | 0.05618 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.125 | 27.8321 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4396 | 0.053926 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0686 | 27.5838 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4396 | 0.053926 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0686 | 27.5838 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4396 | 0.053926 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0686 | 1445 | 2068.596 | 0.9779 | 1.0974 | 0.0054 | 27.5838
1.446 | 1.5284 | 0.056181 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1272 | 27.8418 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4406 | 0.053927 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0708 | 27.5934 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4406 | 0.053927 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0708 | 27.5934 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4406 | 0.053927 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.9779 | 2.0708 | 1446 | 2070.7576 | 0.9779 | 1.0974 | 0.0054 | 27.5934
1.447 | 1.5295 | 0.056182 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1294 | 27.8514 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4416 | 0.053929 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97791 | 2.0729 | 27.603 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4416 | 0.053929 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97791 | 2.0729 | 27.603 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4416 | 0.053929 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97791 | 2.0729 | 1447 | 2072.9199 | 0.97791 | 1.0974 | 0.0054 | 27.603
1.448 | 1.5305 | 0.056184 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1316 | 27.8611 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4426 | 0.05393 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97791 | 2.0751 | 27.6126 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4426 | 0.05393 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97791 | 2.0751 | 27.6126 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4426 | 0.05393 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97791 | 2.0751 | 1448 | 2075.0829 | 0.97791 | 1.0974 | 0.0054 | 27.6126
1.449 | 1.5316 | 0.056185 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1338 | 27.8707 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4436 | 0.053931 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0772 | 27.6222 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4436 | 0.053931 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0772 | 27.6222 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4436 | 0.053931 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0772 | 1449 | 2077.2467 | 0.97792 | 1.0974 | 0.0054 | 27.6222
1.45 | 1.5326 | 0.056186 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.136 | 27.8803 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4446 | 0.053933 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0794 | 27.6318 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4446 | 0.053933 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0794 | 27.6318 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4446 | 0.053933 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0794 | 1450 | 2079.4113 | 0.97792 | 1.0974 | 0.0054 | 27.6318
1.451 | 1.5336 | 0.056187 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1382 | 27.89 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4456 | 0.053934 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0816 | 27.6414 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4456 | 0.053934 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0816 | 27.6414 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4456 | 0.053934 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97792 | 2.0816 | 1451 | 2081.5766 | 0.97792 | 1.0974 | 0.0054 | 27.6414
1.452 | 1.5347 | 0.056188 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1405 | 27.8996 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4466 | 0.053936 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0837 | 27.651 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4466 | 0.053936 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0837 | 27.651 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4466 | 0.053936 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0837 | 1452 | 2083.7427 | 0.97793 | 1.0974 | 0.0054 | 27.651
1.453 | 1.5357 | 0.056189 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1427 | 27.9092 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4476 | 0.053937 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0859 | 27.6605 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4476 | 0.053937 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0859 | 27.6605 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4476 | 0.053937 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0859 | 1453 | 2085.9095 | 0.97793 | 1.0974 | 0.0054 | 27.6605
1.454 | 1.5368 | 0.05619 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1449 | 27.9189 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4486 | 0.053938 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0881 | 27.6701 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4486 | 0.053938 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0881 | 27.6701 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4486 | 0.053938 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97793 | 2.0881 | 1454 | 2088.077 | 0.97793 | 1.0974 | 0.0054 | 27.6701
1.455 | 1.5378 | 0.056192 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1471 | 27.9285 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4496 | 0.05394 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97794 | 2.0902 | 27.6797 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4496 | 0.05394 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97794 | 2.0902 | 27.6797 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4496 | 0.05394 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97794 | 2.0902 | 1455 | 2090.2453 | 0.97794 | 1.0974 | 0.0054 | 27.6797
1.456 | 1.5388 | 0.056193 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1493 | 27.9381 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4506 | 0.053941 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97794 | 2.0924 | 27.6893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4506 | 0.053941 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97794 | 2.0924 | 27.6893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4506 | 0.053941 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97794 | 2.0924 | 1456 | 2092.4144 | 0.97794 | 1.0974 | 0.0054 | 27.6893
1.457 | 1.5399 | 0.056194 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1516 | 27.9477 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4516 | 0.053943 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0946 | 27.6988 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4516 | 0.053943 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0946 | 27.6988 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4516 | 0.053943 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0946 | 1457 | 2094.5842 | 0.97795 | 1.0974 | 0.0054 | 27.6988
1.458 | 1.5409 | 0.056195 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1538 | 27.9573 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4526 | 0.053944 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0968 | 27.7084 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4526 | 0.053944 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0968 | 27.7084 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4526 | 0.053944 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0968 | 1458 | 2096.7548 | 0.97795 | 1.0974 | 0.0054 | 27.7084
1.459 | 1.542 | 0.056196 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.156 | 27.9669 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4536 | 0.053945 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0989 | 27.718 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4536 | 0.053945 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0989 | 27.718 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4536 | 0.053945 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97795 | 2.0989 | 1459 | 2098.9261 | 0.97795 | 1.0974 | 0.0054 | 27.718
1.46 | 1.543 | 0.056197 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1582 | 27.9765 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4546 | 0.053947 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1011 | 27.7275 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4546 | 0.053947 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1011 | 27.7275 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4546 | 0.053947 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1011 | 1460 | 2101.0982 | 0.97796 | 1.0974 | 0.0054 | 27.7275
1.461 | 1.5441 | 0.056198 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1604 | 27.9861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4556 | 0.053948 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1033 | 27.7371 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4556 | 0.053948 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1033 | 27.7371 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4556 | 0.053948 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1033 | 1461 | 2103.271 | 0.97796 | 1.0974 | 0.0054 | 27.7371
1.462 | 1.5451 | 0.0562 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1627 | 27.9957 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4566 | 0.053949 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1054 | 27.7466 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4566 | 0.053949 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1054 | 27.7466 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4566 | 0.053949 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97796 | 2.1054 | 1462 | 2105.4445 | 0.97796 | 1.0974 | 0.0054 | 27.7466
1.463 | 1.5461 | 0.056201 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1649 | 28.0053 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4576 | 0.053951 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97797 | 2.1076 | 27.7562 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4576 | 0.053951 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97797 | 2.1076 | 27.7562 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4576 | 0.053951 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97797 | 2.1076 | 1463 | 2107.6188 | 0.97797 | 1.0974 | 0.0054 | 27.7562
1.464 | 1.5472 | 0.056202 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1671 | 28.0149 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4586 | 0.053952 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97797 | 2.1098 | 27.7657 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4586 | 0.053952 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97797 | 2.1098 | 27.7657 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4586 | 0.053952 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97797 | 2.1098 | 1464 | 2109.7939 | 0.97797 | 1.0974 | 0.0054 | 27.7657
1.465 | 1.5482 | 0.056203 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1693 | 28.0245 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4596 | 0.053954 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.112 | 27.7753 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4596 | 0.053954 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.112 | 27.7753 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4596 | 0.053954 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.112 | 1465 | 2111.9697 | 0.97798 | 1.0974 | 0.0054 | 27.7753
1.466 | 1.5493 | 0.056204 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1716 | 28.0341 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4606 | 0.053955 | 1.0976 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.1141 | 27.7848 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4606 | 0.053955 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.1141 | 27.7848 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4606 | 0.053955 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.1141 | 1466 | 2114.1463 | 0.97798 | 1.0974 | 0.0054 | 27.7848
1.467 | 1.5503 | 0.056205 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1738 | 28.0437 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4616 | 0.053956 | 1.0976 | 1.0975 | 1.0974 | 1.0974 | 0.97798 | 2.1163 | 27.7943 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4616 | 0.053956 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.1163 | 27.7943 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4616 | 0.053956 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97798 | 2.1163 | 1467 | 2116.3236 | 0.97798 | 1.0974 | 0.0054 | 27.7943
1.468 | 1.5513 | 0.056206 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.176 | 28.0532 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4626 | 0.053958 | 1.0976 | 1.0975 | 1.0974 | 1.0974 | 0.97799 | 2.1185 | 27.8039 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4626 | 0.053958 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97799 | 2.1185 | 27.8039 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4626 | 0.053958 | 1.0974 | 1.0974 | 1.0974 | 1.0974 | 0.97799 | 2.1185 | 1468 | 2118.5016 | 0.97799 | 1.0974 | 0.0054 | 27.8039
1.469 | 1.5524 | 0.056208 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1782 | 28.0628 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4636 | 0.053959 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97799 | 2.1207 | 27.8134 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4636 | 0.053959 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97799 | 2.1207 | 27.8134 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4636 | 0.053959 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97799 | 2.1207 | 1469 | 2120.6804 | 0.97799 | 1.0975 | 0.0054 | 27.8134
1.47 | 1.5534 | 0.056209 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1805 | 28.0724 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4646 | 0.05396 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97799 | 2.1229 | 27.8229 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4646 | 0.05396 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97799 | 2.1229 | 27.8229 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4646 | 0.05396 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97799 | 2.1229 | 1470 | 2122.8599 | 0.97799 | 1.0975 | 0.0054 | 27.8229
1.471 | 1.5545 | 0.05621 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1827 | 28.082 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4656 | 0.053962 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.978 | 2.125 | 27.8324 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4656 | 0.053962 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.978 | 2.125 | 27.8324 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4656 | 0.053962 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.978 | 2.125 | 1471 | 2125.0402 | 0.978 | 1.0975 | 0.0054 | 27.8324
1.472 | 1.5555 | 0.056211 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1849 | 28.0915 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4666 | 0.053963 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.978 | 2.1272 | 27.842 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4666 | 0.053963 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.978 | 2.1272 | 27.842 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4666 | 0.053963 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.978 | 2.1272 | 1472 | 2127.2213 | 0.978 | 1.0975 | 0.0054 | 27.842
1.473 | 1.5565 | 0.056212 | 1.1023 | 1.1024 | 1.1024 | 1.1024 | 2.1872 | 28.1011 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4676 | 0.053964 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1294 | 27.8515 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4676 | 0.053964 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1294 | 27.8515 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4676 | 0.053964 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1294 | 1473 | 2129.403 | 0.97801 | 1.0975 | 0.0054 | 27.8515
1.474 | 1.5576 | 0.056213 | 1.1024 | 1.1024 | 1.1024 | 1.1024 | 2.1894 | 28.1106 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4686 | 0.053966 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1316 | 27.861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4686 | 0.053966 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1316 | 27.861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4686 | 0.053966 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1316 | 1474 | 2131.5856 | 0.97801 | 1.0975 | 0.0054 | 27.861
1.475 | 1.5586 | 0.056214 | 1.1024 | 1.1024 | 1.1024 | 1.1024 | 2.1916 | 28.1202 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4696 | 0.053967 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1338 | 27.8705 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4696 | 0.053967 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1338 | 27.8705 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4696 | 0.053967 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97801 | 2.1338 | 1475 | 2133.7688 | 0.97801 | 1.0975 | 0.0054 | 27.8705
1.476 | 1.5597 | 0.056215 | 1.1024 | 1.1024 | 1.1024 | 1.1024 | 2.1939 | 28.1298 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4706 | 0.053968 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.136 | 27.88 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4706 | 0.053968 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.136 | 27.88 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4706 | 0.053968 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.136 | 1476 | 2135.9529 | 0.97802 | 1.0975 | 0.0054 | 27.88
1.477 | 1.5607 | 0.056217 | 1.1024 | 1.1024 | 1.1025 | 1.1025 | 2.1961 | 28.1393 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4716 | 0.05397 | 1.0976 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.1381 | 27.8895 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4716 | 0.05397 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.1381 | 27.8895 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4716 | 0.05397 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.1381 | 1477 | 2138.1376 | 0.97802 | 1.0975 | 0.0054 | 27.8895
1.478 | 1.5617 | 0.056218 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.1983 | 28.1488 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4726 | 0.053971 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.1403 | 27.899 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4726 | 0.053971 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.1403 | 27.899 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4726 | 0.053971 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97802 | 2.1403 | 1478 | 2140.3231 | 0.97802 | 1.0975 | 0.0054 | 27.899
1.479 | 1.5628 | 0.056219 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2006 | 28.1584 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4736 | 0.053972 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1425 | 27.9085 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4736 | 0.053972 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1425 | 27.9085 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4736 | 0.053972 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1425 | 1479 | 2142.5094 | 0.97803 | 1.0975 | 0.0054 | 27.9085
1.48 | 1.5638 | 0.05622 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2028 | 28.1679 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4746 | 0.053974 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1447 | 27.918 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4746 | 0.053974 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1447 | 27.918 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4746 | 0.053974 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1447 | 1480 | 2144.6964 | 0.97803 | 1.0975 | 0.0054 | 27.918
1.481 | 1.5649 | 0.056221 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2051 | 28.1775 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4756 | 0.053975 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1469 | 27.9275 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4756 | 0.053975 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1469 | 27.9275 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4756 | 0.053975 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97803 | 2.1469 | 1481 | 2146.8841 | 0.97803 | 1.0975 | 0.0054 | 27.9275
1.482 | 1.5659 | 0.056222 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2073 | 28.187 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4766 | 0.053976 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97804 | 2.1491 | 27.937 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4766 | 0.053976 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97804 | 2.1491 | 27.937 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4766 | 0.053976 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97804 | 2.1491 | 1482 | 2149.0726 | 0.97804 | 1.0975 | 0.0054 | 27.937
1.483 | 1.567 | 0.056223 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2095 | 28.1965 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4776 | 0.053978 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97804 | 2.1513 | 27.9465 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4776 | 0.053978 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97804 | 2.1513 | 27.9465 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4776 | 0.053978 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97804 | 2.1513 | 1483 | 2151.2618 | 0.97804 | 1.0975 | 0.0054 | 27.9465
1.484 | 1.568 | 0.056224 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2118 | 28.2061 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4786 | 0.053979 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1535 | 27.9559 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4786 | 0.053979 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1535 | 27.9559 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4786 | 0.053979 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1535 | 1484 | 2153.4518 | 0.97805 | 1.0975 | 0.0054 | 27.9559
1.485 | 1.569 | 0.056225 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.214 | 28.2156 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4796 | 0.05398 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1556 | 27.9654 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4796 | 0.05398 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1556 | 27.9654 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4796 | 0.05398 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1556 | 1485 | 2155.6425 | 0.97805 | 1.0975 | 0.0054 | 27.9654
1.486 | 1.5701 | 0.056227 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2163 | 28.2251 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4806 | 0.053982 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1578 | 27.9749 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4806 | 0.053982 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1578 | 27.9749 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4806 | 0.053982 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97805 | 2.1578 | 1486 | 2157.8339 | 0.97805 | 1.0975 | 0.0054 | 27.9749
1.487 | 1.5711 | 0.056228 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2185 | 28.2346 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4816 | 0.053983 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.16 | 27.9844 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4816 | 0.053983 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.16 | 27.9844 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4816 | 0.053983 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.16 | 1487 | 2160.0261 | 0.97806 | 1.0975 | 0.0054 | 27.9844
1.488 | 1.5722 | 0.056229 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2207 | 28.2441 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4826 | 0.053984 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.1622 | 27.9938 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4826 | 0.053984 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.1622 | 27.9938 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4826 | 0.053984 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.1622 | 1488 | 2162.2191 | 0.97806 | 1.0975 | 0.0054 | 27.9938
1.489 | 1.5732 | 0.05623 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.223 | 28.2536 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4836 | 0.053986 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.1644 | 28.0033 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4836 | 0.053986 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.1644 | 28.0033 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4836 | 0.053986 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97806 | 2.1644 | 1489 | 2164.4128 | 0.97806 | 1.0975 | 0.0054 | 28.0033
1.49 | 1.5742 | 0.056231 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2252 | 28.2631 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4846 | 0.053987 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.1666 | 28.0127 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4846 | 0.053987 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.1666 | 28.0127 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4846 | 0.053987 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.1666 | 1490 | 2166.6072 | 0.97807 | 1.0975 | 0.0054 | 28.0127
1.491 | 1.5753 | 0.056232 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2275 | 28.2726 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4856 | 0.053988 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.1688 | 28.0222 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4856 | 0.053988 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.1688 | 28.0222 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4856 | 0.053988 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.1688 | 1491 | 2168.8023 | 0.97807 | 1.0975 | 0.0054 | 28.0222
1.492 | 1.5763 | 0.056233 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2297 | 28.2821 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4866 | 0.05399 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.171 | 28.0317 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4866 | 0.05399 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.171 | 28.0317 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4866 | 0.05399 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97807 | 2.171 | 1492 | 2170.9982 | 0.97807 | 1.0975 | 0.0054 | 28.0317
1.493 | 1.5774 | 0.056234 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.232 | 28.2916 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4876 | 0.053991 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1732 | 28.0411 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4876 | 0.053991 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1732 | 28.0411 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4876 | 0.053991 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1732 | 1493 | 2173.1949 | 0.97808 | 1.0975 | 0.0054 | 28.0411
1.494 | 1.5784 | 0.056235 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2342 | 28.3011 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4886 | 0.053992 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1754 | 28.0506 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4886 | 0.053992 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1754 | 28.0506 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4886 | 0.053992 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1754 | 1494 | 2175.3923 | 0.97808 | 1.0975 | 0.0054 | 28.0506
1.495 | 1.5794 | 0.056236 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2365 | 28.3106 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4896 | 0.053994 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1776 | 28.06 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4896 | 0.053994 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1776 | 28.06 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4896 | 0.053994 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97808 | 2.1776 | 1495 | 2177.5904 | 0.97808 | 1.0975 | 0.0054 | 28.06
1.496 | 1.5805 | 0.056238 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2387 | 28.3201 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4906 | 0.053995 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97809 | 2.1798 | 28.0694 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4906 | 0.053995 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97809 | 2.1798 | 28.0694 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4906 | 0.053995 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97809 | 2.1798 | 1496 | 2179.7893 | 0.97809 | 1.0975 | 0.0054 | 28.0694
1.497 | 1.5815 | 0.056239 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.241 | 28.3296 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4916 | 0.053996 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97809 | 2.182 | 28.0789 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4916 | 0.053996 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97809 | 2.182 | 28.0789 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4916 | 0.053996 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97809 | 2.182 | 1497 | 2181.9889 | 0.97809 | 1.0975 | 0.0054 | 28.0789
1.498 | 1.5826 | 0.05624 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2432 | 28.3391 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4926 | 0.053998 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1842 | 28.0883 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4926 | 0.053998 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1842 | 28.0883 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4926 | 0.053998 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1842 | 1498 | 2184.1892 | 0.9781 | 1.0975 | 0.0054 | 28.0883
1.499 | 1.5836 | 0.056241 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2455 | 28.3486 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4936 | 0.053999 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1864 | 28.0977 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4936 | 0.053999 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1864 | 28.0977 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4936 | 0.053999 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1864 | 1499 | 2186.3903 | 0.9781 | 1.0975 | 0.0054 | 28.0977
1.5 | 1.5847 | 0.056242 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2477 | 28.358 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4946 | 0.054 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1886 | 28.1072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4946 | 0.054 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1886 | 28.1072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4946 | 0.054 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.9781 | 2.1886 | 1500 | 2188.5921 | 0.9781 | 1.0975 | 0.0054 | 28.1072
1.501 | 1.5857 | 0.056243 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.25 | 28.3675 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4956 | 0.054001 | 1.0977 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.1908 | 28.1166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4956 | 0.054001 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.1908 | 28.1166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4956 | 0.054001 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.1908 | 1501 | 2190.7947 | 0.97811 | 1.0975 | 0.0054 | 28.1166
1.502 | 1.5867 | 0.056244 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2522 | 28.377 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4966 | 0.054003 | 1.0977 | 1.0976 | 1.0975 | 1.0975 | 0.97811 | 2.193 | 28.126 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4966 | 0.054003 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.193 | 28.126 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4966 | 0.054003 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.193 | 1502 | 2192.998 | 0.97811 | 1.0975 | 0.0054 | 28.126
1.503 | 1.5878 | 0.056245 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2545 | 28.3864 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4976 | 0.054004 | 1.0977 | 1.0976 | 1.0975 | 1.0975 | 0.97811 | 2.1952 | 28.1354 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4976 | 0.054004 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.1952 | 28.1354 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4976 | 0.054004 | 1.0975 | 1.0975 | 1.0975 | 1.0975 | 0.97811 | 2.1952 | 1503 | 2195.202 | 0.97811 | 1.0975 | 0.0054 | 28.1354
1.504 | 1.5888 | 0.056246 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2567 | 28.3959 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4986 | 0.054005 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.1974 | 28.1449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4986 | 0.054005 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.1974 | 28.1449 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4986 | 0.054005 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.1974 | 1504 | 2197.4068 | 0.97812 | 1.0976 | 0.0054 | 28.1449
1.505 | 1.5899 | 0.056247 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.259 | 28.4054 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4996 | 0.054007 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.1996 | 28.1543 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4996 | 0.054007 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.1996 | 28.1543 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.4996 | 0.054007 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.1996 | 1505 | 2199.6123 | 0.97812 | 1.0976 | 0.0054 | 28.1543
1.506 | 1.5909 | 0.056248 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2612 | 28.4148 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5006 | 0.054008 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.2018 | 28.1637 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5006 | 0.054008 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.2018 | 28.1637 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5006 | 0.054008 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97812 | 2.2018 | 1506 | 2201.8186 | 0.97812 | 1.0976 | 0.0054 | 28.1637
1.507 | 1.5919 | 0.056249 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2635 | 28.4243 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5016 | 0.054009 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.204 | 28.1731 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5016 | 0.054009 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.204 | 28.1731 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5016 | 0.054009 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.204 | 1507 | 2204.0256 | 0.97813 | 1.0976 | 0.0054 | 28.1731
1.508 | 1.593 | 0.05625 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2658 | 28.4337 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5026 | 0.05401 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.2062 | 28.1825 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5026 | 0.05401 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.2062 | 28.1825 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5026 | 0.05401 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.2062 | 1508 | 2206.2333 | 0.97813 | 1.0976 | 0.0054 | 28.1825
1.509 | 1.594 | 0.056252 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.268 | 28.4432 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5036 | 0.054012 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.2084 | 28.1919 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5036 | 0.054012 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.2084 | 28.1919 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5036 | 0.054012 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97813 | 2.2084 | 1509 | 2208.4418 | 0.97813 | 1.0976 | 0.0054 | 28.1919
1.51 | 1.5951 | 0.056253 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2703 | 28.4526 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5046 | 0.054013 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2107 | 28.2013 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5046 | 0.054013 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2107 | 28.2013 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5046 | 0.054013 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2107 | 1510 | 2210.651 | 0.97814 | 1.0976 | 0.0054 | 28.2013
1.511 | 1.5961 | 0.056254 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2725 | 28.4621 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5056 | 0.054014 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2129 | 28.2107 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5056 | 0.054014 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2129 | 28.2107 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5056 | 0.054014 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2129 | 1511 | 2212.8609 | 0.97814 | 1.0976 | 0.0054 | 28.2107
1.512 | 1.5971 | 0.056255 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2748 | 28.4715 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5066 | 0.054016 | 1.0977 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2151 | 28.2201 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5066 | 0.054016 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2151 | 28.2201 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5066 | 0.054016 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97814 | 2.2151 | 1512 | 2215.0716 | 0.97814 | 1.0976 | 0.0054 | 28.2201
1.513 | 1.5982 | 0.056256 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2771 | 28.4809 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5076 | 0.054017 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2173 | 28.2295 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5076 | 0.054017 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2173 | 28.2295 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5076 | 0.054017 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2173 | 1513 | 2217.283 | 0.97815 | 1.0976 | 0.0054 | 28.2295
1.514 | 1.5992 | 0.056257 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2793 | 28.4904 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5086 | 0.054018 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2195 | 28.2388 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5086 | 0.054018 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2195 | 28.2388 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5086 | 0.054018 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2195 | 1514 | 2219.4951 | 0.97815 | 1.0976 | 0.0054 | 28.2388
1.515 | 1.6003 | 0.056258 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2816 | 28.4998 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5096 | 0.054019 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2217 | 28.2482 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5096 | 0.054019 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2217 | 28.2482 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5096 | 0.054019 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97815 | 2.2217 | 1515 | 2221.708 | 0.97815 | 1.0976 | 0.0054 | 28.2482
1.516 | 1.6013 | 0.056259 | 1.1024 | 1.1025 | 1.1025 | 1.1025 | 2.2839 | 28.5092 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5106 | 0.054021 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97816 | 2.2239 | 28.2576 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5106 | 0.054021 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97816 | 2.2239 | 28.2576 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5106 | 0.054021 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97816 | 2.2239 | 1516 | 2223.9216 | 0.97816 | 1.0976 | 0.0054 | 28.2576
1.517 | 1.6024 | 0.05626 | 1.1025 | 1.1025 | 1.1025 | 1.1025 | 2.2861 | 28.5186 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5116 | 0.054022 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97816 | 2.2261 | 28.267 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5116 | 0.054022 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97816 | 2.2261 | 28.267 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5116 | 0.054022 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97816 | 2.2261 | 1517 | 2226.136 | 0.97816 | 1.0976 | 0.0054 | 28.267
1.518 | 1.6034 | 0.056261 | 1.1025 | 1.1025 | 1.1026 | 1.1026 | 2.2884 | 28.528 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5126 | 0.054023 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2284 | 28.2764 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5126 | 0.054023 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2284 | 28.2764 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5126 | 0.054023 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2284 | 1518 | 2228.3511 | 0.97817 | 1.0976 | 0.0054 | 28.2764
1.519 | 1.6044 | 0.056262 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.2907 | 28.5375 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5136 | 0.054025 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2306 | 28.2857 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5136 | 0.054025 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2306 | 28.2857 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5136 | 0.054025 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2306 | 1519 | 2230.5669 | 0.97817 | 1.0976 | 0.0054 | 28.2857
1.52 | 1.6055 | 0.056263 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.2929 | 28.5469 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5146 | 0.054026 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2328 | 28.2951 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5146 | 0.054026 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2328 | 28.2951 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5146 | 0.054026 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97817 | 2.2328 | 1520 | 2232.7834 | 0.97817 | 1.0976 | 0.0054 | 28.2951
1.521 | 1.6065 | 0.056264 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.2952 | 28.5563 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5156 | 0.054027 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.235 | 28.3045 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5156 | 0.054027 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.235 | 28.3045 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5156 | 0.054027 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.235 | 1521 | 2235.0007 | 0.97818 | 1.0976 | 0.0054 | 28.3045
1.522 | 1.6076 | 0.056265 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.2975 | 28.5657 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5166 | 0.054028 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.2372 | 28.3138 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5166 | 0.054028 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.2372 | 28.3138 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5166 | 0.054028 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.2372 | 1522 | 2237.2188 | 0.97818 | 1.0976 | 0.0054 | 28.3138
1.523 | 1.6086 | 0.056266 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.2997 | 28.5751 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5176 | 0.05403 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.2394 | 28.3232 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5176 | 0.05403 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.2394 | 28.3232 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5176 | 0.05403 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97818 | 2.2394 | 1523 | 2239.4375 | 0.97818 | 1.0976 | 0.0054 | 28.3232
1.524 | 1.6096 | 0.056267 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.302 | 28.5845 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5186 | 0.054031 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2417 | 28.3325 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5186 | 0.054031 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2417 | 28.3325 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5186 | 0.054031 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2417 | 1524 | 2241.657 | 0.97819 | 1.0976 | 0.0054 | 28.3325
1.525 | 1.6107 | 0.056269 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3043 | 28.5939 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5196 | 0.054032 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2439 | 28.3419 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5196 | 0.054032 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2439 | 28.3419 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5196 | 0.054032 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2439 | 1525 | 2243.8772 | 0.97819 | 1.0976 | 0.0054 | 28.3419
1.526 | 1.6117 | 0.05627 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3065 | 28.6033 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5206 | 0.054033 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2461 | 28.3512 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5206 | 0.054033 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2461 | 28.3512 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5206 | 0.054033 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97819 | 2.2461 | 1526 | 2246.0982 | 0.97819 | 1.0976 | 0.0054 | 28.3512
1.527 | 1.6128 | 0.056271 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3088 | 28.6127 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5216 | 0.054035 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2483 | 28.3606 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5216 | 0.054035 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2483 | 28.3606 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5216 | 0.054035 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2483 | 1527 | 2248.3199 | 0.9782 | 1.0976 | 0.0054 | 28.3606
1.528 | 1.6138 | 0.056272 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3111 | 28.6221 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5226 | 0.054036 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2505 | 28.3699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5226 | 0.054036 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2505 | 28.3699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5226 | 0.054036 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2505 | 1528 | 2250.5423 | 0.9782 | 1.0976 | 0.0054 | 28.3699
1.529 | 1.6148 | 0.056273 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3134 | 28.6314 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5236 | 0.054037 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2528 | 28.3792 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5236 | 0.054037 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2528 | 28.3792 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5236 | 0.054037 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.9782 | 2.2528 | 1529 | 2252.7654 | 0.9782 | 1.0976 | 0.0054 | 28.3792
1.53 | 1.6159 | 0.056274 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3156 | 28.6408 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5246 | 0.054038 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.255 | 28.3886 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5246 | 0.054038 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.255 | 28.3886 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5246 | 0.054038 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.255 | 1530 | 2254.9893 | 0.97821 | 1.0976 | 0.0054 | 28.3886
1.531 | 1.6169 | 0.056275 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3179 | 28.6502 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5256 | 0.05404 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.2572 | 28.3979 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5256 | 0.05404 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.2572 | 28.3979 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5256 | 0.05404 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.2572 | 1531 | 2257.2139 | 0.97821 | 1.0976 | 0.0054 | 28.3979
1.532 | 1.618 | 0.056276 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3202 | 28.6596 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5266 | 0.054041 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.2594 | 28.4072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5266 | 0.054041 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.2594 | 28.4072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5266 | 0.054041 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97821 | 2.2594 | 1532 | 2259.4393 | 0.97821 | 1.0976 | 0.0054 | 28.4072
1.533 | 1.619 | 0.056277 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3225 | 28.669 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5276 | 0.054042 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2617 | 28.4166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5276 | 0.054042 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2617 | 28.4166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5276 | 0.054042 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2617 | 1533 | 2261.6654 | 0.97822 | 1.0976 | 0.0054 | 28.4166
1.534 | 1.6201 | 0.056278 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3247 | 28.6783 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5286 | 0.054043 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2639 | 28.4259 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5286 | 0.054043 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2639 | 28.4259 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5286 | 0.054043 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2639 | 1534 | 2263.8922 | 0.97822 | 1.0976 | 0.0054 | 28.4259
1.535 | 1.6211 | 0.056279 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.327 | 28.6877 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5296 | 0.054045 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2661 | 28.4352 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5296 | 0.054045 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2661 | 28.4352 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5296 | 0.054045 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97822 | 2.2661 | 1535 | 2266.1197 | 0.97822 | 1.0976 | 0.0054 | 28.4352
1.536 | 1.6221 | 0.05628 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3293 | 28.6971 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5306 | 0.054046 | 1.0978 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2683 | 28.4445 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5306 | 0.054046 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2683 | 28.4445 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5306 | 0.054046 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2683 | 1536 | 2268.348 | 0.97823 | 1.0976 | 0.0054 | 28.4445
1.537 | 1.6232 | 0.056281 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3316 | 28.7064 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5316 | 0.054047 | 1.0978 | 1.0977 | 1.0976 | 1.0976 | 0.97823 | 2.2706 | 28.4538 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5316 | 0.054047 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2706 | 28.4538 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5316 | 0.054047 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2706 | 1537 | 2270.577 | 0.97823 | 1.0976 | 0.0054 | 28.4538
1.538 | 1.6242 | 0.056282 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3339 | 28.7158 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5326 | 0.054048 | 1.0978 | 1.0977 | 1.0976 | 1.0976 | 0.97823 | 2.2728 | 28.4632 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5326 | 0.054048 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2728 | 28.4632 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5326 | 0.054048 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97823 | 2.2728 | 1538 | 2272.8067 | 0.97823 | 1.0976 | 0.0054 | 28.4632
1.539 | 1.6253 | 0.056283 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3361 | 28.7251 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5336 | 0.05405 | 1.0978 | 1.0977 | 1.0976 | 1.0976 | 0.97824 | 2.275 | 28.4725 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5336 | 0.05405 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97824 | 2.275 | 28.4725 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5336 | 0.05405 | 1.0976 | 1.0976 | 1.0976 | 1.0976 | 0.97824 | 2.275 | 1539 | 2275.0372 | 0.97824 | 1.0976 | 0.0054 | 28.4725
1.54 | 1.6263 | 0.056284 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3384 | 28.7345 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5346 | 0.054051 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97824 | 2.2773 | 28.4818 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5346 | 0.054051 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97824 | 2.2773 | 28.4818 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5346 | 0.054051 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97824 | 2.2773 | 1540 | 2277.2684 | 0.97824 | 1.0977 | 0.0054 | 28.4818
1.541 | 1.6273 | 0.056285 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3407 | 28.7438 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5356 | 0.054052 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97824 | 2.2795 | 28.4911 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5356 | 0.054052 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97824 | 2.2795 | 28.4911 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5356 | 0.054052 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97824 | 2.2795 | 1541 | 2279.5003 | 0.97824 | 1.0977 | 0.0054 | 28.4911
1.542 | 1.6284 | 0.056286 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.343 | 28.7532 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5366 | 0.054053 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.2817 | 28.5004 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5366 | 0.054053 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.2817 | 28.5004 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5366 | 0.054053 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.2817 | 1542 | 2281.7329 | 0.97825 | 1.0977 | 0.0054 | 28.5004
1.543 | 1.6294 | 0.056287 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3453 | 28.7625 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5376 | 0.054055 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.284 | 28.5097 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5376 | 0.054055 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.284 | 28.5097 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5376 | 0.054055 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.284 | 1543 | 2283.9663 | 0.97825 | 1.0977 | 0.0054 | 28.5097
1.544 | 1.6305 | 0.056288 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3476 | 28.7719 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5386 | 0.054056 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.2862 | 28.519 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5386 | 0.054056 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.2862 | 28.519 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5386 | 0.054056 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97825 | 2.2862 | 1544 | 2286.2004 | 0.97825 | 1.0977 | 0.0054 | 28.519
1.545 | 1.6315 | 0.056289 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3498 | 28.7812 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5396 | 0.054057 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2884 | 28.5282 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5396 | 0.054057 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2884 | 28.5282 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5396 | 0.054057 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2884 | 1545 | 2288.4352 | 0.97826 | 1.0977 | 0.0054 | 28.5282
1.546 | 1.6325 | 0.05629 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3521 | 28.7905 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5406 | 0.054058 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2907 | 28.5375 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5406 | 0.054058 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2907 | 28.5375 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5406 | 0.054058 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2907 | 1546 | 2290.6708 | 0.97826 | 1.0977 | 0.0054 | 28.5375
1.547 | 1.6336 | 0.056291 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3544 | 28.7998 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5416 | 0.054059 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2929 | 28.5468 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5416 | 0.054059 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2929 | 28.5468 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5416 | 0.054059 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97826 | 2.2929 | 1547 | 2292.9071 | 0.97826 | 1.0977 | 0.0054 | 28.5468
1.548 | 1.6346 | 0.056292 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3567 | 28.8092 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5426 | 0.054061 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2951 | 28.5561 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5426 | 0.054061 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2951 | 28.5561 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5426 | 0.054061 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2951 | 1548 | 2295.1441 | 0.97827 | 1.0977 | 0.0054 | 28.5561
1.549 | 1.6357 | 0.056293 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.359 | 28.8185 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5436 | 0.054062 | 1.0978 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2974 | 28.5654 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5436 | 0.054062 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2974 | 28.5654 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5436 | 0.054062 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2974 | 1549 | 2297.3819 | 0.97827 | 1.0977 | 0.0054 | 28.5654
1.55 | 1.6367 | 0.056294 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3613 | 28.8278 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5446 | 0.054063 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2996 | 28.5747 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5446 | 0.054063 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2996 | 28.5747 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5446 | 0.054063 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97827 | 2.2996 | 1550 | 2299.6203 | 0.97827 | 1.0977 | 0.0054 | 28.5747
1.551 | 1.6378 | 0.056295 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3636 | 28.8371 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5456 | 0.054064 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3019 | 28.5839 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5456 | 0.054064 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3019 | 28.5839 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5456 | 0.054064 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3019 | 1551 | 2301.8595 | 0.97828 | 1.0977 | 0.0054 | 28.5839
1.552 | 1.6388 | 0.056296 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3659 | 28.8465 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5466 | 0.054066 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3041 | 28.5932 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5466 | 0.054066 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3041 | 28.5932 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5466 | 0.054066 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3041 | 1552 | 2304.0994 | 0.97828 | 1.0977 | 0.0054 | 28.5932
1.553 | 1.6398 | 0.056297 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3682 | 28.8558 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5476 | 0.054067 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3063 | 28.6025 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5476 | 0.054067 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3063 | 28.6025 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5476 | 0.054067 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97828 | 2.3063 | 1553 | 2306.3401 | 0.97828 | 1.0977 | 0.0054 | 28.6025
1.554 | 1.6409 | 0.056298 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3705 | 28.8651 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5486 | 0.054068 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3086 | 28.6117 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5486 | 0.054068 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3086 | 28.6117 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5486 | 0.054068 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3086 | 1554 | 2308.5815 | 0.97829 | 1.0977 | 0.0054 | 28.6117
1.555 | 1.6419 | 0.056299 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3727 | 28.8744 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5496 | 0.054069 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3108 | 28.621 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5496 | 0.054069 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3108 | 28.621 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5496 | 0.054069 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3108 | 1555 | 2310.8236 | 0.97829 | 1.0977 | 0.0054 | 28.621
1.556 | 1.643 | 0.0563 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.375 | 28.8837 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5506 | 0.05407 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3131 | 28.6302 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5506 | 0.05407 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3131 | 28.6302 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5506 | 0.05407 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97829 | 2.3131 | 1556 | 2313.0664 | 0.97829 | 1.0977 | 0.0054 | 28.6302
1.557 | 1.644 | 0.056301 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3773 | 28.893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5516 | 0.054072 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3153 | 28.6395 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5516 | 0.054072 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3153 | 28.6395 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5516 | 0.054072 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3153 | 1557 | 2315.3099 | 0.9783 | 1.0977 | 0.0054 | 28.6395
1.558 | 1.645 | 0.056302 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3796 | 28.9023 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5526 | 0.054073 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3176 | 28.6487 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5526 | 0.054073 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3176 | 28.6487 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5526 | 0.054073 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3176 | 1558 | 2317.5542 | 0.9783 | 1.0977 | 0.0054 | 28.6487
1.559 | 1.6461 | 0.056303 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3819 | 28.9116 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5536 | 0.054074 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3198 | 28.658 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5536 | 0.054074 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3198 | 28.658 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5536 | 0.054074 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.9783 | 2.3198 | 1559 | 2319.7992 | 0.9783 | 1.0977 | 0.0054 | 28.658
1.56 | 1.6471 | 0.056304 | 1.1025 | 1.1026 | 1.1026 | 1.1026 | 2.3842 | 28.9209 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5546 | 0.054075 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.322 | 28.6672 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5546 | 0.054075 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.322 | 28.6672 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5546 | 0.054075 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.322 | 1560 | 2322.045 | 0.97831 | 1.0977 | 0.0054 | 28.6672
1.561 | 1.6482 | 0.056305 | 1.1025 | 1.1026 | 1.1027 | 1.1027 | 2.3865 | 28.9301 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5556 | 0.054076 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.3243 | 28.6765 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5556 | 0.054076 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.3243 | 28.6765 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5556 | 0.054076 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.3243 | 1561 | 2324.2914 | 0.97831 | 1.0977 | 0.0054 | 28.6765
1.562 | 1.6492 | 0.056306 | 1.1026 | 1.1026 | 1.1027 | 1.1027 | 2.3888 | 28.9394 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5566 | 0.054078 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.3265 | 28.6857 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5566 | 0.054078 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.3265 | 28.6857 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5566 | 0.054078 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97831 | 2.3265 | 1562 | 2326.5386 | 0.97831 | 1.0977 | 0.0054 | 28.6857
1.563 | 1.6502 | 0.056307 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.3911 | 28.9487 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5576 | 0.054079 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.3288 | 28.6949 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5576 | 0.054079 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.3288 | 28.6949 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5576 | 0.054079 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.3288 | 1563 | 2328.7865 | 0.97832 | 1.0977 | 0.0054 | 28.6949
1.564 | 1.6513 | 0.056308 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.3934 | 28.958 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5586 | 0.05408 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.331 | 28.7042 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5586 | 0.05408 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.331 | 28.7042 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5586 | 0.05408 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.331 | 1564 | 2331.0351 | 0.97832 | 1.0977 | 0.0054 | 28.7042
1.565 | 1.6523 | 0.056309 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.3957 | 28.9673 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5596 | 0.054081 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.3333 | 28.7134 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5596 | 0.054081 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.3333 | 28.7134 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5596 | 0.054081 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97832 | 2.3333 | 1565 | 2333.2845 | 0.97832 | 1.0977 | 0.0054 | 28.7134
1.566 | 1.6534 | 0.05631 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.398 | 28.9765 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5606 | 0.054082 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.3355 | 28.7226 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5606 | 0.054082 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.3355 | 28.7226 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5606 | 0.054082 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.3355 | 1566 | 2335.5345 | 0.97833 | 1.0977 | 0.0054 | 28.7226
1.567 | 1.6544 | 0.056311 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4003 | 28.9858 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5616 | 0.054084 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.3378 | 28.7319 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5616 | 0.054084 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.3378 | 28.7319 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5616 | 0.054084 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.3378 | 1567 | 2337.7853 | 0.97833 | 1.0977 | 0.0054 | 28.7319
1.568 | 1.6555 | 0.056312 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4026 | 28.9951 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5626 | 0.054085 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.34 | 28.7411 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5626 | 0.054085 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.34 | 28.7411 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5626 | 0.054085 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97833 | 2.34 | 1568 | 2340.0368 | 0.97833 | 1.0977 | 0.0054 | 28.7411
1.569 | 1.6565 | 0.056313 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4049 | 29.0043 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5636 | 0.054086 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3423 | 28.7503 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5636 | 0.054086 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3423 | 28.7503 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5636 | 0.054086 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3423 | 1569 | 2342.2891 | 0.97834 | 1.0977 | 0.0054 | 28.7503
1.57 | 1.6575 | 0.056314 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4072 | 29.0136 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5646 | 0.054087 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3445 | 28.7595 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5646 | 0.054087 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3445 | 28.7595 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5646 | 0.054087 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3445 | 1570 | 2344.542 | 0.97834 | 1.0977 | 0.0054 | 28.7595
1.571 | 1.6586 | 0.056315 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4095 | 29.0229 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5656 | 0.054088 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3468 | 28.7687 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5656 | 0.054088 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3468 | 28.7687 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5656 | 0.054088 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97834 | 2.3468 | 1571 | 2346.7957 | 0.97834 | 1.0977 | 0.0054 | 28.7687
1.572 | 1.6596 | 0.056316 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4118 | 29.0321 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5666 | 0.05409 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3491 | 28.7779 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5666 | 0.05409 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3491 | 28.7779 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5666 | 0.05409 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3491 | 1572 | 2349.0501 | 0.97835 | 1.0977 | 0.0054 | 28.7779
1.573 | 1.6607 | 0.056317 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4142 | 29.0414 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5676 | 0.054091 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3513 | 28.7871 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5676 | 0.054091 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3513 | 28.7871 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5676 | 0.054091 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3513 | 1573 | 2351.3052 | 0.97835 | 1.0977 | 0.0054 | 28.7871
1.574 | 1.6617 | 0.056318 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4165 | 29.0506 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5686 | 0.054092 | 1.0979 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3536 | 28.7963 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5686 | 0.054092 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3536 | 28.7963 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5686 | 0.054092 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3536 | 1574 | 2353.5611 | 0.97835 | 1.0977 | 0.0054 | 28.7963
1.575 | 1.6627 | 0.056319 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4188 | 29.0599 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5696 | 0.054093 | 1.0979 | 1.0978 | 1.0977 | 1.0977 | 0.97835 | 2.3558 | 28.8055 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5696 | 0.054093 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3558 | 28.8055 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5696 | 0.054093 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97835 | 2.3558 | 1575 | 2355.8177 | 0.97835 | 1.0977 | 0.0054 | 28.8055
1.576 | 1.6638 | 0.05632 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4211 | 29.0691 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5706 | 0.054094 | 1.0979 | 1.0978 | 1.0977 | 1.0977 | 0.97836 | 2.3581 | 28.8147 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5706 | 0.054094 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97836 | 2.3581 | 28.8147 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5706 | 0.054094 | 1.0977 | 1.0977 | 1.0977 | 1.0977 | 0.97836 | 2.3581 | 1576 | 2358.075 | 0.97836 | 1.0977 | 0.0054 | 28.8147
1.577 | 1.6648 | 0.056321 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4234 | 29.0783 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5716 | 0.054095 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97836 | 2.3603 | 28.8239 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5716 | 0.054095 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97836 | 2.3603 | 28.8239 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5716 | 0.054095 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97836 | 2.3603 | 1577 | 2360.333 | 0.97836 | 1.0978 | 0.0054 | 28.8239
1.578 | 1.6659 | 0.056322 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4257 | 29.0876 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5726 | 0.054097 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97836 | 2.3626 | 28.8331 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5726 | 0.054097 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97836 | 2.3626 | 28.8331 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5726 | 0.054097 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97836 | 2.3626 | 1578 | 2362.5917 | 0.97836 | 1.0978 | 0.0054 | 28.8331
1.579 | 1.6669 | 0.056323 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.428 | 29.0968 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5736 | 0.054098 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3649 | 28.8423 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5736 | 0.054098 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3649 | 28.8423 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5736 | 0.054098 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3649 | 1579 | 2364.8512 | 0.97837 | 1.0978 | 0.0054 | 28.8423
1.58 | 1.6679 | 0.056324 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4303 | 29.1061 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5746 | 0.054099 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3671 | 28.8515 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5746 | 0.054099 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3671 | 28.8515 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5746 | 0.054099 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3671 | 1580 | 2367.1113 | 0.97837 | 1.0978 | 0.0054 | 28.8515
1.581 | 1.669 | 0.056325 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4326 | 29.1153 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5756 | 0.0541 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3694 | 28.8607 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5756 | 0.0541 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3694 | 28.8607 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5756 | 0.0541 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97837 | 2.3694 | 1581 | 2369.3722 | 0.97837 | 1.0978 | 0.0054 | 28.8607
1.582 | 1.67 | 0.056326 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4349 | 29.1245 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5766 | 0.054101 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3716 | 28.8699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5766 | 0.054101 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3716 | 28.8699 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5766 | 0.054101 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3716 | 1582 | 2371.6338 | 0.97838 | 1.0978 | 0.0054 | 28.8699
1.583 | 1.6711 | 0.056327 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4373 | 29.1337 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5776 | 0.054103 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3739 | 28.879 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5776 | 0.054103 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3739 | 28.879 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5776 | 0.054103 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3739 | 1583 | 2373.8962 | 0.97838 | 1.0978 | 0.0054 | 28.879
1.584 | 1.6721 | 0.056328 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4396 | 29.1429 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5786 | 0.054104 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3762 | 28.8882 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5786 | 0.054104 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3762 | 28.8882 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5786 | 0.054104 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97838 | 2.3762 | 1584 | 2376.1592 | 0.97838 | 1.0978 | 0.0054 | 28.8882
1.585 | 1.6732 | 0.056329 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4419 | 29.1522 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5796 | 0.054105 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.3784 | 28.8974 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5796 | 0.054105 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.3784 | 28.8974 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5796 | 0.054105 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.3784 | 1585 | 2378.423 | 0.97839 | 1.0978 | 0.0054 | 28.8974
1.586 | 1.6742 | 0.05633 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4442 | 29.1614 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5806 | 0.054106 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.3807 | 28.9066 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5806 | 0.054106 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.3807 | 28.9066 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5806 | 0.054106 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.3807 | 1586 | 2380.6875 | 0.97839 | 1.0978 | 0.0054 | 28.9066
1.587 | 1.6752 | 0.056331 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4465 | 29.1706 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5816 | 0.054107 | 1.0979 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.383 | 28.9157 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5816 | 0.054107 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.383 | 28.9157 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5816 | 0.054107 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97839 | 2.383 | 1587 | 2382.9527 | 0.97839 | 1.0978 | 0.0054 | 28.9157
1.588 | 1.6763 | 0.056332 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4488 | 29.1798 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5826 | 0.054108 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3852 | 28.9249 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5826 | 0.054108 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3852 | 28.9249 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5826 | 0.054108 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3852 | 1588 | 2385.2186 | 0.9784 | 1.0978 | 0.0054 | 28.9249
1.589 | 1.6773 | 0.056333 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4512 | 29.189 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5836 | 0.05411 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3875 | 28.934 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5836 | 0.05411 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3875 | 28.934 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5836 | 0.05411 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3875 | 1589 | 2387.4852 | 0.9784 | 1.0978 | 0.0054 | 28.934
1.59 | 1.6784 | 0.056334 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4535 | 29.1982 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5846 | 0.054111 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3898 | 28.9432 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5846 | 0.054111 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3898 | 28.9432 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5846 | 0.054111 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.9784 | 2.3898 | 1590 | 2389.7526 | 0.9784 | 1.0978 | 0.0054 | 28.9432
1.591 | 1.6794 | 0.056335 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4558 | 29.2074 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5856 | 0.054112 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.392 | 28.9524 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5856 | 0.054112 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.392 | 28.9524 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5856 | 0.054112 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.392 | 1591 | 2392.0207 | 0.97841 | 1.0978 | 0.0054 | 28.9524
1.592 | 1.6804 | 0.056336 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4581 | 29.2166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5866 | 0.054113 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.3943 | 28.9615 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5866 | 0.054113 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.3943 | 28.9615 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5866 | 0.054113 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.3943 | 1592 | 2394.2895 | 0.97841 | 1.0978 | 0.0054 | 28.9615
1.593 | 1.6815 | 0.056337 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4604 | 29.2258 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5876 | 0.054114 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.3966 | 28.9707 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5876 | 0.054114 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.3966 | 28.9707 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5876 | 0.054114 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97841 | 2.3966 | 1593 | 2396.559 | 0.97841 | 1.0978 | 0.0054 | 28.9707
1.594 | 1.6825 | 0.056338 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4628 | 29.235 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5886 | 0.054115 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.3988 | 28.9798 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5886 | 0.054115 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.3988 | 28.9798 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5886 | 0.054115 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.3988 | 1594 | 2398.8292 | 0.97842 | 1.0978 | 0.0054 | 28.9798
1.595 | 1.6836 | 0.056339 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4651 | 29.2442 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5896 | 0.054116 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4011 | 28.9889 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5896 | 0.054116 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4011 | 28.9889 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5896 | 0.054116 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4011 | 1595 | 2401.1002 | 0.97842 | 1.0978 | 0.0054 | 28.9889
1.596 | 1.6846 | 0.05634 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4674 | 29.2534 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5906 | 0.054118 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4034 | 28.9981 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5906 | 0.054118 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4034 | 28.9981 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5906 | 0.054118 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4034 | 1596 | 2403.3718 | 0.97842 | 1.0978 | 0.0054 | 28.9981
1.597 | 1.6856 | 0.056341 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4697 | 29.2625 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5916 | 0.054119 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4056 | 29.0072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5916 | 0.054119 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4056 | 29.0072 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5916 | 0.054119 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97842 | 2.4056 | 1597 | 2405.6442 | 0.97842 | 1.0978 | 0.0054 | 29.0072
1.598 | 1.6867 | 0.056342 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4721 | 29.2717 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5926 | 0.05412 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4079 | 29.0163 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5926 | 0.05412 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4079 | 29.0163 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5926 | 0.05412 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4079 | 1598 | 2407.9173 | 0.97843 | 1.0978 | 0.0054 | 29.0163
1.599 | 1.6877 | 0.056343 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4744 | 29.2809 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5936 | 0.054121 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4102 | 29.0255 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5936 | 0.054121 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4102 | 29.0255 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5936 | 0.054121 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4102 | 1599 | 2410.1911 | 0.97843 | 1.0978 | 0.0054 | 29.0255
1.6 | 1.6888 | 0.056344 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4767 | 29.2901 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5946 | 0.054122 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4125 | 29.0346 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5946 | 0.054122 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4125 | 29.0346 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5946 | 0.054122 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97843 | 2.4125 | 1600 | 2412.4656 | 0.97843 | 1.0978 | 0.0054 | 29.0346
1.601 | 1.6898 | 0.056345 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.479 | 29.2992 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5956 | 0.054123 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.4147 | 29.0437 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5956 | 0.054123 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.4147 | 29.0437 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5956 | 0.054123 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.4147 | 1601 | 2414.7409 | 0.97844 | 1.0978 | 0.0054 | 29.0437
1.602 | 1.6909 | 0.056346 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4814 | 29.3084 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5966 | 0.054125 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.417 | 29.0529 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5966 | 0.054125 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.417 | 29.0529 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5966 | 0.054125 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.417 | 1602 | 2417.0168 | 0.97844 | 1.0978 | 0.0054 | 29.0529
1.603 | 1.6919 | 0.056346 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4837 | 29.3176 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5976 | 0.054126 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.4193 | 29.062 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5976 | 0.054126 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.4193 | 29.062 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5976 | 0.054126 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97844 | 2.4193 | 1603 | 2419.2935 | 0.97844 | 1.0978 | 0.0054 | 29.062
1.604 | 1.6929 | 0.056347 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.486 | 29.3267 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5986 | 0.054127 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4216 | 29.0711 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5986 | 0.054127 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4216 | 29.0711 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5986 | 0.054127 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4216 | 1604 | 2421.5709 | 0.97845 | 1.0978 | 0.0054 | 29.0711
1.605 | 1.694 | 0.056348 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4883 | 29.3359 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5996 | 0.054128 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4238 | 29.0802 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5996 | 0.054128 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4238 | 29.0802 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.5996 | 0.054128 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4238 | 1605 | 2423.849 | 0.97845 | 1.0978 | 0.0054 | 29.0802
1.606 | 1.695 | 0.056349 | 1.1026 | 1.1027 | 1.1027 | 1.1027 | 2.4907 | 29.3451 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6006 | 0.054129 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4261 | 29.0893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6006 | 0.054129 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4261 | 29.0893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6006 | 0.054129 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97845 | 2.4261 | 1606 | 2426.1278 | 0.97845 | 1.0978 | 0.0054 | 29.0893
1.607 | 1.6961 | 0.05635 | 1.1026 | 1.1027 | 1.1028 | 1.1028 | 2.493 | 29.3542 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6016 | 0.05413 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4284 | 29.0984 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6016 | 0.05413 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4284 | 29.0984 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6016 | 0.05413 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4284 | 1607 | 2428.4073 | 0.97846 | 1.0978 | 0.0054 | 29.0984
1.608 | 1.6971 | 0.056351 | 1.1026 | 1.1027 | 1.1028 | 1.1028 | 2.4953 | 29.3634 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6026 | 0.054131 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4307 | 29.1075 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6026 | 0.054131 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4307 | 29.1075 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6026 | 0.054131 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4307 | 1608 | 2430.6876 | 0.97846 | 1.0978 | 0.0054 | 29.1075
1.609 | 1.6981 | 0.056352 | 1.1026 | 1.1028 | 1.1028 | 1.1028 | 2.4977 | 29.3725 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6036 | 0.054133 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.433 | 29.1166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6036 | 0.054133 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.433 | 29.1166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6036 | 0.054133 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.433 | 1609 | 2432.9685 | 0.97846 | 1.0978 | 0.0054 | 29.1166
1.61 | 1.6992 | 0.056353 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5 | 29.3816 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6046 | 0.054134 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4353 | 29.1257 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6046 | 0.054134 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4353 | 29.1257 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6046 | 0.054134 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97846 | 2.4353 | 1610 | 2435.2502 | 0.97846 | 1.0978 | 0.0054 | 29.1257
1.611 | 1.7002 | 0.056354 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5023 | 29.3908 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6056 | 0.054135 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4375 | 29.1348 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6056 | 0.054135 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4375 | 29.1348 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6056 | 0.054135 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4375 | 1611 | 2437.5326 | 0.97847 | 1.0978 | 0.0054 | 29.1348
1.612 | 1.7013 | 0.056355 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5047 | 29.3999 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6066 | 0.054136 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4398 | 29.1439 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6066 | 0.054136 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4398 | 29.1439 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6066 | 0.054136 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4398 | 1612 | 2439.8156 | 0.97847 | 1.0978 | 0.0054 | 29.1439
1.613 | 1.7023 | 0.056356 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.507 | 29.4091 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6076 | 0.054137 | 1.098 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4421 | 29.153 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6076 | 0.054137 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4421 | 29.153 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6076 | 0.054137 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97847 | 2.4421 | 1613 | 2442.0995 | 0.97847 | 1.0978 | 0.0054 | 29.153
1.614 | 1.7033 | 0.056357 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5094 | 29.4182 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6086 | 0.054138 | 1.098 | 1.0979 | 1.0978 | 1.0978 | 0.97848 | 2.4444 | 29.1621 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6086 | 0.054138 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97848 | 2.4444 | 29.1621 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6086 | 0.054138 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97848 | 2.4444 | 1614 | 2444.384 | 0.97848 | 1.0978 | 0.0054 | 29.1621
1.615 | 1.7044 | 0.056358 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5117 | 29.4273 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6096 | 0.054139 | 1.098 | 1.0979 | 1.0978 | 1.0978 | 0.97848 | 2.4467 | 29.1712 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6096 | 0.054139 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97848 | 2.4467 | 29.1712 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6096 | 0.054139 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97848 | 2.4467 | 1615 | 2446.6692 | 0.97848 | 1.0978 | 0.0054 | 29.1712
1.616 | 1.7054 | 0.056359 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.514 | 29.4365 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6106 | 0.05414 | 1.098 | 1.0979 | 1.0978 | 1.0978 | 0.97848 | 2.449 | 29.1803 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6106 | 0.05414 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97848 | 2.449 | 29.1803 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6106 | 0.05414 | 1.0978 | 1.0978 | 1.0978 | 1.0978 | 0.97848 | 2.449 | 1616 | 2448.9551 | 0.97848 | 1.0978 | 0.0054 | 29.1803
1.617 | 1.7065 | 0.05636 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5164 | 29.4456 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6116 | 0.054142 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4512 | 29.1893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6116 | 0.054142 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4512 | 29.1893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6116 | 0.054142 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4512 | 1617 | 2451.2418 | 0.97849 | 1.0979 | 0.0054 | 29.1893
1.618 | 1.7075 | 0.056361 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5187 | 29.4547 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6126 | 0.054143 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4535 | 29.1984 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6126 | 0.054143 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4535 | 29.1984 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6126 | 0.054143 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4535 | 1618 | 2453.5292 | 0.97849 | 1.0979 | 0.0054 | 29.1984
1.619 | 1.7086 | 0.056362 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.521 | 29.4638 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6136 | 0.054144 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4558 | 29.2075 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6136 | 0.054144 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4558 | 29.2075 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6136 | 0.054144 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97849 | 2.4558 | 1619 | 2455.8172 | 0.97849 | 1.0979 | 0.0054 | 29.2075
1.62 | 1.7096 | 0.056362 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5234 | 29.4729 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6146 | 0.054145 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4581 | 29.2166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6146 | 0.054145 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4581 | 29.2166 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6146 | 0.054145 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4581 | 1620 | 2458.106 | 0.9785 | 1.0979 | 0.0054 | 29.2166
1.621 | 1.7106 | 0.056363 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5257 | 29.4821 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6156 | 0.054146 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4604 | 29.2256 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6156 | 0.054146 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4604 | 29.2256 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6156 | 0.054146 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4604 | 1621 | 2460.3955 | 0.9785 | 1.0979 | 0.0054 | 29.2256
1.622 | 1.7117 | 0.056364 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5281 | 29.4912 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6166 | 0.054147 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4627 | 29.2347 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6166 | 0.054147 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4627 | 29.2347 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6166 | 0.054147 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.4627 | 1622 | 2462.6857 | 0.9785 | 1.0979 | 0.0054 | 29.2347
1.623 | 1.7127 | 0.056365 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5304 | 29.5003 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6176 | 0.054148 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.465 | 29.2438 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6176 | 0.054148 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.465 | 29.2438 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6176 | 0.054148 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9785 | 2.465 | 1623 | 2464.9767 | 0.9785 | 1.0979 | 0.0054 | 29.2438
1.624 | 1.7138 | 0.056366 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5328 | 29.5094 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6186 | 0.054149 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4673 | 29.2528 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6186 | 0.054149 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4673 | 29.2528 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6186 | 0.054149 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4673 | 1624 | 2467.2683 | 0.97851 | 1.0979 | 0.0054 | 29.2528
1.625 | 1.7148 | 0.056367 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5351 | 29.5185 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6196 | 0.05415 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4696 | 29.2619 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6196 | 0.05415 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4696 | 29.2619 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6196 | 0.05415 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4696 | 1625 | 2469.5606 | 0.97851 | 1.0979 | 0.0054 | 29.2619
1.626 | 1.7158 | 0.056368 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5374 | 29.5276 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6206 | 0.054152 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4719 | 29.2709 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6206 | 0.054152 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4719 | 29.2709 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6206 | 0.054152 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97851 | 2.4719 | 1626 | 2471.8537 | 0.97851 | 1.0979 | 0.0054 | 29.2709
1.627 | 1.7169 | 0.056369 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5398 | 29.5367 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6216 | 0.054153 | 1.098 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4741 | 29.28 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6216 | 0.054153 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4741 | 29.28 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6216 | 0.054153 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4741 | 1627 | 2474.1474 | 0.97852 | 1.0979 | 0.0054 | 29.28
1.628 | 1.7179 | 0.05637 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5421 | 29.5458 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6226 | 0.054154 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4764 | 29.289 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6226 | 0.054154 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4764 | 29.289 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6226 | 0.054154 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4764 | 1628 | 2476.4419 | 0.97852 | 1.0979 | 0.0054 | 29.289
1.629 | 1.719 | 0.056371 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5445 | 29.5549 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6236 | 0.054155 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4787 | 29.2981 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6236 | 0.054155 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4787 | 29.2981 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6236 | 0.054155 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97852 | 2.4787 | 1629 | 2478.7371 | 0.97852 | 1.0979 | 0.0054 | 29.2981
1.63 | 1.72 | 0.056372 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5468 | 29.564 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6246 | 0.054156 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.481 | 29.3071 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6246 | 0.054156 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.481 | 29.3071 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6246 | 0.054156 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.481 | 1630 | 2481.033 | 0.97853 | 1.0979 | 0.0054 | 29.3071
1.631 | 1.721 | 0.056373 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5492 | 29.573 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6256 | 0.054157 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4833 | 29.3162 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6256 | 0.054157 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4833 | 29.3162 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6256 | 0.054157 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4833 | 1631 | 2483.3296 | 0.97853 | 1.0979 | 0.0054 | 29.3162
1.632 | 1.7221 | 0.056374 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5515 | 29.5821 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6266 | 0.054158 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4856 | 29.3252 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6266 | 0.054158 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4856 | 29.3252 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6266 | 0.054158 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4856 | 1632 | 2485.6269 | 0.97853 | 1.0979 | 0.0054 | 29.3252
1.633 | 1.7231 | 0.056375 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5539 | 29.5912 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6276 | 0.054159 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4879 | 29.3342 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6276 | 0.054159 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4879 | 29.3342 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6276 | 0.054159 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97853 | 2.4879 | 1633 | 2487.9249 | 0.97853 | 1.0979 | 0.0054 | 29.3342
1.634 | 1.7242 | 0.056375 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5562 | 29.6003 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6286 | 0.05416 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4902 | 29.3433 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6286 | 0.05416 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4902 | 29.3433 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6286 | 0.05416 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4902 | 1634 | 2490.2236 | 0.97854 | 1.0979 | 0.0054 | 29.3433
1.635 | 1.7252 | 0.056376 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5586 | 29.6094 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6296 | 0.054162 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4925 | 29.3523 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6296 | 0.054162 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4925 | 29.3523 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6296 | 0.054162 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4925 | 1635 | 2492.523 | 0.97854 | 1.0979 | 0.0054 | 29.3523
1.636 | 1.7263 | 0.056377 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5609 | 29.6184 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6306 | 0.054163 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4948 | 29.3613 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6306 | 0.054163 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4948 | 29.3613 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6306 | 0.054163 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97854 | 2.4948 | 1636 | 2494.8232 | 0.97854 | 1.0979 | 0.0054 | 29.3613
1.637 | 1.7273 | 0.056378 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5633 | 29.6275 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6316 | 0.054164 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.4971 | 29.3703 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6316 | 0.054164 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.4971 | 29.3703 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6316 | 0.054164 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.4971 | 1637 | 2497.124 | 0.97855 | 1.0979 | 0.0054 | 29.3703
1.638 | 1.7283 | 0.056379 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5656 | 29.6366 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6326 | 0.054165 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.4994 | 29.3794 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6326 | 0.054165 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.4994 | 29.3794 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6326 | 0.054165 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.4994 | 1638 | 2499.4256 | 0.97855 | 1.0979 | 0.0054 | 29.3794
1.639 | 1.7294 | 0.05638 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.568 | 29.6456 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6336 | 0.054166 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.5017 | 29.3884 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6336 | 0.054166 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.5017 | 29.3884 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6336 | 0.054166 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.5017 | 1639 | 2501.7278 | 0.97855 | 1.0979 | 0.0054 | 29.3884
1.64 | 1.7304 | 0.056381 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5704 | 29.6547 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6346 | 0.054167 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.504 | 29.3974 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6346 | 0.054167 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.504 | 29.3974 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6346 | 0.054167 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97855 | 2.504 | 1640 | 2504.0308 | 0.97855 | 1.0979 | 0.0054 | 29.3974
1.641 | 1.7315 | 0.056382 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5727 | 29.6637 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6356 | 0.054168 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5063 | 29.4064 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6356 | 0.054168 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5063 | 29.4064 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6356 | 0.054168 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5063 | 1641 | 2506.3344 | 0.97856 | 1.0979 | 0.0054 | 29.4064
1.642 | 1.7325 | 0.056383 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5751 | 29.6728 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6366 | 0.054169 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5086 | 29.4154 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6366 | 0.054169 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5086 | 29.4154 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6366 | 0.054169 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5086 | 1642 | 2508.6388 | 0.97856 | 1.0979 | 0.0054 | 29.4154
1.643 | 1.7335 | 0.056384 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5774 | 29.6819 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6376 | 0.05417 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5109 | 29.4244 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6376 | 0.05417 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5109 | 29.4244 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6376 | 0.05417 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97856 | 2.5109 | 1643 | 2510.9439 | 0.97856 | 1.0979 | 0.0054 | 29.4244
1.644 | 1.7346 | 0.056385 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5798 | 29.6909 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6386 | 0.054171 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5132 | 29.4334 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6386 | 0.054171 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5132 | 29.4334 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6386 | 0.054171 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5132 | 1644 | 2513.2497 | 0.97857 | 1.0979 | 0.0054 | 29.4334
1.645 | 1.7356 | 0.056385 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5821 | 29.6999 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6396 | 0.054172 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5156 | 29.4424 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6396 | 0.054172 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5156 | 29.4424 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6396 | 0.054172 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5156 | 1645 | 2515.5562 | 0.97857 | 1.0979 | 0.0054 | 29.4424
1.646 | 1.7367 | 0.056386 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5845 | 29.709 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6406 | 0.054174 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5179 | 29.4514 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6406 | 0.054174 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5179 | 29.4514 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6406 | 0.054174 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97857 | 2.5179 | 1646 | 2517.8634 | 0.97857 | 1.0979 | 0.0054 | 29.4514
1.647 | 1.7377 | 0.056387 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5869 | 29.718 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6416 | 0.054175 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5202 | 29.4604 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6416 | 0.054175 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5202 | 29.4604 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6416 | 0.054175 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5202 | 1647 | 2520.1713 | 0.97858 | 1.0979 | 0.0054 | 29.4604
1.648 | 1.7387 | 0.056388 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5892 | 29.7271 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6426 | 0.054176 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5225 | 29.4694 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6426 | 0.054176 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5225 | 29.4694 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6426 | 0.054176 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5225 | 1648 | 2522.4799 | 0.97858 | 1.0979 | 0.0054 | 29.4694
1.649 | 1.7398 | 0.056389 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5916 | 29.7361 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6436 | 0.054177 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5248 | 29.4784 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6436 | 0.054177 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5248 | 29.4784 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6436 | 0.054177 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5248 | 1649 | 2524.7892 | 0.97858 | 1.0979 | 0.0054 | 29.4784
1.65 | 1.7408 | 0.05639 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5939 | 29.7451 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6446 | 0.054178 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5271 | 29.4874 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6446 | 0.054178 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5271 | 29.4874 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6446 | 0.054178 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97858 | 2.5271 | 1650 | 2527.0992 | 0.97858 | 1.0979 | 0.0054 | 29.4874
1.651 | 1.7419 | 0.056391 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5963 | 29.7542 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6456 | 0.054179 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.5294 | 29.4964 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6456 | 0.054179 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.5294 | 29.4964 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6456 | 0.054179 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.5294 | 1651 | 2529.4099 | 0.97859 | 1.0979 | 0.0054 | 29.4964
1.652 | 1.7429 | 0.056392 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.5987 | 29.7632 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6466 | 0.05418 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.5317 | 29.5054 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6466 | 0.05418 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.5317 | 29.5054 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6466 | 0.05418 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.5317 | 1652 | 2531.7214 | 0.97859 | 1.0979 | 0.0054 | 29.5054
1.653 | 1.744 | 0.056393 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.601 | 29.7722 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6476 | 0.054181 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.534 | 29.5143 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6476 | 0.054181 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.534 | 29.5143 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6476 | 0.054181 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.97859 | 2.534 | 1653 | 2534.0335 | 0.97859 | 1.0979 | 0.0054 | 29.5143
1.654 | 1.745 | 0.056394 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.6034 | 29.7812 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6486 | 0.054182 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5363 | 29.5233 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6486 | 0.054182 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5363 | 29.5233 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6486 | 0.054182 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5363 | 1654 | 2536.3463 | 0.9786 | 1.0979 | 0.0054 | 29.5233
1.655 | 1.746 | 0.056394 | 1.1027 | 1.1028 | 1.1028 | 1.1028 | 2.6058 | 29.7903 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6496 | 0.054183 | 1.0981 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5387 | 29.5323 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6496 | 0.054183 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5387 | 29.5323 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6496 | 0.054183 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5387 | 1655 | 2538.6599 | 0.9786 | 1.0979 | 0.0054 | 29.5323
1.656 | 1.7471 | 0.056395 | 1.1027 | 1.1028 | 1.1029 | 1.1029 | 2.6081 | 29.7993 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6506 | 0.054184 | 1.0981 | 1.098 | 1.0979 | 1.0979 | 0.9786 | 2.541 | 29.5413 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6506 | 0.054184 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.541 | 29.5413 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6506 | 0.054184 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.541 | 1656 | 2540.9741 | 0.9786 | 1.0979 | 0.0054 | 29.5413
1.657 | 1.7481 | 0.056396 | 1.1027 | 1.1028 | 1.1029 | 1.1029 | 2.6105 | 29.8083 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6516 | 0.054185 | 1.0981 | 1.098 | 1.0979 | 1.0979 | 0.9786 | 2.5433 | 29.5502 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6516 | 0.054185 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5433 | 29.5502 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6516 | 0.054185 | 1.0979 | 1.0979 | 1.0979 | 1.0979 | 0.9786 | 2.5433 | 1657 | 2543.289 | 0.9786 | 1.0979 | 0.0054 | 29.5502
1.658 | 1.7492 | 0.056397 | 1.1027 | 1.1029 | 1.1029 | 1.1029 | 2.6129 | 29.8173 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6526 | 0.054186 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5456 | 29.5592 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6526 | 0.054186 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5456 | 29.5592 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6526 | 0.054186 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5456 | 1658 | 2545.6047 | 0.97861 | 1.098 | 0.0054 | 29.5592
1.659 | 1.7502 | 0.056398 | 1.1027 | 1.1029 | 1.1029 | 1.1029 | 2.6152 | 29.8263 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6536 | 0.054188 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5479 | 29.5682 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6536 | 0.054188 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5479 | 29.5682 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6536 | 0.054188 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5479 | 1659 | 2547.921 | 0.97861 | 1.098 | 0.0054 | 29.5682
1.66 | 1.7512 | 0.056399 | 1.1027 | 1.1029 | 1.1029 | 1.1029 | 2.6176 | 29.8353 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6546 | 0.054189 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5502 | 29.5771 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6546 | 0.054189 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5502 | 29.5771 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6546 | 0.054189 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.5502 | 1660 | 2550.2381 | 0.97861 | 1.098 | 0.0054 | 29.5771
1.661 | 1.7523 | 0.0564 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.62 | 29.8443 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6556 | 0.05419 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5526 | 29.5861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6556 | 0.05419 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5526 | 29.5861 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6556 | 0.05419 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5526 | 1661 | 2552.5558 | 0.97862 | 1.098 | 0.0054 | 29.5861
1.662 | 1.7533 | 0.056401 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6224 | 29.8533 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6566 | 0.054191 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5549 | 29.595 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6566 | 0.054191 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5549 | 29.595 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6566 | 0.054191 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5549 | 1662 | 2554.8743 | 0.97862 | 1.098 | 0.0054 | 29.595
1.663 | 1.7544 | 0.056402 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6247 | 29.8623 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6576 | 0.054192 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5572 | 29.604 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6576 | 0.054192 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5572 | 29.604 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6576 | 0.054192 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5572 | 1663 | 2557.1935 | 0.97862 | 1.098 | 0.0054 | 29.604
1.664 | 1.7554 | 0.056402 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6271 | 29.8713 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6586 | 0.054193 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5595 | 29.6129 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6586 | 0.054193 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5595 | 29.6129 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6586 | 0.054193 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.5595 | 1664 | 2559.5133 | 0.97862 | 1.098 | 0.0054 | 29.6129
1.665 | 1.7564 | 0.056403 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6295 | 29.8803 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6596 | 0.054194 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5618 | 29.6219 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6596 | 0.054194 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5618 | 29.6219 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6596 | 0.054194 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5618 | 1665 | 2561.8339 | 0.97863 | 1.098 | 0.0054 | 29.6219
1.666 | 1.7575 | 0.056404 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6318 | 29.8893 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6606 | 0.054195 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5642 | 29.6308 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6606 | 0.054195 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5642 | 29.6308 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6606 | 0.054195 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5642 | 1666 | 2564.1551 | 0.97863 | 1.098 | 0.0054 | 29.6308
1.667 | 1.7585 | 0.056405 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6342 | 29.8983 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6616 | 0.054196 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5665 | 29.6398 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6616 | 0.054196 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5665 | 29.6398 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6616 | 0.054196 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.5665 | 1667 | 2566.4771 | 0.97863 | 1.098 | 0.0054 | 29.6398
1.668 | 1.7596 | 0.056406 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6366 | 29.9073 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6626 | 0.054197 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5688 | 29.6487 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6626 | 0.054197 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5688 | 29.6487 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6626 | 0.054197 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5688 | 1668 | 2568.7998 | 0.97864 | 1.098 | 0.0054 | 29.6487
1.669 | 1.7606 | 0.056407 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.639 | 29.9163 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6636 | 0.054198 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5711 | 29.6576 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6636 | 0.054198 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5711 | 29.6576 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6636 | 0.054198 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5711 | 1669 | 2571.1231 | 0.97864 | 1.098 | 0.0054 | 29.6576
1.67 | 1.7617 | 0.056408 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6413 | 29.9252 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6646 | 0.054199 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5734 | 29.6666 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6646 | 0.054199 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5734 | 29.6666 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6646 | 0.054199 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5734 | 1670 | 2573.4472 | 0.97864 | 1.098 | 0.0054 | 29.6666
1.671 | 1.7627 | 0.056409 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6437 | 29.9342 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6656 | 0.0542 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5758 | 29.6755 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6656 | 0.0542 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5758 | 29.6755 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6656 | 0.0542 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97864 | 2.5758 | 1671 | 2575.7719 | 0.97864 | 1.098 | 0.0054 | 29.6755
1.672 | 1.7637 | 0.056409 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6461 | 29.9432 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6666 | 0.054201 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5781 | 29.6844 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6666 | 0.054201 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5781 | 29.6844 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6666 | 0.054201 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5781 | 1672 | 2578.0974 | 0.97865 | 1.098 | 0.0054 | 29.6844
1.673 | 1.7648 | 0.05641 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6485 | 29.9522 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6676 | 0.054202 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5804 | 29.6934 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6676 | 0.054202 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5804 | 29.6934 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6676 | 0.054202 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5804 | 1673 | 2580.4236 | 0.97865 | 1.098 | 0.0054 | 29.6934
1.674 | 1.7658 | 0.056411 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6509 | 29.9611 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6686 | 0.054203 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5828 | 29.7023 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6686 | 0.054203 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5828 | 29.7023 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6686 | 0.054203 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97865 | 2.5828 | 1674 | 2582.7504 | 0.97865 | 1.098 | 0.0054 | 29.7023
1.675 | 1.7669 | 0.056412 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6532 | 29.9701 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6696 | 0.054204 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5851 | 29.7112 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6696 | 0.054204 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5851 | 29.7112 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6696 | 0.054204 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5851 | 1675 | 2585.078 | 0.97866 | 1.098 | 0.0054 | 29.7112
1.676 | 1.7679 | 0.056413 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6556 | 29.979 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6706 | 0.054206 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5874 | 29.7201 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6706 | 0.054206 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5874 | 29.7201 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6706 | 0.054206 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5874 | 1676 | 2587.4062 | 0.97866 | 1.098 | 0.0054 | 29.7201
1.677 | 1.7689 | 0.056414 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.658 | 29.988 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6716 | 0.054207 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5897 | 29.729 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6716 | 0.054207 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5897 | 29.729 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6716 | 0.054207 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5897 | 1677 | 2589.7352 | 0.97866 | 1.098 | 0.0054 | 29.729
1.678 | 1.77 | 0.056415 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6604 | 29.997 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6726 | 0.054208 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5921 | 29.7379 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6726 | 0.054208 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5921 | 29.7379 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6726 | 0.054208 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97866 | 2.5921 | 1678 | 2592.0649 | 0.97866 | 1.098 | 0.0054 | 29.7379
1.679 | 1.771 | 0.056416 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6628 | 30.0059 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6736 | 0.054195 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97854 | 2.594 | 29.7453 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6736 | 0.054209 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97867 | 2.5944 | 29.7468 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6736 | 0.054209 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97867 | 2.5944 | 1679 | 2594.3952 | 0.97867 | 1.098 | 0.0054 | 29.7468
1.68 | 1.7721 | 0.056416 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6652 | 30.0149 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6746 | 0.054196 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97854 | 2.5963 | 29.7542 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6746 | 0.05421 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97867 | 2.5967 | 29.7558 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6746 | 0.05421 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97867 | 2.5967 | 1680 | 2596.7263 | 0.97867 | 1.098 | 0.0054 | 29.7558
1.681 | 1.7731 | 0.056417 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6675 | 30.0238 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6756 | 0.054197 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97854 | 2.5986 | 29.7631 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6756 | 0.054211 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97867 | 2.5991 | 29.7647 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6756 | 0.054211 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97867 | 2.5991 | 1681 | 2599.058 | 0.97867 | 1.098 | 0.0054 | 29.7647
1.682 | 1.7741 | 0.056418 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6699 | 30.0328 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6766 | 0.054198 | 1.0981 | 1.098 | 1.098 | 1.098 | 0.97854 | 2.601 | 29.772 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6766 | 0.054212 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6014 | 29.7736 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6766 | 0.054212 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6014 | 1682 | 2601.3905 | 0.97868 | 1.098 | 0.0054 | 29.7736
1.683 | 1.7752 | 0.056419 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6723 | 30.0417 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6776 | 0.054199 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97855 | 2.6033 | 29.7809 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6776 | 0.054213 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6037 | 29.7825 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6776 | 0.054213 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6037 | 1683 | 2603.7236 | 0.97868 | 1.098 | 0.0054 | 29.7825
1.684 | 1.7762 | 0.05642 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6747 | 30.0507 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6786 | 0.0542 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97855 | 2.6056 | 29.7898 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6786 | 0.054214 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6061 | 29.7914 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6786 | 0.054214 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6061 | 1684 | 2606.0575 | 0.97868 | 1.098 | 0.0054 | 29.7914
1.685 | 1.7773 | 0.056421 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6771 | 30.0596 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6796 | 0.054201 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97855 | 2.608 | 29.7986 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6796 | 0.054215 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6084 | 29.8002 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6796 | 0.054215 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97868 | 2.6084 | 1685 | 2608.392 | 0.97868 | 1.098 | 0.0054 | 29.8002
1.686 | 1.7783 | 0.056422 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6795 | 30.0685 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6806 | 0.054202 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97856 | 2.6103 | 29.8075 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6806 | 0.054216 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97869 | 2.6107 | 29.8091 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6806 | 0.054216 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97869 | 2.6107 | 1686 | 2610.7272 | 0.97869 | 1.098 | 0.0054 | 29.8091
1.687 | 1.7794 | 0.056423 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6819 | 30.0775 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6816 | 0.054204 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97856 | 2.6126 | 29.8164 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6816 | 0.054217 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97869 | 2.6131 | 29.818 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6816 | 0.054217 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97869 | 2.6131 | 1687 | 2613.0632 | 0.97869 | 1.098 | 0.0054 | 29.818
1.688 | 1.7804 | 0.056423 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6843 | 30.0864 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6826 | 0.054205 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97856 | 2.615 | 29.8253 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6826 | 0.054218 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97869 | 2.6154 | 29.8269 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6826 | 0.054218 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97869 | 2.6154 | 1688 | 2615.3998 | 0.97869 | 1.098 | 0.0054 | 29.8269
1.689 | 1.7814 | 0.056424 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6866 | 30.0953 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6836 | 0.054206 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97856 | 2.6173 | 29.8342 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6836 | 0.054219 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6177 | 29.8358 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6836 | 0.054219 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6177 | 1689 | 2617.7371 | 0.9787 | 1.098 | 0.0054 | 29.8358
1.69 | 1.7825 | 0.056425 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.689 | 30.1042 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6846 | 0.054207 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97857 | 2.6197 | 29.8431 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6846 | 0.05422 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6201 | 29.8447 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6846 | 0.05422 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6201 | 1690 | 2620.0752 | 0.9787 | 1.098 | 0.0054 | 29.8447
1.691 | 1.7835 | 0.056426 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6914 | 30.1132 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6856 | 0.054208 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97857 | 2.622 | 29.8519 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6856 | 0.054221 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6224 | 29.8535 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6856 | 0.054221 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6224 | 1691 | 2622.4139 | 0.9787 | 1.098 | 0.0054 | 29.8535
1.692 | 1.7846 | 0.056427 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6938 | 30.1221 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6866 | 0.054209 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97857 | 2.6243 | 29.8608 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6866 | 0.054222 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6248 | 29.8624 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6866 | 0.054222 | 1.098 | 1.098 | 1.098 | 1.098 | 0.9787 | 2.6248 | 1692 | 2624.7533 | 0.9787 | 1.098 | 0.0054 | 29.8624
1.693 | 1.7856 | 0.056428 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6962 | 30.131 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6876 | 0.05421 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97858 | 2.6267 | 29.8697 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6876 | 0.054223 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97871 | 2.6271 | 29.8713 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6876 | 0.054223 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97871 | 2.6271 | 1693 | 2627.0934 | 0.97871 | 1.098 | 0.0054 | 29.8713
1.694 | 1.7866 | 0.056429 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.6986 | 30.1399 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6886 | 0.054211 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97858 | 2.629 | 29.8786 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6886 | 0.054224 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97871 | 2.6294 | 29.8802 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6886 | 0.054224 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97871 | 2.6294 | 1694 | 2629.4342 | 0.97871 | 1.098 | 0.0054 | 29.8802
1.695 | 1.7877 | 0.056429 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.701 | 30.1488 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6896 | 0.054212 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97858 | 2.6314 | 29.8874 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6896 | 0.054225 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97871 | 2.6318 | 29.889 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6896 | 0.054225 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97871 | 2.6318 | 1695 | 2631.7757 | 0.97871 | 1.098 | 0.0054 | 29.889
1.696 | 1.7887 | 0.05643 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7034 | 30.1577 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6906 | 0.054213 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97858 | 2.6337 | 29.8963 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6906 | 0.054226 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6341 | 29.8979 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6906 | 0.054226 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6341 | 1696 | 2634.1179 | 0.97872 | 1.098 | 0.0054 | 29.8979
1.697 | 1.7898 | 0.056431 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7058 | 30.1666 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6916 | 0.054214 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97859 | 2.636 | 29.9052 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6916 | 0.054227 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6365 | 29.9068 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6916 | 0.054227 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6365 | 1697 | 2636.4608 | 0.97872 | 1.098 | 0.0054 | 29.9068
1.698 | 1.7908 | 0.056432 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7082 | 30.1756 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6926 | 0.054215 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97859 | 2.6384 | 29.914 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6926 | 0.054228 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6388 | 29.9156 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6926 | 0.054228 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6388 | 1698 | 2638.8044 | 0.97872 | 1.098 | 0.0054 | 29.9156
1.699 | 1.7918 | 0.056433 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7106 | 30.1845 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6936 | 0.054216 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97859 | 2.6407 | 29.9229 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6936 | 0.054229 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6411 | 29.9245 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6936 | 0.054229 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97872 | 2.6411 | 1699 | 2641.1487 | 0.97872 | 1.098 | 0.0054 | 29.9245
1.7 | 1.7929 | 0.056434 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.713 | 30.1934 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6946 | 0.054217 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.9786 | 2.6431 | 29.9317 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6946 | 0.05423 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97873 | 2.6435 | 29.9333 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6946 | 0.05423 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97873 | 2.6435 | 1700 | 2643.4936 | 0.97873 | 1.098 | 0.0054 | 29.9333
1.701 | 1.7939 | 0.056434 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7154 | 30.2022 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6956 | 0.054218 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.9786 | 2.6454 | 29.9406 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6956 | 0.054231 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97873 | 2.6458 | 29.9422 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6956 | 0.054231 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97873 | 2.6458 | 1701 | 2645.8393 | 0.97873 | 1.098 | 0.0054 | 29.9422
1.702 | 1.795 | 0.056435 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7178 | 30.2111 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6966 | 0.054219 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.9786 | 2.6478 | 29.9494 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6966 | 0.054232 | 1.098 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.6482 | 29.951 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6966 | 0.054232 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.6482 | 1702 | 2648.1857 | 0.97873 | 1.0981 | 0.0054 | 29.951
1.703 | 1.796 | 0.056436 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7202 | 30.22 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6976 | 0.05422 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.9786 | 2.6501 | 29.9583 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6976 | 0.054233 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.6505 | 29.9599 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6976 | 0.054233 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.6505 | 1703 | 2650.5327 | 0.97873 | 1.0981 | 0.0054 | 29.9599
1.704 | 1.7971 | 0.056437 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7226 | 30.2289 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6986 | 0.054221 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.6525 | 29.9671 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6986 | 0.054234 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.6529 | 29.9687 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6986 | 0.054234 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.6529 | 1704 | 2652.8805 | 0.97874 | 1.0981 | 0.0054 | 29.9687
1.705 | 1.7981 | 0.056438 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.725 | 30.2378 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.6996 | 0.054222 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.6548 | 29.976 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6996 | 0.054235 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.6552 | 29.9776 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.6996 | 0.054235 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.6552 | 1705 | 2655.2289 | 0.97874 | 1.0981 | 0.0054 | 29.9776
1.706 | 1.7991 | 0.056439 | 1.1028 | 1.1029 | 1.1029 | 1.1029 | 2.7274 | 30.2467 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7006 | 0.054223 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.6572 | 29.9848 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.7006 | 0.054236 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.6576 | 29.9864 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.7006 | 0.054236 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.6576 | 1706 | 2657.578 | 0.97874 | 1.0981 | 0.0054 | 29.9864
1.707 | 1.8002 | 0.05644 | 1.1028 | 1.1029 | 1.103 | 1.103 | 2.7298 | 30.2556 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7016 | 0.054224 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97861 | 2.6595 | 29.9936 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.7016 | 0.054237 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.6599 | 29.9952 | 0.0062 | 0.005 | 0.0054 | 0.64012 | 1.7016 | 0.054237 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.6599 | 1707 | 2659.9278 | 0.97875 | 1.0981 | 0.0054 | 29.9952
1.708 | 1.8012 | 0.05644 | 1.1028 | 1.1029 | 1.103 | 1.103 | 2.7322 | 30.2645 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7026 | 0.054225 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6619 | 30.0025 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7026 | 0.054225 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6619 | 30.0025 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7026 | 0.054225 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6619 | 1708 | 2661.8514 | 0.97862 | 1.098 | 0.0054333 | 30.0025
1.709 | 1.8023 | 0.056441 | 1.1028 | 1.103 | 1.103 | 1.103 | 2.7346 | 30.2733 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7036 | 0.054226 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6642 | 30.0113 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7036 | 0.054226 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6642 | 30.0113 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7036 | 0.054226 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6642 | 1709 | 2664.2022 | 0.97862 | 1.098 | 0.0054333 | 30.0113
1.71 | 1.8033 | 0.056442 | 1.1028 | 1.103 | 1.103 | 1.103 | 2.737 | 30.2822 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7046 | 0.054227 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6666 | 30.0201 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7046 | 0.054227 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6666 | 30.0201 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7046 | 0.054227 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97862 | 2.6666 | 1710 | 2666.5538 | 0.97862 | 1.098 | 0.0054333 | 30.0201
1.711 | 1.8043 | 0.056443 | 1.1028 | 1.103 | 1.103 | 1.103 | 2.7394 | 30.2911 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7056 | 0.054228 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6689 | 30.0289 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7056 | 0.054228 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6689 | 30.0289 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7056 | 0.054228 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6689 | 1711 | 2668.9061 | 0.97863 | 1.098 | 0.0054333 | 30.0289
1.712 | 1.8054 | 0.056444 | 1.1028 | 1.103 | 1.103 | 1.103 | 2.7418 | 30.2999 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7066 | 0.054229 | 1.0982 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6713 | 30.0378 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7066 | 0.054229 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6713 | 30.0378 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7066 | 0.054229 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6713 | 1712 | 2671.259 | 0.97863 | 1.098 | 0.0054333 | 30.0378
1.713 | 1.8064 | 0.056445 | 1.1028 | 1.103 | 1.103 | 1.103 | 2.7442 | 30.3088 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7076 | 0.05423 | 1.0982 | 1.0981 | 1.098 | 1.098 | 0.97863 | 2.6736 | 30.0466 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7076 | 0.05423 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6736 | 30.0466 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7076 | 0.05423 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.6736 | 1713 | 2673.6127 | 0.97863 | 1.098 | 0.0054333 | 30.0466
1.714 | 1.8075 | 0.056445 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7466 | 30.3177 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7086 | 0.054231 | 1.0982 | 1.0981 | 1.098 | 1.098 | 0.97863 | 2.676 | 30.0554 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7086 | 0.054231 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.676 | 30.0554 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7086 | 0.054231 | 1.098 | 1.098 | 1.098 | 1.098 | 0.97863 | 2.676 | 1714 | 2675.967 | 0.97863 | 1.098 | 0.0054333 | 30.0554
1.715 | 1.8085 | 0.056446 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.749 | 30.3265 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7096 | 0.054232 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6783 | 30.0642 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7096 | 0.054232 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6783 | 30.0642 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7096 | 0.054232 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6783 | 1715 | 2678.3221 | 0.97864 | 1.0981 | 0.0054333 | 30.0642
1.716 | 1.8095 | 0.056447 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7515 | 30.3354 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7106 | 0.054233 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6807 | 30.073 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7106 | 0.054233 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6807 | 30.073 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7106 | 0.054233 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6807 | 1716 | 2680.6778 | 0.97864 | 1.0981 | 0.0054333 | 30.073
1.717 | 1.8106 | 0.056448 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7539 | 30.3442 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7116 | 0.054234 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.683 | 30.0818 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7116 | 0.054234 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.683 | 30.0818 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7116 | 0.054234 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.683 | 1717 | 2683.0342 | 0.97864 | 1.0981 | 0.0054333 | 30.0818
1.718 | 1.8116 | 0.056449 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7563 | 30.3531 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7126 | 0.054235 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6854 | 30.0906 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7126 | 0.054235 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6854 | 30.0906 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7126 | 0.054235 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97864 | 2.6854 | 1718 | 2685.3913 | 0.97864 | 1.0981 | 0.0054333 | 30.0906
1.719 | 1.8127 | 0.05645 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7587 | 30.3619 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7136 | 0.054236 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6877 | 30.0994 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7136 | 0.054236 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6877 | 30.0994 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7136 | 0.054236 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6877 | 1719 | 2687.7491 | 0.97865 | 1.0981 | 0.0054333 | 30.0994
1.72 | 1.8137 | 0.05645 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7611 | 30.3708 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7146 | 0.054237 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6901 | 30.1082 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7146 | 0.054237 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6901 | 30.1082 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7146 | 0.054237 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6901 | 1720 | 2690.1076 | 0.97865 | 1.0981 | 0.0054333 | 30.1082
1.721 | 1.8148 | 0.056451 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7635 | 30.3796 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7156 | 0.054238 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6925 | 30.117 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7156 | 0.054238 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6925 | 30.117 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7156 | 0.054238 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97865 | 2.6925 | 1721 | 2692.4668 | 0.97865 | 1.0981 | 0.0054333 | 30.117
1.722 | 1.8158 | 0.056452 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7659 | 30.3885 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7166 | 0.054239 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6948 | 30.1258 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7166 | 0.054239 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6948 | 30.1258 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7166 | 0.054239 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6948 | 1722 | 2694.8266 | 0.97866 | 1.0981 | 0.0054333 | 30.1258
1.723 | 1.8168 | 0.056453 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7683 | 30.3973 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7176 | 0.05424 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6972 | 30.1346 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7176 | 0.05424 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6972 | 30.1346 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7176 | 0.05424 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6972 | 1723 | 2697.1872 | 0.97866 | 1.0981 | 0.0054333 | 30.1346
1.724 | 1.8179 | 0.056454 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7708 | 30.4061 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7186 | 0.054241 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6995 | 30.1434 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7186 | 0.054241 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6995 | 30.1434 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7186 | 0.054241 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.6995 | 1724 | 2699.5484 | 0.97866 | 1.0981 | 0.0054333 | 30.1434
1.725 | 1.8189 | 0.056455 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7732 | 30.415 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7196 | 0.054242 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.7019 | 30.1522 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7196 | 0.054242 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.7019 | 30.1522 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7196 | 0.054242 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97866 | 2.7019 | 1725 | 2701.9103 | 0.97866 | 1.0981 | 0.0054333 | 30.1522
1.726 | 1.82 | 0.056455 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7756 | 30.4238 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7206 | 0.054243 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7043 | 30.161 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7206 | 0.054243 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7043 | 30.161 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7206 | 0.054243 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7043 | 1726 | 2704.2729 | 0.97867 | 1.0981 | 0.0054333 | 30.161
1.727 | 1.821 | 0.056456 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.778 | 30.4326 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7216 | 0.054244 | 1.0982 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7066 | 30.1698 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7216 | 0.054244 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7066 | 30.1698 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7216 | 0.054244 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7066 | 1727 | 2706.6363 | 0.97867 | 1.0981 | 0.0054333 | 30.1698
1.728 | 1.822 | 0.056457 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7804 | 30.4415 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7226 | 0.054245 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.709 | 30.1786 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7226 | 0.054245 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.709 | 30.1786 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7226 | 0.054245 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.709 | 1728 | 2709.0002 | 0.97867 | 1.0981 | 0.0054333 | 30.1786
1.729 | 1.8231 | 0.056458 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7828 | 30.4503 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7236 | 0.054246 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7114 | 30.1873 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7236 | 0.054246 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7114 | 30.1873 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7236 | 0.054246 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97867 | 2.7114 | 1729 | 2711.3649 | 0.97867 | 1.0981 | 0.0054333 | 30.1873
1.73 | 1.8241 | 0.056459 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7853 | 30.4591 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7246 | 0.054247 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7137 | 30.1961 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7246 | 0.054247 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7137 | 30.1961 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7246 | 0.054247 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7137 | 1730 | 2713.7303 | 0.97868 | 1.0981 | 0.0054333 | 30.1961
1.731 | 1.8252 | 0.056459 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7877 | 30.4679 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7256 | 0.054248 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7161 | 30.2049 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7256 | 0.054248 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7161 | 30.2049 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7256 | 0.054248 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7161 | 1731 | 2716.0964 | 0.97868 | 1.0981 | 0.0054333 | 30.2049
1.732 | 1.8262 | 0.05646 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7901 | 30.4768 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7266 | 0.054249 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7185 | 30.2137 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7266 | 0.054249 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7185 | 30.2137 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7266 | 0.054249 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7185 | 1732 | 2718.4631 | 0.97868 | 1.0981 | 0.0054333 | 30.2137
1.733 | 1.8272 | 0.056461 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7925 | 30.4856 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7276 | 0.05425 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7208 | 30.2224 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7276 | 0.05425 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7208 | 30.2224 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7276 | 0.05425 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97868 | 2.7208 | 1733 | 2720.8305 | 0.97868 | 1.0981 | 0.0054333 | 30.2224
1.734 | 1.8283 | 0.056462 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7949 | 30.4944 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7286 | 0.054251 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7232 | 30.2312 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7286 | 0.054251 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7232 | 30.2312 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7286 | 0.054251 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7232 | 1734 | 2723.1987 | 0.97869 | 1.0981 | 0.0054333 | 30.2312
1.735 | 1.8293 | 0.056463 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7974 | 30.5032 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7296 | 0.054252 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7256 | 30.24 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7296 | 0.054252 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7256 | 30.24 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7296 | 0.054252 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7256 | 1735 | 2725.5675 | 0.97869 | 1.0981 | 0.0054333 | 30.24
1.736 | 1.8304 | 0.056464 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.7998 | 30.512 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7306 | 0.054253 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7279 | 30.2487 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7306 | 0.054253 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7279 | 30.2487 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7306 | 0.054253 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97869 | 2.7279 | 1736 | 2727.9369 | 0.97869 | 1.0981 | 0.0054333 | 30.2487
1.737 | 1.8314 | 0.056464 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8022 | 30.5208 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7316 | 0.054254 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7303 | 30.2575 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7316 | 0.054254 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7303 | 30.2575 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7316 | 0.054254 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7303 | 1737 | 2730.3071 | 0.9787 | 1.0981 | 0.0054333 | 30.2575
1.738 | 1.8325 | 0.056465 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8046 | 30.5296 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7326 | 0.054255 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7327 | 30.2662 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7326 | 0.054255 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7327 | 30.2662 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7326 | 0.054255 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7327 | 1738 | 2732.678 | 0.9787 | 1.0981 | 0.0054333 | 30.2662
1.739 | 1.8335 | 0.056466 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8071 | 30.5384 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7336 | 0.054256 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.735 | 30.275 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7336 | 0.054256 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.735 | 30.275 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7336 | 0.054256 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.735 | 1739 | 2735.0495 | 0.9787 | 1.0981 | 0.0054333 | 30.275
1.74 | 1.8345 | 0.056467 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8095 | 30.5472 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7346 | 0.054257 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7374 | 30.2837 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7346 | 0.054257 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7374 | 30.2837 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7346 | 0.054257 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.9787 | 2.7374 | 1740 | 2737.4218 | 0.9787 | 1.0981 | 0.0054333 | 30.2837
1.741 | 1.8356 | 0.056468 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8119 | 30.556 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7356 | 0.054258 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7398 | 30.2925 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7356 | 0.054258 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7398 | 30.2925 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7356 | 0.054258 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7398 | 1741 | 2739.7947 | 0.97871 | 1.0981 | 0.0054333 | 30.2925
1.742 | 1.8366 | 0.056468 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8143 | 30.5648 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7366 | 0.054259 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7422 | 30.3012 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7366 | 0.054259 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7422 | 30.3012 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7366 | 0.054259 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7422 | 1742 | 2742.1683 | 0.97871 | 1.0981 | 0.0054333 | 30.3012
1.743 | 1.8377 | 0.056469 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8168 | 30.5736 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7376 | 0.05426 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7445 | 30.31 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7376 | 0.05426 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7445 | 30.31 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7376 | 0.05426 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7445 | 1743 | 2744.5426 | 0.97871 | 1.0981 | 0.0054333 | 30.31
1.744 | 1.8387 | 0.05647 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8192 | 30.5823 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7386 | 0.054261 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7469 | 30.3187 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7386 | 0.054261 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7469 | 30.3187 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7386 | 0.054261 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97871 | 2.7469 | 1744 | 2746.9176 | 0.97871 | 1.0981 | 0.0054333 | 30.3187
1.745 | 1.8397 | 0.056471 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8216 | 30.5911 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7396 | 0.054262 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7493 | 30.3275 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7396 | 0.054262 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7493 | 30.3275 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7396 | 0.054262 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7493 | 1745 | 2749.2932 | 0.97872 | 1.0981 | 0.0054333 | 30.3275
1.746 | 1.8408 | 0.056472 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8241 | 30.5999 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7406 | 0.054263 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7517 | 30.3362 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7406 | 0.054263 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7517 | 30.3362 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7406 | 0.054263 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7517 | 1746 | 2751.6696 | 0.97872 | 1.0981 | 0.0054333 | 30.3362
1.747 | 1.8418 | 0.056472 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8265 | 30.6087 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7416 | 0.054264 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.754 | 30.3449 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7416 | 0.054264 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.754 | 30.3449 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7416 | 0.054264 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.754 | 1747 | 2754.0466 | 0.97872 | 1.0981 | 0.0054333 | 30.3449
1.748 | 1.8429 | 0.056473 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8289 | 30.6175 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7426 | 0.054264 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7564 | 30.3536 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7426 | 0.054264 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7564 | 30.3536 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7426 | 0.054264 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97872 | 2.7564 | 1748 | 2756.4243 | 0.97872 | 1.0981 | 0.0054333 | 30.3536
1.749 | 1.8439 | 0.056474 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8314 | 30.6262 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7436 | 0.054265 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7588 | 30.3624 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7436 | 0.054265 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7588 | 30.3624 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7436 | 0.054265 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7588 | 1749 | 2758.8027 | 0.97873 | 1.0981 | 0.0054333 | 30.3624
1.75 | 1.8449 | 0.056475 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8338 | 30.635 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7446 | 0.054266 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7612 | 30.3711 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7446 | 0.054266 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7612 | 30.3711 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7446 | 0.054266 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7612 | 1750 | 2761.1818 | 0.97873 | 1.0981 | 0.0054333 | 30.3711
1.751 | 1.846 | 0.056476 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8362 | 30.6438 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7456 | 0.054267 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7636 | 30.3798 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7456 | 0.054267 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7636 | 30.3798 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7456 | 0.054267 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7636 | 1751 | 2763.5616 | 0.97873 | 1.0981 | 0.0054333 | 30.3798
1.752 | 1.847 | 0.056476 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8387 | 30.6525 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7466 | 0.054268 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7659 | 30.3885 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7466 | 0.054268 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7659 | 30.3885 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7466 | 0.054268 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97873 | 2.7659 | 1752 | 2765.942 | 0.97873 | 1.0981 | 0.0054333 | 30.3885
1.753 | 1.8481 | 0.056477 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8411 | 30.6613 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7476 | 0.054269 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7683 | 30.3973 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7476 | 0.054269 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7683 | 30.3973 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7476 | 0.054269 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7683 | 1753 | 2768.3232 | 0.97874 | 1.0981 | 0.0054333 | 30.3973
1.754 | 1.8491 | 0.056478 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8435 | 30.6701 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7486 | 0.05427 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7707 | 30.406 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7486 | 0.05427 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7707 | 30.406 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7486 | 0.05427 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7707 | 1754 | 2770.705 | 0.97874 | 1.0981 | 0.0054333 | 30.406
1.755 | 1.8502 | 0.056479 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.846 | 30.6788 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7496 | 0.054271 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7731 | 30.4147 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7496 | 0.054271 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7731 | 30.4147 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7496 | 0.054271 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97874 | 2.7731 | 1755 | 2773.0875 | 0.97874 | 1.0981 | 0.0054333 | 30.4147
1.756 | 1.8512 | 0.05648 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8484 | 30.6876 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7506 | 0.054272 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7755 | 30.4234 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7506 | 0.054272 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7755 | 30.4234 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7506 | 0.054272 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7755 | 1756 | 2775.4707 | 0.97875 | 1.0981 | 0.0054333 | 30.4234
1.757 | 1.8522 | 0.05648 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8508 | 30.6963 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7516 | 0.054273 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7779 | 30.4321 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7516 | 0.054273 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7779 | 30.4321 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7516 | 0.054273 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7779 | 1757 | 2777.8545 | 0.97875 | 1.0981 | 0.0054333 | 30.4321
1.758 | 1.8533 | 0.056481 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8533 | 30.7051 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7526 | 0.054274 | 1.0983 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7802 | 30.4408 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7526 | 0.054274 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7802 | 30.4408 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7526 | 0.054274 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7802 | 1758 | 2780.2391 | 0.97875 | 1.0981 | 0.0054333 | 30.4408
1.759 | 1.8543 | 0.056482 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8557 | 30.7138 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7536 | 0.054275 | 1.0983 | 1.0982 | 1.0981 | 1.0981 | 0.97875 | 2.7826 | 30.4495 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7536 | 0.054275 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7826 | 30.4495 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7536 | 0.054275 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97875 | 2.7826 | 1759 | 2782.6243 | 0.97875 | 1.0981 | 0.0054333 | 30.4495
1.76 | 1.8554 | 0.056483 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8582 | 30.7226 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7546 | 0.054276 | 1.0983 | 1.0982 | 1.0981 | 1.0981 | 0.97876 | 2.785 | 30.4582 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7546 | 0.054276 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97876 | 2.785 | 30.4582 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7546 | 0.054276 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97876 | 2.785 | 1760 | 2785.0102 | 0.97876 | 1.0981 | 0.0054333 | 30.4582
1.761 | 1.8564 | 0.056484 | 1.1029 | 1.103 | 1.103 | 1.103 | 2.8606 | 30.7313 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7556 | 0.054277 | 1.0983 | 1.0982 | 1.0981 | 1.0981 | 0.97876 | 2.7874 | 30.4669 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7556 | 0.054277 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97876 | 2.7874 | 30.4669 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7556 | 0.054277 | 1.0981 | 1.0981 | 1.0981 | 1.0981 | 0.97876 | 2.7874 | 1761 | 2787.3968 | 0.97876 | 1.0981 | 0.0054333 | 30.4669
1.762 | 1.8574 | 0.056484 | 1.1029 | 1.103 | 1.1031 | 1.1031 | 2.863 | 30.7401 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7566 | 0.054278 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97876 | 2.7898 | 30.4756 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7566 | 0.054278 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97876 | 2.7898 | 30.4756 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7566 | 0.054278 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97876 | 2.7898 | 1762 | 2789.7841 | 0.97876 | 1.0982 | 0.0054333 | 30.4756
1.763 | 1.8585 | 0.056485 | 1.1029 | 1.103 | 1.1031 | 1.1031 | 2.8655 | 30.7488 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7576 | 0.054279 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97876 | 2.7922 | 30.4843 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7576 | 0.054279 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97876 | 2.7922 | 30.4843 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7576 | 0.054279 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97876 | 2.7922 | 1763 | 2792.1721 | 0.97876 | 1.0982 | 0.0054333 | 30.4843
1.764 | 1.8595 | 0.056486 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8679 | 30.7575 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7586 | 0.05428 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.7946 | 30.493 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7586 | 0.05428 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.7946 | 30.493 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7586 | 0.05428 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.7946 | 1764 | 2794.5607 | 0.97877 | 1.0982 | 0.0054333 | 30.493
1.765 | 1.8606 | 0.056487 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8704 | 30.7663 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7596 | 0.054281 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.797 | 30.5017 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7596 | 0.054281 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.797 | 30.5017 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7596 | 0.054281 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.797 | 1765 | 2796.95 | 0.97877 | 1.0982 | 0.0054333 | 30.5017
1.766 | 1.8616 | 0.056488 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8728 | 30.775 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7606 | 0.054282 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.7993 | 30.5104 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7606 | 0.054282 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.7993 | 30.5104 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7606 | 0.054282 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.7993 | 1766 | 2799.34 | 0.97877 | 1.0982 | 0.0054333 | 30.5104
1.767 | 1.8626 | 0.056488 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8753 | 30.7837 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7616 | 0.054283 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.8017 | 30.5191 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7616 | 0.054283 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.8017 | 30.5191 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7616 | 0.054283 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97877 | 2.8017 | 1767 | 2801.7307 | 0.97877 | 1.0982 | 0.0054333 | 30.5191
1.768 | 1.8637 | 0.056489 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8777 | 30.7925 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7626 | 0.054284 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8041 | 30.5277 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7626 | 0.054284 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8041 | 30.5277 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7626 | 0.054284 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8041 | 1768 | 2804.1221 | 0.97878 | 1.0982 | 0.0054333 | 30.5277
1.769 | 1.8647 | 0.05649 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8802 | 30.8012 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7636 | 0.054285 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8065 | 30.5364 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7636 | 0.054285 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8065 | 30.5364 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7636 | 0.054285 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8065 | 1769 | 2806.5141 | 0.97878 | 1.0982 | 0.0054333 | 30.5364
1.77 | 1.8658 | 0.056491 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.8826 | 30.8099 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7646 | 0.054285 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8089 | 30.5451 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7646 | 0.054285 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8089 | 30.5451 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7646 | 0.054285 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8089 | 1770 | 2808.9068 | 0.97878 | 1.0982 | 0.0054333 | 30.5451
1.771 | 1.8668 | 0.056491 | 1.1029 | 1.1031 | 1.1031 | 1.1031 | 2.885 | 30.8186 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7656 | 0.054286 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8113 | 30.5538 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7656 | 0.054286 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8113 | 30.5538 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7656 | 0.054286 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97878 | 2.8113 | 1771 | 2811.3002 | 0.97878 | 1.0982 | 0.0054333 | 30.5538
1.772 | 1.8679 | 0.056492 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.8875 | 30.8273 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7666 | 0.054287 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8137 | 30.5624 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7666 | 0.054287 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8137 | 30.5624 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7666 | 0.054287 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8137 | 1772 | 2813.6943 | 0.97879 | 1.0982 | 0.0054333 | 30.5624
1.773 | 1.8689 | 0.056493 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.8899 | 30.836 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7676 | 0.054288 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8161 | 30.5711 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7676 | 0.054288 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8161 | 30.5711 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7676 | 0.054288 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8161 | 1773 | 2816.0891 | 0.97879 | 1.0982 | 0.0054333 | 30.5711
1.774 | 1.8699 | 0.056494 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.8924 | 30.8448 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7686 | 0.054289 | 1.0983 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8185 | 30.5798 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7686 | 0.054289 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8185 | 30.5798 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7686 | 0.054289 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8185 | 1774 | 2818.4845 | 0.97879 | 1.0982 | 0.0054333 | 30.5798
1.775 | 1.871 | 0.056495 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.8948 | 30.8535 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7696 | 0.05429 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8209 | 30.5884 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7696 | 0.05429 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8209 | 30.5884 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7696 | 0.05429 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97879 | 2.8209 | 1775 | 2820.8806 | 0.97879 | 1.0982 | 0.0054333 | 30.5884
1.776 | 1.872 | 0.056495 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.8973 | 30.8622 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7706 | 0.054291 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8233 | 30.5971 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7706 | 0.054291 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8233 | 30.5971 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7706 | 0.054291 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8233 | 1776 | 2823.2774 | 0.9788 | 1.0982 | 0.0054333 | 30.5971
1.777 | 1.8731 | 0.056496 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.8997 | 30.8709 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7716 | 0.054292 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8257 | 30.6057 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7716 | 0.054292 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8257 | 30.6057 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7716 | 0.054292 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8257 | 1777 | 2825.6749 | 0.9788 | 1.0982 | 0.0054333 | 30.6057
1.778 | 1.8741 | 0.056497 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9022 | 30.8796 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7726 | 0.054293 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8281 | 30.6144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7726 | 0.054293 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8281 | 30.6144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7726 | 0.054293 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8281 | 1778 | 2828.073 | 0.9788 | 1.0982 | 0.0054333 | 30.6144
1.779 | 1.8751 | 0.056498 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9047 | 30.8883 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7736 | 0.054294 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8305 | 30.6231 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7736 | 0.054294 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8305 | 30.6231 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7736 | 0.054294 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.9788 | 2.8305 | 1779 | 2830.4719 | 0.9788 | 1.0982 | 0.0054333 | 30.6231
1.78 | 1.8762 | 0.056499 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9071 | 30.897 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7746 | 0.054295 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8329 | 30.6317 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7746 | 0.054295 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8329 | 30.6317 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7746 | 0.054295 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8329 | 1780 | 2832.8714 | 0.97881 | 1.0982 | 0.0054333 | 30.6317
1.781 | 1.8772 | 0.056499 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9096 | 30.9057 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7756 | 0.054296 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8353 | 30.6404 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7756 | 0.054296 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8353 | 30.6404 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7756 | 0.054296 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8353 | 1781 | 2835.2716 | 0.97881 | 1.0982 | 0.0054333 | 30.6404
1.782 | 1.8783 | 0.0565 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.912 | 30.9144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7766 | 0.054297 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8377 | 30.649 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7766 | 0.054297 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8377 | 30.649 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7766 | 0.054297 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8377 | 1782 | 2837.6724 | 0.97881 | 1.0982 | 0.0054333 | 30.649
1.783 | 1.8793 | 0.056501 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9145 | 30.923 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7776 | 0.054298 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8401 | 30.6576 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7776 | 0.054298 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8401 | 30.6576 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7776 | 0.054298 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97881 | 2.8401 | 1783 | 2840.074 | 0.97881 | 1.0982 | 0.0054333 | 30.6576
1.784 | 1.8803 | 0.056502 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9169 | 30.9317 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7786 | 0.054299 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8425 | 30.6663 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7786 | 0.054299 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8425 | 30.6663 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7786 | 0.054299 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8425 | 1784 | 2842.4762 | 0.97882 | 1.0982 | 0.0054333 | 30.6663
1.785 | 1.8814 | 0.056502 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9194 | 30.9404 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7796 | 0.054299 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8449 | 30.6749 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7796 | 0.054299 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8449 | 30.6749 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7796 | 0.054299 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8449 | 1785 | 2844.8791 | 0.97882 | 1.0982 | 0.0054333 | 30.6749
1.786 | 1.8824 | 0.056503 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9218 | 30.9491 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7806 | 0.0543 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8473 | 30.6836 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7806 | 0.0543 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8473 | 30.6836 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7806 | 0.0543 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8473 | 1786 | 2847.2827 | 0.97882 | 1.0982 | 0.0054333 | 30.6836
1.787 | 1.8835 | 0.056504 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9243 | 30.9578 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7816 | 0.054301 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8497 | 30.6922 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7816 | 0.054301 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8497 | 30.6922 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7816 | 0.054301 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97882 | 2.8497 | 1787 | 2849.6869 | 0.97882 | 1.0982 | 0.0054333 | 30.6922
1.788 | 1.8845 | 0.056505 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9268 | 30.9665 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7826 | 0.054302 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8521 | 30.7008 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7826 | 0.054302 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8521 | 30.7008 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7826 | 0.054302 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8521 | 1788 | 2852.0918 | 0.97883 | 1.0982 | 0.0054333 | 30.7008
1.789 | 1.8856 | 0.056505 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9292 | 30.9751 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7836 | 0.054303 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8545 | 30.7095 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7836 | 0.054303 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8545 | 30.7095 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7836 | 0.054303 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8545 | 1789 | 2854.4974 | 0.97883 | 1.0982 | 0.0054333 | 30.7095
1.79 | 1.8866 | 0.056506 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9317 | 30.9838 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7846 | 0.054304 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8569 | 30.7181 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7846 | 0.054304 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8569 | 30.7181 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7846 | 0.054304 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8569 | 1790 | 2856.9037 | 0.97883 | 1.0982 | 0.0054333 | 30.7181
1.791 | 1.8876 | 0.056507 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9341 | 30.9925 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7856 | 0.054305 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8593 | 30.7267 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7856 | 0.054305 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8593 | 30.7267 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7856 | 0.054305 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97883 | 2.8593 | 1791 | 2859.3107 | 0.97883 | 1.0982 | 0.0054333 | 30.7267
1.792 | 1.8887 | 0.056508 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9366 | 31.0011 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7866 | 0.054306 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8617 | 30.7353 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7866 | 0.054306 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8617 | 30.7353 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7866 | 0.054306 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8617 | 1792 | 2861.7183 | 0.97884 | 1.0982 | 0.0054333 | 30.7353
1.793 | 1.8897 | 0.056509 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9391 | 31.0098 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7876 | 0.054307 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8641 | 30.7439 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7876 | 0.054307 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8641 | 30.7439 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7876 | 0.054307 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8641 | 1793 | 2864.1266 | 0.97884 | 1.0982 | 0.0054333 | 30.7439
1.794 | 1.8908 | 0.056509 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9415 | 31.0185 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7886 | 0.054308 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8665 | 30.7526 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7886 | 0.054308 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8665 | 30.7526 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7886 | 0.054308 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8665 | 1794 | 2866.5356 | 0.97884 | 1.0982 | 0.0054333 | 30.7526
1.795 | 1.8918 | 0.05651 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.944 | 31.0271 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7896 | 0.054309 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8689 | 30.7612 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7896 | 0.054309 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8689 | 30.7612 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7896 | 0.054309 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97884 | 2.8689 | 1795 | 2868.9453 | 0.97884 | 1.0982 | 0.0054333 | 30.7612
1.796 | 1.8928 | 0.056511 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9465 | 31.0358 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7906 | 0.05431 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8714 | 30.7698 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7906 | 0.05431 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8714 | 30.7698 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7906 | 0.05431 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8714 | 1796 | 2871.3556 | 0.97885 | 1.0982 | 0.0054333 | 30.7698
1.797 | 1.8939 | 0.056512 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9489 | 31.0444 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7916 | 0.054311 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8738 | 30.7784 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7916 | 0.054311 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8738 | 30.7784 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7916 | 0.054311 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8738 | 1797 | 2873.7666 | 0.97885 | 1.0982 | 0.0054333 | 30.7784
1.798 | 1.8949 | 0.056512 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9514 | 31.0531 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7926 | 0.054311 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8762 | 30.787 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7926 | 0.054311 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8762 | 30.787 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7926 | 0.054311 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8762 | 1798 | 2876.1783 | 0.97885 | 1.0982 | 0.0054333 | 30.787
1.799 | 1.896 | 0.056513 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9539 | 31.0617 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7936 | 0.054312 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8786 | 30.7956 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7936 | 0.054312 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8786 | 30.7956 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7936 | 0.054312 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97885 | 2.8786 | 1799 | 2878.5906 | 0.97885 | 1.0982 | 0.0054333 | 30.7956
1.8 | 1.897 | 0.056514 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9563 | 31.0704 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7946 | 0.054313 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.881 | 30.8042 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7946 | 0.054313 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.881 | 30.8042 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7946 | 0.054313 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.881 | 1800 | 2881.0037 | 0.97886 | 1.0982 | 0.0054333 | 30.8042
1.801 | 1.898 | 0.056515 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9588 | 31.079 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7956 | 0.054314 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8834 | 30.8128 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7956 | 0.054314 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8834 | 30.8128 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7956 | 0.054314 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8834 | 1801 | 2883.4174 | 0.97886 | 1.0982 | 0.0054333 | 30.8128
1.802 | 1.8991 | 0.056515 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9613 | 31.0877 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7966 | 0.054315 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8858 | 30.8214 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7966 | 0.054315 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8858 | 30.8214 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7966 | 0.054315 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8858 | 1802 | 2885.8317 | 0.97886 | 1.0982 | 0.0054333 | 30.8214
1.803 | 1.9001 | 0.056516 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9637 | 31.0963 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7976 | 0.054316 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8882 | 30.83 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7976 | 0.054316 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8882 | 30.83 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7976 | 0.054316 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97886 | 2.8882 | 1803 | 2888.2468 | 0.97886 | 1.0982 | 0.0054333 | 30.83
1.804 | 1.9012 | 0.056517 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9662 | 31.105 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7986 | 0.054317 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8907 | 30.8386 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7986 | 0.054317 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8907 | 30.8386 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7986 | 0.054317 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8907 | 1804 | 2890.6625 | 0.97887 | 1.0982 | 0.0054333 | 30.8386
1.805 | 1.9022 | 0.056518 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9687 | 31.1136 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7996 | 0.054318 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8931 | 30.8472 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7996 | 0.054318 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8931 | 30.8472 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.7996 | 0.054318 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8931 | 1805 | 2893.0789 | 0.97887 | 1.0982 | 0.0054333 | 30.8472
1.806 | 1.9033 | 0.056518 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9712 | 31.1222 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8006 | 0.054319 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8955 | 30.8558 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8006 | 0.054319 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8955 | 30.8558 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8006 | 0.054319 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8955 | 1806 | 2895.496 | 0.97887 | 1.0982 | 0.0054333 | 30.8558
1.807 | 1.9043 | 0.056519 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9736 | 31.1309 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8016 | 0.05432 | 1.0984 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8979 | 30.8644 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8016 | 0.05432 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8979 | 30.8644 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8016 | 0.05432 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97887 | 2.8979 | 1807 | 2897.9137 | 0.97887 | 1.0982 | 0.0054333 | 30.8644
1.808 | 1.9053 | 0.05652 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9761 | 31.1395 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8026 | 0.054321 | 1.0984 | 1.0983 | 1.0982 | 1.0982 | 0.97888 | 2.9003 | 30.873 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8026 | 0.054321 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97888 | 2.9003 | 30.873 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8026 | 0.054321 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97888 | 2.9003 | 1808 | 2900.3322 | 0.97888 | 1.0982 | 0.0054333 | 30.873
1.809 | 1.9064 | 0.056521 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9786 | 31.1481 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8036 | 0.054321 | 1.0984 | 1.0983 | 1.0982 | 1.0982 | 0.97888 | 2.9028 | 30.8815 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8036 | 0.054321 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97888 | 2.9028 | 30.8815 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8036 | 0.054321 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97888 | 2.9028 | 1809 | 2902.7512 | 0.97888 | 1.0982 | 0.0054333 | 30.8815
1.81 | 1.9074 | 0.056521 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9811 | 31.1567 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8046 | 0.054322 | 1.0984 | 1.0983 | 1.0982 | 1.0982 | 0.97888 | 2.9052 | 30.8901 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8046 | 0.054322 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97888 | 2.9052 | 30.8901 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8046 | 0.054322 | 1.0982 | 1.0982 | 1.0982 | 1.0982 | 0.97888 | 2.9052 | 1810 | 2905.171 | 0.97888 | 1.0982 | 0.0054333 | 30.8901
1.811 | 1.9085 | 0.056522 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9835 | 31.1654 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8056 | 0.054323 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97888 | 2.9076 | 30.8987 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8056 | 0.054323 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97888 | 2.9076 | 30.8987 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8056 | 0.054323 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97888 | 2.9076 | 1811 | 2907.5914 | 0.97888 | 1.0983 | 0.0054333 | 30.8987
1.812 | 1.9095 | 0.056523 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.986 | 31.174 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8066 | 0.054324 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.91 | 30.9073 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8066 | 0.054324 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.91 | 30.9073 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8066 | 0.054324 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.91 | 1812 | 2910.0126 | 0.97889 | 1.0983 | 0.0054333 | 30.9073
1.813 | 1.9105 | 0.056524 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9885 | 31.1826 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8076 | 0.054325 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9124 | 30.9158 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8076 | 0.054325 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9124 | 30.9158 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8076 | 0.054325 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9124 | 1813 | 2912.4343 | 0.97889 | 1.0983 | 0.0054333 | 30.9158
1.814 | 1.9116 | 0.056524 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.991 | 31.1912 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8086 | 0.054326 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9149 | 30.9244 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8086 | 0.054326 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9149 | 30.9244 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8086 | 0.054326 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9149 | 1814 | 2914.8568 | 0.97889 | 1.0983 | 0.0054333 | 30.9244
1.815 | 1.9126 | 0.056525 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9934 | 31.1998 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8096 | 0.054327 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9173 | 30.933 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8096 | 0.054327 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9173 | 30.933 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8096 | 0.054327 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97889 | 2.9173 | 1815 | 2917.2799 | 0.97889 | 1.0983 | 0.0054333 | 30.933
1.816 | 1.9137 | 0.056526 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9959 | 31.2084 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8106 | 0.054328 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9197 | 30.9415 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8106 | 0.054328 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9197 | 30.9415 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8106 | 0.054328 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9197 | 1816 | 2919.7037 | 0.9789 | 1.0983 | 0.0054333 | 30.9415
1.817 | 1.9147 | 0.056527 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 2.9984 | 31.217 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8116 | 0.054329 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9221 | 30.9501 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8116 | 0.054329 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9221 | 30.9501 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8116 | 0.054329 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9221 | 1817 | 2922.1282 | 0.9789 | 1.0983 | 0.0054333 | 30.9501
1.818 | 1.9157 | 0.056527 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 3.0009 | 31.2256 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8126 | 0.05433 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9246 | 30.9587 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8126 | 0.05433 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9246 | 30.9587 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8126 | 0.05433 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.9246 | 1818 | 2924.5533 | 0.9789 | 1.0983 | 0.0054333 | 30.9587
1.819 | 1.9168 | 0.056528 | 1.103 | 1.1031 | 1.1031 | 1.1031 | 3.0034 | 31.2342 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8136 | 0.05433 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.927 | 30.9672 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8136 | 0.05433 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.927 | 30.9672 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8136 | 0.05433 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.9789 | 2.927 | 1819 | 2926.9791 | 0.9789 | 1.0983 | 0.0054333 | 30.9672
1.82 | 1.9178 | 0.056529 | 1.103 | 1.1031 | 1.1032 | 1.1032 | 3.0058 | 31.2428 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8146 | 0.054331 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9294 | 30.9758 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8146 | 0.054331 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9294 | 30.9758 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8146 | 0.054331 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9294 | 1820 | 2929.4056 | 0.97891 | 1.0983 | 0.0054333 | 30.9758
1.821 | 1.9189 | 0.05653 | 1.103 | 1.1031 | 1.1032 | 1.1032 | 3.0083 | 31.2514 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8156 | 0.054332 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9318 | 30.9843 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8156 | 0.054332 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9318 | 30.9843 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8156 | 0.054332 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9318 | 1821 | 2931.8327 | 0.97891 | 1.0983 | 0.0054333 | 30.9843
1.822 | 1.9199 | 0.05653 | 1.103 | 1.1031 | 1.1032 | 1.1032 | 3.0108 | 31.26 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8166 | 0.054333 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9343 | 30.9929 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8166 | 0.054333 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9343 | 30.9929 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8166 | 0.054333 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9343 | 1822 | 2934.2605 | 0.97891 | 1.0983 | 0.0054333 | 30.9929
1.823 | 1.921 | 0.056531 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0133 | 31.2686 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8176 | 0.054334 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9367 | 31.0014 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8176 | 0.054334 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9367 | 31.0014 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8176 | 0.054334 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97891 | 2.9367 | 1823 | 2936.689 | 0.97891 | 1.0983 | 0.0054333 | 31.0014
1.824 | 1.922 | 0.056532 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0158 | 31.2772 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8186 | 0.054335 | 1.0984 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9391 | 31.01 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8186 | 0.054335 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9391 | 31.01 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8186 | 0.054335 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9391 | 1824 | 2939.1182 | 0.97892 | 1.0983 | 0.0054333 | 31.01
1.825 | 1.923 | 0.056533 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0183 | 31.2858 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8196 | 0.054336 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9415 | 31.0185 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8196 | 0.054336 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9415 | 31.0185 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8196 | 0.054336 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9415 | 1825 | 2941.548 | 0.97892 | 1.0983 | 0.0054333 | 31.0185
1.826 | 1.9241 | 0.056533 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0207 | 31.2944 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8206 | 0.054337 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.944 | 31.027 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8206 | 0.054337 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.944 | 31.027 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8206 | 0.054337 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.944 | 1826 | 2943.9785 | 0.97892 | 1.0983 | 0.0054333 | 31.027
1.827 | 1.9251 | 0.056534 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0232 | 31.303 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8216 | 0.054338 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9464 | 31.0356 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8216 | 0.054338 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9464 | 31.0356 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8216 | 0.054338 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9464 | 1827 | 2946.4097 | 0.97892 | 1.0983 | 0.0054333 | 31.0356
1.828 | 1.9262 | 0.056535 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0257 | 31.3116 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8226 | 0.054338 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9488 | 31.0441 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8226 | 0.054338 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9488 | 31.0441 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8226 | 0.054338 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97892 | 2.9488 | 1828 | 2948.8415 | 0.97892 | 1.0983 | 0.0054333 | 31.0441
1.829 | 1.9272 | 0.056535 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0282 | 31.3201 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8236 | 0.054339 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9513 | 31.0527 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8236 | 0.054339 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9513 | 31.0527 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8236 | 0.054339 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9513 | 1829 | 2951.274 | 0.97893 | 1.0983 | 0.0054333 | 31.0527
1.83 | 1.9282 | 0.056536 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0307 | 31.3287 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8246 | 0.05434 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9537 | 31.0612 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8246 | 0.05434 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9537 | 31.0612 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8246 | 0.05434 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9537 | 1830 | 2953.7072 | 0.97893 | 1.0983 | 0.0054333 | 31.0612
1.831 | 1.9293 | 0.056537 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0332 | 31.3373 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8256 | 0.054341 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9561 | 31.0697 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8256 | 0.054341 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9561 | 31.0697 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8256 | 0.054341 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9561 | 1831 | 2956.141 | 0.97893 | 1.0983 | 0.0054333 | 31.0697
1.832 | 1.9303 | 0.056538 | 1.103 | 1.1032 | 1.1032 | 1.1032 | 3.0357 | 31.3459 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8266 | 0.054342 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9586 | 31.0782 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8266 | 0.054342 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9586 | 31.0782 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8266 | 0.054342 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97893 | 2.9586 | 1832 | 2958.5755 | 0.97893 | 1.0983 | 0.0054333 | 31.0782
1.833 | 1.9314 | 0.056538 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0382 | 31.3544 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8276 | 0.054343 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.961 | 31.0868 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8276 | 0.054343 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.961 | 31.0868 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8276 | 0.054343 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.961 | 1833 | 2961.0107 | 0.97894 | 1.0983 | 0.0054333 | 31.0868
1.834 | 1.9324 | 0.056539 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0406 | 31.363 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8286 | 0.054344 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9634 | 31.0953 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8286 | 0.054344 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9634 | 31.0953 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8286 | 0.054344 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9634 | 1834 | 2963.4465 | 0.97894 | 1.0983 | 0.0054333 | 31.0953
1.835 | 1.9334 | 0.05654 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0431 | 31.3716 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8296 | 0.054345 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9659 | 31.1038 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8296 | 0.054345 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9659 | 31.1038 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8296 | 0.054345 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9659 | 1835 | 2965.883 | 0.97894 | 1.0983 | 0.0054333 | 31.1038
1.836 | 1.9345 | 0.056541 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0456 | 31.3801 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8306 | 0.054345 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9683 | 31.1123 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8306 | 0.054345 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9683 | 31.1123 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8306 | 0.054345 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97894 | 2.9683 | 1836 | 2968.3202 | 0.97894 | 1.0983 | 0.0054333 | 31.1123
1.837 | 1.9355 | 0.056541 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0481 | 31.3887 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8316 | 0.054346 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9708 | 31.1208 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8316 | 0.054346 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9708 | 31.1208 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8316 | 0.054346 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9708 | 1837 | 2970.7581 | 0.97895 | 1.0983 | 0.0054333 | 31.1208
1.838 | 1.9366 | 0.056542 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0506 | 31.3972 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8326 | 0.054347 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9732 | 31.1294 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8326 | 0.054347 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9732 | 31.1294 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8326 | 0.054347 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9732 | 1838 | 2973.1966 | 0.97895 | 1.0983 | 0.0054333 | 31.1294
1.839 | 1.9376 | 0.056543 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0531 | 31.4058 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8336 | 0.054348 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9756 | 31.1379 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8336 | 0.054348 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9756 | 31.1379 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8336 | 0.054348 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9756 | 1839 | 2975.6358 | 0.97895 | 1.0983 | 0.0054333 | 31.1379
1.84 | 1.9387 | 0.056544 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0556 | 31.4144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8346 | 0.054349 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9781 | 31.1464 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8346 | 0.054349 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9781 | 31.1464 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8346 | 0.054349 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97895 | 2.9781 | 1840 | 2978.0756 | 0.97895 | 1.0983 | 0.0054333 | 31.1464
1.841 | 1.9397 | 0.056544 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0581 | 31.4229 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8356 | 0.05435 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9805 | 31.1549 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8356 | 0.05435 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9805 | 31.1549 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8356 | 0.05435 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9805 | 1841 | 2980.5161 | 0.97896 | 1.0983 | 0.0054333 | 31.1549
1.842 | 1.9407 | 0.056545 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0606 | 31.4315 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8366 | 0.054351 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.983 | 31.1634 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8366 | 0.054351 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.983 | 31.1634 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8366 | 0.054351 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.983 | 1842 | 2982.9573 | 0.97896 | 1.0983 | 0.0054333 | 31.1634
1.843 | 1.9418 | 0.056546 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0631 | 31.44 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8376 | 0.054352 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9854 | 31.1719 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8376 | 0.054352 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9854 | 31.1719 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8376 | 0.054352 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9854 | 1843 | 2985.3991 | 0.97896 | 1.0983 | 0.0054333 | 31.1719
1.844 | 1.9428 | 0.056546 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0656 | 31.4485 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8386 | 0.054352 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9878 | 31.1804 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8386 | 0.054352 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9878 | 31.1804 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8386 | 0.054352 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97896 | 2.9878 | 1844 | 2987.8417 | 0.97896 | 1.0983 | 0.0054333 | 31.1804
1.845 | 1.9439 | 0.056547 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0681 | 31.4571 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8396 | 0.054353 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9903 | 31.1889 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8396 | 0.054353 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9903 | 31.1889 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8396 | 0.054353 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9903 | 1845 | 2990.2848 | 0.97897 | 1.0983 | 0.0054333 | 31.1889
1.846 | 1.9449 | 0.056548 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0706 | 31.4656 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8406 | 0.054354 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9927 | 31.1974 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8406 | 0.054354 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9927 | 31.1974 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8406 | 0.054354 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9927 | 1846 | 2992.7287 | 0.97897 | 1.0983 | 0.0054333 | 31.1974
1.847 | 1.9459 | 0.056549 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0731 | 31.4742 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8416 | 0.054355 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9952 | 31.2059 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8416 | 0.054355 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9952 | 31.2059 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8416 | 0.054355 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9952 | 1847 | 2995.1732 | 0.97897 | 1.0983 | 0.0054333 | 31.2059
1.848 | 1.947 | 0.056549 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0756 | 31.4827 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8426 | 0.054356 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9976 | 31.2144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8426 | 0.054356 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9976 | 31.2144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8426 | 0.054356 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 2.9976 | 1848 | 2997.6184 | 0.97897 | 1.0983 | 0.0054333 | 31.2144
1.849 | 1.948 | 0.05655 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0781 | 31.4912 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8436 | 0.054357 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 3.0001 | 31.2228 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8436 | 0.054357 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 3.0001 | 31.2228 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8436 | 0.054357 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97897 | 3.0001 | 1849 | 3000.0642 | 0.97897 | 1.0983 | 0.0054333 | 31.2228
1.85 | 1.9491 | 0.056551 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0806 | 31.4998 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8446 | 0.054358 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0025 | 31.2313 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8446 | 0.054358 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0025 | 31.2313 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8446 | 0.054358 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0025 | 1850 | 3002.5107 | 0.97898 | 1.0983 | 0.0054333 | 31.2313
1.851 | 1.9501 | 0.056551 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0831 | 31.5083 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8456 | 0.054358 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.005 | 31.2398 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8456 | 0.054358 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.005 | 31.2398 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8456 | 0.054358 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.005 | 1851 | 3004.9579 | 0.97898 | 1.0983 | 0.0054333 | 31.2398
1.852 | 1.9511 | 0.056552 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0856 | 31.5168 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8466 | 0.054359 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0074 | 31.2483 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8466 | 0.054359 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0074 | 31.2483 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8466 | 0.054359 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0074 | 1852 | 3007.4057 | 0.97898 | 1.0983 | 0.0054333 | 31.2483
1.853 | 1.9522 | 0.056553 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0881 | 31.5253 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8476 | 0.05436 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0099 | 31.2568 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8476 | 0.05436 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0099 | 31.2568 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8476 | 0.05436 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97898 | 3.0099 | 1853 | 3009.8542 | 0.97898 | 1.0983 | 0.0054333 | 31.2568
1.854 | 1.9532 | 0.056554 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0906 | 31.5339 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8486 | 0.054361 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0123 | 31.2652 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8486 | 0.054361 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0123 | 31.2652 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8486 | 0.054361 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0123 | 1854 | 3012.3034 | 0.97899 | 1.0983 | 0.0054333 | 31.2652
1.855 | 1.9543 | 0.056554 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0931 | 31.5424 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8496 | 0.054362 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0148 | 31.2737 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8496 | 0.054362 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0148 | 31.2737 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8496 | 0.054362 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0148 | 1855 | 3014.7532 | 0.97899 | 1.0983 | 0.0054333 | 31.2737
1.856 | 1.9553 | 0.056555 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0956 | 31.5509 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8506 | 0.054363 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0172 | 31.2822 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8506 | 0.054363 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0172 | 31.2822 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8506 | 0.054363 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0172 | 1856 | 3017.2037 | 0.97899 | 1.0983 | 0.0054333 | 31.2822
1.857 | 1.9564 | 0.056556 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.0981 | 31.5594 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8516 | 0.054364 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0197 | 31.2907 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8516 | 0.054364 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0197 | 31.2907 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8516 | 0.054364 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.97899 | 3.0197 | 1857 | 3019.6549 | 0.97899 | 1.0983 | 0.0054333 | 31.2907
1.858 | 1.9574 | 0.056556 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1006 | 31.5679 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8526 | 0.054365 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0221 | 31.2991 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8526 | 0.054365 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0221 | 31.2991 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8526 | 0.054365 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0221 | 1858 | 3022.1067 | 0.979 | 1.0983 | 0.0054333 | 31.2991
1.859 | 1.9584 | 0.056557 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1031 | 31.5764 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8536 | 0.054365 | 1.0985 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0246 | 31.3076 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8536 | 0.054365 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0246 | 31.3076 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8536 | 0.054365 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0246 | 1859 | 3024.5592 | 0.979 | 1.0983 | 0.0054333 | 31.3076
1.86 | 1.9595 | 0.056558 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1057 | 31.5849 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8546 | 0.054366 | 1.0985 | 1.0984 | 1.0983 | 1.0983 | 0.979 | 3.027 | 31.316 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8546 | 0.054366 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.027 | 31.316 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8546 | 0.054366 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.027 | 1860 | 3027.0123 | 0.979 | 1.0983 | 0.0054333 | 31.316
1.861 | 1.9605 | 0.056559 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1082 | 31.5934 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8556 | 0.054367 | 1.0985 | 1.0984 | 1.0983 | 1.0983 | 0.979 | 3.0295 | 31.3245 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8556 | 0.054367 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0295 | 31.3245 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8556 | 0.054367 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0295 | 1861 | 3029.4661 | 0.979 | 1.0983 | 0.0054333 | 31.3245
1.862 | 1.9616 | 0.056559 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1107 | 31.6019 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8566 | 0.054368 | 1.0985 | 1.0984 | 1.0983 | 1.0983 | 0.979 | 3.0319 | 31.333 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8566 | 0.054368 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0319 | 31.333 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8566 | 0.054368 | 1.0983 | 1.0983 | 1.0983 | 1.0983 | 0.979 | 3.0319 | 1862 | 3031.9206 | 0.979 | 1.0983 | 0.0054333 | 31.333
1.863 | 1.9626 | 0.05656 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1132 | 31.6104 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8576 | 0.054369 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0344 | 31.3414 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8576 | 0.054369 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0344 | 31.3414 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8576 | 0.054369 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0344 | 1863 | 3034.3757 | 0.97901 | 1.0984 | 0.0054333 | 31.3414
1.864 | 1.9636 | 0.056561 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1157 | 31.6189 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8586 | 0.05437 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0368 | 31.3499 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8586 | 0.05437 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0368 | 31.3499 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8586 | 0.05437 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0368 | 1864 | 3036.8315 | 0.97901 | 1.0984 | 0.0054333 | 31.3499
1.865 | 1.9647 | 0.056561 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1182 | 31.6274 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8596 | 0.05437 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0393 | 31.3583 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8596 | 0.05437 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0393 | 31.3583 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8596 | 0.05437 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0393 | 1865 | 3039.288 | 0.97901 | 1.0984 | 0.0054333 | 31.3583
1.866 | 1.9657 | 0.056562 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1207 | 31.6359 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8606 | 0.054371 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0417 | 31.3668 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8606 | 0.054371 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0417 | 31.3668 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8606 | 0.054371 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97901 | 3.0417 | 1866 | 3041.7451 | 0.97901 | 1.0984 | 0.0054333 | 31.3668
1.867 | 1.9668 | 0.056563 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1232 | 31.6444 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8616 | 0.054372 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0442 | 31.3752 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8616 | 0.054372 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0442 | 31.3752 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8616 | 0.054372 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0442 | 1867 | 3044.2029 | 0.97902 | 1.0984 | 0.0054333 | 31.3752
1.868 | 1.9678 | 0.056564 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1257 | 31.6529 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8626 | 0.054373 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0467 | 31.3837 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8626 | 0.054373 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0467 | 31.3837 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8626 | 0.054373 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0467 | 1868 | 3046.6613 | 0.97902 | 1.0984 | 0.0054333 | 31.3837
1.869 | 1.9688 | 0.056564 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1283 | 31.6614 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8636 | 0.054374 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0491 | 31.3921 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8636 | 0.054374 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0491 | 31.3921 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8636 | 0.054374 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0491 | 1869 | 3049.1204 | 0.97902 | 1.0984 | 0.0054333 | 31.3921
1.87 | 1.9699 | 0.056565 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1308 | 31.6699 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8646 | 0.054375 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0516 | 31.4005 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8646 | 0.054375 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0516 | 31.4005 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8646 | 0.054375 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97902 | 3.0516 | 1870 | 3051.5802 | 0.97902 | 1.0984 | 0.0054333 | 31.4005
1.871 | 1.9709 | 0.056566 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1333 | 31.6784 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8656 | 0.054376 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.054 | 31.409 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8656 | 0.054376 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.054 | 31.409 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8656 | 0.054376 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.054 | 1871 | 3054.0406 | 0.97903 | 1.0984 | 0.0054333 | 31.409
1.872 | 1.972 | 0.056566 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1358 | 31.6868 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8666 | 0.054376 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0565 | 31.4174 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8666 | 0.054376 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0565 | 31.4174 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8666 | 0.054376 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0565 | 1872 | 3056.5017 | 0.97903 | 1.0984 | 0.0054333 | 31.4174
1.873 | 1.973 | 0.056567 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1383 | 31.6953 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8676 | 0.054377 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.059 | 31.4258 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8676 | 0.054377 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.059 | 31.4258 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8676 | 0.054377 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.059 | 1873 | 3058.9635 | 0.97903 | 1.0984 | 0.0054333 | 31.4258
1.874 | 1.9741 | 0.056568 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1408 | 31.7038 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8686 | 0.054378 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0614 | 31.4343 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8686 | 0.054378 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0614 | 31.4343 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8686 | 0.054378 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0614 | 1874 | 3061.4259 | 0.97903 | 1.0984 | 0.0054333 | 31.4343
1.875 | 1.9751 | 0.056568 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1434 | 31.7123 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8696 | 0.054379 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0639 | 31.4427 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8696 | 0.054379 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0639 | 31.4427 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8696 | 0.054379 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97903 | 3.0639 | 1875 | 3063.8889 | 0.97903 | 1.0984 | 0.0054333 | 31.4427
1.876 | 1.9761 | 0.056569 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1459 | 31.7207 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8706 | 0.05438 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0664 | 31.4511 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8706 | 0.05438 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0664 | 31.4511 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8706 | 0.05438 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0664 | 1876 | 3066.3527 | 0.97904 | 1.0984 | 0.0054333 | 31.4511
1.877 | 1.9772 | 0.05657 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1484 | 31.7292 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8716 | 0.054381 | 1.0985 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0688 | 31.4596 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8716 | 0.054381 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0688 | 31.4596 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8716 | 0.054381 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0688 | 1877 | 3068.8171 | 0.97904 | 1.0984 | 0.0054333 | 31.4596
1.878 | 1.9782 | 0.056571 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1509 | 31.7377 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8726 | 0.054381 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0713 | 31.468 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8726 | 0.054381 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0713 | 31.468 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8726 | 0.054381 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0713 | 1878 | 3071.2821 | 0.97904 | 1.0984 | 0.0054333 | 31.468
1.879 | 1.9793 | 0.056571 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1534 | 31.7461 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8736 | 0.054382 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0737 | 31.4764 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8736 | 0.054382 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0737 | 31.4764 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8736 | 0.054382 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97904 | 3.0737 | 1879 | 3073.7478 | 0.97904 | 1.0984 | 0.0054333 | 31.4764
1.88 | 1.9803 | 0.056572 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.156 | 31.7546 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8746 | 0.054383 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0762 | 31.4848 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8746 | 0.054383 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0762 | 31.4848 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8746 | 0.054383 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0762 | 1880 | 3076.2142 | 0.97905 | 1.0984 | 0.0054333 | 31.4848
1.881 | 1.9813 | 0.056573 | 1.1031 | 1.1032 | 1.1032 | 1.1032 | 3.1585 | 31.763 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8756 | 0.054384 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0787 | 31.4932 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8756 | 0.054384 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0787 | 31.4932 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8756 | 0.054384 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0787 | 1881 | 3078.6812 | 0.97905 | 1.0984 | 0.0054333 | 31.4932
1.882 | 1.9824 | 0.056573 | 1.1031 | 1.1032 | 1.1033 | 1.1033 | 3.161 | 31.7715 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8766 | 0.054385 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0811 | 31.5016 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8766 | 0.054385 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0811 | 31.5016 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8766 | 0.054385 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0811 | 1882 | 3081.1489 | 0.97905 | 1.0984 | 0.0054333 | 31.5016
1.883 | 1.9834 | 0.056574 | 1.1031 | 1.1032 | 1.1033 | 1.1033 | 3.1635 | 31.78 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8776 | 0.054386 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0836 | 31.51 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8776 | 0.054386 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0836 | 31.51 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8776 | 0.054386 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0836 | 1883 | 3083.6173 | 0.97905 | 1.0984 | 0.0054333 | 31.51
1.884 | 1.9845 | 0.056575 | 1.1031 | 1.1032 | 1.1033 | 1.1033 | 3.1661 | 31.7884 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8786 | 0.054386 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0861 | 31.5185 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8786 | 0.054386 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0861 | 31.5185 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8786 | 0.054386 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97905 | 3.0861 | 1884 | 3086.0863 | 0.97905 | 1.0984 | 0.0054333 | 31.5185
1.885 | 1.9855 | 0.056575 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1686 | 31.7969 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8796 | 0.054387 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.0886 | 31.5269 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8796 | 0.054387 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.0886 | 31.5269 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8796 | 0.054387 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.0886 | 1885 | 3088.5559 | 0.97906 | 1.0984 | 0.0054333 | 31.5269
1.886 | 1.9865 | 0.056576 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1711 | 31.8053 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8806 | 0.054388 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.091 | 31.5353 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8806 | 0.054388 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.091 | 31.5353 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8806 | 0.054388 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.091 | 1886 | 3091.0263 | 0.97906 | 1.0984 | 0.0054333 | 31.5353
1.887 | 1.9876 | 0.056577 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1736 | 31.8138 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8816 | 0.054389 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.0935 | 31.5437 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8816 | 0.054389 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.0935 | 31.5437 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8816 | 0.054389 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.0935 | 1887 | 3093.4973 | 0.97906 | 1.0984 | 0.0054333 | 31.5437
1.888 | 1.9886 | 0.056577 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1762 | 31.8222 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8826 | 0.05439 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.096 | 31.5521 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8826 | 0.05439 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.096 | 31.5521 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8826 | 0.05439 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97906 | 3.096 | 1888 | 3095.9689 | 0.97906 | 1.0984 | 0.0054333 | 31.5521
1.889 | 1.9897 | 0.056578 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1787 | 31.8306 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8836 | 0.054391 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.0984 | 31.5605 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8836 | 0.054391 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.0984 | 31.5605 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8836 | 0.054391 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.0984 | 1889 | 3098.4412 | 0.97907 | 1.0984 | 0.0054333 | 31.5605
1.89 | 1.9907 | 0.056579 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1812 | 31.8391 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8846 | 0.054391 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1009 | 31.5689 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8846 | 0.054391 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1009 | 31.5689 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8846 | 0.054391 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1009 | 1890 | 3100.9142 | 0.97907 | 1.0984 | 0.0054333 | 31.5689
1.891 | 1.9918 | 0.05658 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1838 | 31.8475 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8856 | 0.054392 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1034 | 31.5772 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8856 | 0.054392 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1034 | 31.5772 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8856 | 0.054392 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1034 | 1891 | 3103.3878 | 0.97907 | 1.0984 | 0.0054333 | 31.5772
1.892 | 1.9928 | 0.05658 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1863 | 31.856 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8866 | 0.054393 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1059 | 31.5856 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8866 | 0.054393 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1059 | 31.5856 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8866 | 0.054393 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97907 | 3.1059 | 1892 | 3105.8621 | 0.97907 | 1.0984 | 0.0054333 | 31.5856
1.893 | 1.9938 | 0.056581 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1888 | 31.8644 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8876 | 0.054394 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1083 | 31.594 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8876 | 0.054394 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1083 | 31.594 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8876 | 0.054394 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1083 | 1893 | 3108.337 | 0.97908 | 1.0984 | 0.0054333 | 31.594
1.894 | 1.9949 | 0.056582 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1914 | 31.8728 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8886 | 0.054395 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1108 | 31.6024 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8886 | 0.054395 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1108 | 31.6024 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8886 | 0.054395 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1108 | 1894 | 3110.8126 | 0.97908 | 1.0984 | 0.0054333 | 31.6024
1.895 | 1.9959 | 0.056582 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1939 | 31.8812 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8896 | 0.054396 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1133 | 31.6108 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8896 | 0.054396 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1133 | 31.6108 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8896 | 0.054396 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1133 | 1895 | 3113.2888 | 0.97908 | 1.0984 | 0.0054333 | 31.6108
1.896 | 1.997 | 0.056583 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1964 | 31.8897 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8906 | 0.054396 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1158 | 31.6192 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8906 | 0.054396 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1158 | 31.6192 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8906 | 0.054396 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1158 | 1896 | 3115.7657 | 0.97908 | 1.0984 | 0.0054333 | 31.6192
1.897 | 1.998 | 0.056584 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.1989 | 31.8981 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8916 | 0.054397 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1182 | 31.6276 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8916 | 0.054397 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1182 | 31.6276 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8916 | 0.054397 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97908 | 3.1182 | 1897 | 3118.2433 | 0.97908 | 1.0984 | 0.0054333 | 31.6276
1.898 | 1.999 | 0.056584 | 1.1031 | 1.1033 | 1.1033 | 1.1033 | 3.2015 | 31.9065 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8926 | 0.054398 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1207 | 31.6359 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8926 | 0.054398 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1207 | 31.6359 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8926 | 0.054398 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1207 | 1898 | 3120.7215 | 0.97909 | 1.0984 | 0.0054333 | 31.6359
1.899 | 2.0001 | 0.056585 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.204 | 31.9149 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8936 | 0.054399 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1232 | 31.6443 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8936 | 0.054399 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1232 | 31.6443 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8936 | 0.054399 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1232 | 1899 | 3123.2004 | 0.97909 | 1.0984 | 0.0054333 | 31.6443
1.9 | 2.0011 | 0.056586 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2066 | 31.9233 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8946 | 0.0544 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1257 | 31.6527 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8946 | 0.0544 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1257 | 31.6527 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8946 | 0.0544 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1257 | 1900 | 3125.6799 | 0.97909 | 1.0984 | 0.0054333 | 31.6527
1.901 | 2.0022 | 0.056586 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2091 | 31.9318 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8956 | 0.054401 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1282 | 31.661 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8956 | 0.054401 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1282 | 31.661 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8956 | 0.054401 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97909 | 3.1282 | 1901 | 3128.1601 | 0.97909 | 1.0984 | 0.0054333 | 31.661
1.902 | 2.0032 | 0.056587 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2116 | 31.9402 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8966 | 0.054401 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1306 | 31.6694 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8966 | 0.054401 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1306 | 31.6694 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8966 | 0.054401 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1306 | 1902 | 3130.6409 | 0.9791 | 1.0984 | 0.0054333 | 31.6694
1.903 | 2.0042 | 0.056588 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2142 | 31.9486 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8976 | 0.054402 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1331 | 31.6778 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8976 | 0.054402 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1331 | 31.6778 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8976 | 0.054402 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1331 | 1903 | 3133.1224 | 0.9791 | 1.0984 | 0.0054333 | 31.6778
1.904 | 2.0053 | 0.056588 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2167 | 31.957 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8986 | 0.054403 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1356 | 31.6861 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8986 | 0.054403 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1356 | 31.6861 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8986 | 0.054403 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1356 | 1904 | 3135.6046 | 0.9791 | 1.0984 | 0.0054333 | 31.6861
1.905 | 2.0063 | 0.056589 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2192 | 31.9654 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8996 | 0.054404 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1381 | 31.6945 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8996 | 0.054404 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1381 | 31.6945 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.8996 | 0.054404 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1381 | 1905 | 3138.0874 | 0.9791 | 1.0984 | 0.0054333 | 31.6945
1.906 | 2.0074 | 0.05659 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2218 | 31.9738 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9006 | 0.054405 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1406 | 31.7029 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9006 | 0.054405 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1406 | 31.7029 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9006 | 0.054405 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.9791 | 3.1406 | 1906 | 3140.5708 | 0.9791 | 1.0984 | 0.0054333 | 31.7029
1.907 | 2.0084 | 0.05659 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2243 | 31.9822 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9016 | 0.054405 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1431 | 31.7112 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9016 | 0.054405 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1431 | 31.7112 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9016 | 0.054405 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1431 | 1907 | 3143.0549 | 0.97911 | 1.0984 | 0.0054333 | 31.7112
1.908 | 2.0095 | 0.056591 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2269 | 31.9906 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9026 | 0.054406 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1455 | 31.7196 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9026 | 0.054406 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1455 | 31.7196 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9026 | 0.054406 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1455 | 1908 | 3145.5397 | 0.97911 | 1.0984 | 0.0054333 | 31.7196
1.909 | 2.0105 | 0.056592 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2294 | 31.999 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9036 | 0.054407 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.148 | 31.7279 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9036 | 0.054407 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.148 | 31.7279 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9036 | 0.054407 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.148 | 1909 | 3148.0251 | 0.97911 | 1.0984 | 0.0054333 | 31.7279
1.91 | 2.0115 | 0.056593 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2319 | 32.0074 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9046 | 0.054408 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1505 | 31.7363 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9046 | 0.054408 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1505 | 31.7363 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9046 | 0.054408 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.1505 | 1910 | 3150.5112 | 0.97911 | 1.0984 | 0.0054333 | 31.7363
1.911 | 2.0126 | 0.056593 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2345 | 32.0158 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9056 | 0.054409 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.153 | 31.7446 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9056 | 0.054409 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.153 | 31.7446 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9056 | 0.054409 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97911 | 3.153 | 1911 | 3152.998 | 0.97911 | 1.0984 | 0.0054333 | 31.7446
1.912 | 2.0136 | 0.056594 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.237 | 32.0242 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9066 | 0.054409 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.1555 | 31.753 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9066 | 0.054409 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.1555 | 31.753 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9066 | 0.054409 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.1555 | 1912 | 3155.4853 | 0.97912 | 1.0984 | 0.0054333 | 31.753
1.913 | 2.0147 | 0.056595 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2396 | 32.0326 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9076 | 0.05441 | 1.0986 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.158 | 31.7613 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9076 | 0.05441 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.158 | 31.7613 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9076 | 0.05441 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.158 | 1913 | 3157.9734 | 0.97912 | 1.0984 | 0.0054333 | 31.7613
1.914 | 2.0157 | 0.056595 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2421 | 32.041 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9086 | 0.054411 | 1.0986 | 1.0985 | 1.0984 | 1.0984 | 0.97912 | 3.1605 | 31.7696 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9086 | 0.054411 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.1605 | 31.7696 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9086 | 0.054411 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.1605 | 1914 | 3160.4621 | 0.97912 | 1.0984 | 0.0054333 | 31.7696
1.915 | 2.0167 | 0.056596 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2447 | 32.0493 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9096 | 0.054412 | 1.0986 | 1.0985 | 1.0984 | 1.0984 | 0.97912 | 3.163 | 31.778 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9096 | 0.054412 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.163 | 31.778 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9096 | 0.054412 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97912 | 3.163 | 1915 | 3162.9514 | 0.97912 | 1.0984 | 0.0054333 | 31.778
1.916 | 2.0178 | 0.056597 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2472 | 32.0577 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9106 | 0.054413 | 1.0986 | 1.0985 | 1.0984 | 1.0984 | 0.97913 | 3.1654 | 31.7863 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9106 | 0.054413 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97913 | 3.1654 | 31.7863 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9106 | 0.054413 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97913 | 3.1654 | 1916 | 3165.4414 | 0.97913 | 1.0984 | 0.0054333 | 31.7863
1.917 | 2.0188 | 0.056597 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2498 | 32.0661 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9116 | 0.054414 | 1.0986 | 1.0985 | 1.0984 | 1.0984 | 0.97913 | 3.1679 | 31.7947 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9116 | 0.054414 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97913 | 3.1679 | 31.7947 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9116 | 0.054414 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 0.97913 | 3.1679 | 1917 | 3167.9321 | 0.97913 | 1.0984 | 0.0054333 | 31.7947
1.918 | 2.0199 | 0.056598 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2523 | 32.0745 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9126 | 0.054414 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1704 | 31.803 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9126 | 0.054414 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1704 | 31.803 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9126 | 0.054414 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1704 | 1918 | 3170.4234 | 0.97913 | 1.0985 | 0.0054333 | 31.803
1.919 | 2.0209 | 0.056599 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2549 | 32.0828 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9136 | 0.054415 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1729 | 31.8113 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9136 | 0.054415 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1729 | 31.8113 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9136 | 0.054415 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1729 | 1919 | 3172.9154 | 0.97913 | 1.0985 | 0.0054333 | 31.8113
1.92 | 2.0219 | 0.056599 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2574 | 32.0912 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9146 | 0.054416 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1754 | 31.8197 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9146 | 0.054416 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1754 | 31.8197 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9146 | 0.054416 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97913 | 3.1754 | 1920 | 3175.408 | 0.97913 | 1.0985 | 0.0054333 | 31.8197
1.921 | 2.023 | 0.0566 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.26 | 32.0996 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9156 | 0.054417 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1779 | 31.828 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9156 | 0.054417 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1779 | 31.828 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9156 | 0.054417 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1779 | 1921 | 3177.9012 | 0.97914 | 1.0985 | 0.0054333 | 31.828
1.922 | 2.024 | 0.056601 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2625 | 32.108 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9166 | 0.054418 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1804 | 31.8363 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9166 | 0.054418 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1804 | 31.8363 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9166 | 0.054418 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1804 | 1922 | 3180.3952 | 0.97914 | 1.0985 | 0.0054333 | 31.8363
1.923 | 2.0251 | 0.056601 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2651 | 32.1163 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9176 | 0.054418 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1829 | 31.8446 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9176 | 0.054418 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1829 | 31.8446 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9176 | 0.054418 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1829 | 1923 | 3182.8897 | 0.97914 | 1.0985 | 0.0054333 | 31.8446
1.924 | 2.0261 | 0.056602 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2676 | 32.1247 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9186 | 0.054419 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1854 | 31.8529 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9186 | 0.054419 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1854 | 31.8529 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9186 | 0.054419 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97914 | 3.1854 | 1924 | 3185.385 | 0.97914 | 1.0985 | 0.0054333 | 31.8529
1.925 | 2.0272 | 0.056603 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2702 | 32.1331 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9196 | 0.05442 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1879 | 31.8613 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9196 | 0.05442 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1879 | 31.8613 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9196 | 0.05442 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1879 | 1925 | 3187.8808 | 0.97915 | 1.0985 | 0.0054333 | 31.8613
1.926 | 2.0282 | 0.056603 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2727 | 32.1414 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9206 | 0.054421 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1904 | 31.8696 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9206 | 0.054421 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1904 | 31.8696 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9206 | 0.054421 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1904 | 1926 | 3190.3774 | 0.97915 | 1.0985 | 0.0054333 | 31.8696
1.927 | 2.0292 | 0.056604 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2753 | 32.1498 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9216 | 0.054422 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1929 | 31.8779 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9216 | 0.054422 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1929 | 31.8779 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9216 | 0.054422 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1929 | 1927 | 3192.8745 | 0.97915 | 1.0985 | 0.0054333 | 31.8779
1.928 | 2.0303 | 0.056605 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2778 | 32.1581 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9226 | 0.054422 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1954 | 31.8862 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9226 | 0.054422 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1954 | 31.8862 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9226 | 0.054422 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1954 | 1928 | 3195.3724 | 0.97915 | 1.0985 | 0.0054333 | 31.8862
1.929 | 2.0313 | 0.056605 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2804 | 32.1665 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9236 | 0.054423 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1979 | 31.8945 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9236 | 0.054423 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1979 | 31.8945 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9236 | 0.054423 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97915 | 3.1979 | 1929 | 3197.8709 | 0.97915 | 1.0985 | 0.0054333 | 31.8945
1.93 | 2.0324 | 0.056606 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2829 | 32.1748 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9246 | 0.054424 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2004 | 31.9028 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9246 | 0.054424 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2004 | 31.9028 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9246 | 0.054424 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2004 | 1930 | 3200.37 | 0.97916 | 1.0985 | 0.0054333 | 31.9028
1.931 | 2.0334 | 0.056607 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2855 | 32.1832 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9256 | 0.054425 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2029 | 31.9111 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9256 | 0.054425 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2029 | 31.9111 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9256 | 0.054425 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2029 | 1931 | 3202.8698 | 0.97916 | 1.0985 | 0.0054333 | 31.9111
1.932 | 2.0344 | 0.056607 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.288 | 32.1915 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9266 | 0.054426 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2054 | 31.9194 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9266 | 0.054426 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2054 | 31.9194 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9266 | 0.054426 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2054 | 1932 | 3205.3702 | 0.97916 | 1.0985 | 0.0054333 | 31.9194
1.933 | 2.0355 | 0.056608 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2906 | 32.1999 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9276 | 0.054426 | 1.0986 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2079 | 31.9277 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9276 | 0.054426 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2079 | 31.9277 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9276 | 0.054426 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2079 | 1933 | 3207.8713 | 0.97916 | 1.0985 | 0.0054333 | 31.9277
1.934 | 2.0365 | 0.056609 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2932 | 32.2082 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9286 | 0.054427 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2104 | 31.936 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9286 | 0.054427 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2104 | 31.936 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9286 | 0.054427 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97916 | 3.2104 | 1934 | 3210.373 | 0.97916 | 1.0985 | 0.0054333 | 31.936
1.935 | 2.0376 | 0.056609 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2957 | 32.2165 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9296 | 0.054428 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2129 | 31.9443 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9296 | 0.054428 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2129 | 31.9443 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9296 | 0.054428 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2129 | 1935 | 3212.8754 | 0.97917 | 1.0985 | 0.0054333 | 31.9443
1.936 | 2.0386 | 0.05661 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.2983 | 32.2249 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9306 | 0.054429 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2154 | 31.9526 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9306 | 0.054429 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2154 | 31.9526 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9306 | 0.054429 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2154 | 1936 | 3215.3784 | 0.97917 | 1.0985 | 0.0054333 | 31.9526
1.937 | 2.0396 | 0.05661 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3008 | 32.2332 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9316 | 0.054429 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2179 | 31.9609 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9316 | 0.054429 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2179 | 31.9609 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9316 | 0.054429 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2179 | 1937 | 3217.8821 | 0.97917 | 1.0985 | 0.0054333 | 31.9609
1.938 | 2.0407 | 0.056611 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3034 | 32.2416 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9326 | 0.05443 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2204 | 31.9692 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9326 | 0.05443 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2204 | 31.9692 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9326 | 0.05443 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97917 | 3.2204 | 1938 | 3220.3865 | 0.97917 | 1.0985 | 0.0054333 | 31.9692
1.939 | 2.0417 | 0.056612 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.306 | 32.2499 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9336 | 0.054431 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2229 | 31.9775 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9336 | 0.054431 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2229 | 31.9775 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9336 | 0.054431 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2229 | 1939 | 3222.8914 | 0.97918 | 1.0985 | 0.0054333 | 31.9775
1.94 | 2.0428 | 0.056612 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3085 | 32.2582 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9346 | 0.054432 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2254 | 31.9858 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9346 | 0.054432 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2254 | 31.9858 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9346 | 0.054432 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2254 | 1940 | 3225.3971 | 0.97918 | 1.0985 | 0.0054333 | 31.9858
1.941 | 2.0438 | 0.056613 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3111 | 32.2665 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9356 | 0.054433 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2279 | 31.994 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9356 | 0.054433 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2279 | 31.994 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9356 | 0.054433 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2279 | 1941 | 3227.9034 | 0.97918 | 1.0985 | 0.0054333 | 31.994
1.942 | 2.0449 | 0.056614 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3137 | 32.2749 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9366 | 0.054433 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2304 | 32.0023 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9366 | 0.054433 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2304 | 32.0023 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9366 | 0.054433 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2304 | 1942 | 3230.4103 | 0.97918 | 1.0985 | 0.0054333 | 32.0023
1.943 | 2.0459 | 0.056614 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3162 | 32.2832 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9376 | 0.054434 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2329 | 32.0106 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9376 | 0.054434 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2329 | 32.0106 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9376 | 0.054434 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97918 | 3.2329 | 1943 | 3232.9179 | 0.97918 | 1.0985 | 0.0054333 | 32.0106
1.944 | 2.0469 | 0.056615 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3188 | 32.2915 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9386 | 0.054435 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2354 | 32.0189 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9386 | 0.054435 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2354 | 32.0189 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9386 | 0.054435 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2354 | 1944 | 3235.4261 | 0.97919 | 1.0985 | 0.0054333 | 32.0189
1.945 | 2.048 | 0.056616 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3213 | 32.2998 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9396 | 0.054436 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2379 | 32.0271 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9396 | 0.054436 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2379 | 32.0271 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9396 | 0.054436 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2379 | 1945 | 3237.935 | 0.97919 | 1.0985 | 0.0054333 | 32.0271
1.946 | 2.049 | 0.056616 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3239 | 32.3081 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9406 | 0.054437 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2404 | 32.0354 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9406 | 0.054437 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2404 | 32.0354 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9406 | 0.054437 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2404 | 1946 | 3240.4445 | 0.97919 | 1.0985 | 0.0054333 | 32.0354
1.947 | 2.0501 | 0.056617 | 1.1032 | 1.1033 | 1.1033 | 1.1033 | 3.3265 | 32.3165 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9416 | 0.054437 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.243 | 32.0437 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9416 | 0.054437 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.243 | 32.0437 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9416 | 0.054437 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.243 | 1947 | 3242.9547 | 0.97919 | 1.0985 | 0.0054333 | 32.0437
1.948 | 2.0511 | 0.056618 | 1.1032 | 1.1033 | 1.1034 | 1.1034 | 3.329 | 32.3248 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9426 | 0.054438 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2455 | 32.052 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9426 | 0.054438 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2455 | 32.052 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9426 | 0.054438 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97919 | 3.2455 | 1948 | 3245.4655 | 0.97919 | 1.0985 | 0.0054333 | 32.052
1.949 | 2.0521 | 0.056618 | 1.1032 | 1.1033 | 1.1034 | 1.1034 | 3.3316 | 32.3331 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9436 | 0.054439 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.248 | 32.0602 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9436 | 0.054439 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.248 | 32.0602 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9436 | 0.054439 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.248 | 1949 | 3247.977 | 0.9792 | 1.0985 | 0.0054333 | 32.0602
1.95 | 2.0532 | 0.056619 | 1.1032 | 1.1033 | 1.1034 | 1.1034 | 3.3342 | 32.3414 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9446 | 0.05444 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.2505 | 32.0685 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9446 | 0.05444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.2505 | 32.0685 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9446 | 0.05444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.2505 | 1950 | 3250.4891 | 0.9792 | 1.0985 | 0.0054333 | 32.0685
1.951 | 2.0542 | 0.05662 | 1.1032 | 1.1033 | 1.1034 | 1.1034 | 3.3368 | 32.3497 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9456 | 0.05444 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.253 | 32.0767 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9456 | 0.05444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.253 | 32.0767 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9456 | 0.05444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.253 | 1951 | 3253.0018 | 0.9792 | 1.0985 | 0.0054333 | 32.0767
1.952 | 2.0553 | 0.05662 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3393 | 32.358 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9466 | 0.054441 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.2555 | 32.085 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9466 | 0.054441 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.2555 | 32.085 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9466 | 0.054441 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.9792 | 3.2555 | 1952 | 3255.5153 | 0.9792 | 1.0985 | 0.0054333 | 32.085
1.953 | 2.0563 | 0.056621 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3419 | 32.3663 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9476 | 0.054442 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.258 | 32.0933 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9476 | 0.054442 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.258 | 32.0933 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9476 | 0.054442 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.258 | 1953 | 3258.0293 | 0.97921 | 1.0985 | 0.0054333 | 32.0933
1.954 | 2.0573 | 0.056622 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3445 | 32.3746 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9486 | 0.054443 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2605 | 32.1015 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9486 | 0.054443 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2605 | 32.1015 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9486 | 0.054443 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2605 | 1954 | 3260.544 | 0.97921 | 1.0985 | 0.0054333 | 32.1015
1.955 | 2.0584 | 0.056622 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.347 | 32.3829 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9496 | 0.054444 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2631 | 32.1098 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9496 | 0.054444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2631 | 32.1098 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9496 | 0.054444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2631 | 1955 | 3263.0594 | 0.97921 | 1.0985 | 0.0054333 | 32.1098
1.956 | 2.0594 | 0.056623 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3496 | 32.3912 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9506 | 0.054444 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2656 | 32.118 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9506 | 0.054444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2656 | 32.118 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9506 | 0.054444 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2656 | 1956 | 3265.5754 | 0.97921 | 1.0985 | 0.0054333 | 32.118
1.957 | 2.0605 | 0.056623 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3522 | 32.3995 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9516 | 0.054445 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2681 | 32.1263 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9516 | 0.054445 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2681 | 32.1263 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9516 | 0.054445 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97921 | 3.2681 | 1957 | 3268.092 | 0.97921 | 1.0985 | 0.0054333 | 32.1263
1.958 | 2.0615 | 0.056624 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3548 | 32.4078 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9526 | 0.054446 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2706 | 32.1345 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9526 | 0.054446 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2706 | 32.1345 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9526 | 0.054446 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2706 | 1958 | 3270.6093 | 0.97922 | 1.0985 | 0.0054333 | 32.1345
1.959 | 2.0626 | 0.056625 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3573 | 32.4161 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9536 | 0.054447 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2731 | 32.1428 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9536 | 0.054447 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2731 | 32.1428 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9536 | 0.054447 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2731 | 1959 | 3273.1273 | 0.97922 | 1.0985 | 0.0054333 | 32.1428
1.96 | 2.0636 | 0.056625 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3599 | 32.4244 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9546 | 0.054447 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2756 | 32.151 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9546 | 0.054447 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2756 | 32.151 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9546 | 0.054447 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2756 | 1960 | 3275.6458 | 0.97922 | 1.0985 | 0.0054333 | 32.151
1.961 | 2.0646 | 0.056626 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3625 | 32.4326 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9556 | 0.054448 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2782 | 32.1592 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9556 | 0.054448 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2782 | 32.1592 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9556 | 0.054448 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2782 | 1961 | 3278.1651 | 0.97922 | 1.0985 | 0.0054333 | 32.1592
1.962 | 2.0657 | 0.056627 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3651 | 32.4409 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9566 | 0.054449 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2807 | 32.1675 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9566 | 0.054449 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2807 | 32.1675 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9566 | 0.054449 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97922 | 3.2807 | 1962 | 3280.6849 | 0.97922 | 1.0985 | 0.0054333 | 32.1675
1.963 | 2.0667 | 0.056627 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3676 | 32.4492 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9576 | 0.05445 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2832 | 32.1757 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9576 | 0.05445 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2832 | 32.1757 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9576 | 0.05445 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2832 | 1963 | 3283.2055 | 0.97923 | 1.0985 | 0.0054333 | 32.1757
1.964 | 2.0678 | 0.056628 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3702 | 32.4575 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9586 | 0.05445 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2857 | 32.184 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9586 | 0.05445 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2857 | 32.184 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9586 | 0.05445 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2857 | 1964 | 3285.7266 | 0.97923 | 1.0985 | 0.0054333 | 32.184
1.965 | 2.0688 | 0.056629 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3728 | 32.4658 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9596 | 0.054451 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2882 | 32.1922 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9596 | 0.054451 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2882 | 32.1922 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9596 | 0.054451 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2882 | 1965 | 3288.2484 | 0.97923 | 1.0985 | 0.0054333 | 32.1922
1.966 | 2.0698 | 0.056629 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3754 | 32.474 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9606 | 0.054452 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2908 | 32.2004 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9606 | 0.054452 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2908 | 32.2004 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9606 | 0.054452 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2908 | 1966 | 3290.7709 | 0.97923 | 1.0985 | 0.0054333 | 32.2004
1.967 | 2.0709 | 0.05663 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.378 | 32.4823 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9616 | 0.054453 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2933 | 32.2086 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9616 | 0.054453 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2933 | 32.2086 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9616 | 0.054453 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97923 | 3.2933 | 1967 | 3293.294 | 0.97923 | 1.0985 | 0.0054333 | 32.2086
1.968 | 2.0719 | 0.056631 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3805 | 32.4906 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9626 | 0.054454 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.2958 | 32.2169 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9626 | 0.054454 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.2958 | 32.2169 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9626 | 0.054454 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.2958 | 1968 | 3295.8177 | 0.97924 | 1.0985 | 0.0054333 | 32.2169
1.969 | 2.073 | 0.056631 | 1.1032 | 1.1034 | 1.1034 | 1.1034 | 3.3831 | 32.4988 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9636 | 0.054454 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.2983 | 32.2251 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9636 | 0.054454 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.2983 | 32.2251 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9636 | 0.054454 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.2983 | 1969 | 3298.3421 | 0.97924 | 1.0985 | 0.0054333 | 32.2251
1.97 | 2.074 | 0.056632 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.3857 | 32.5071 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9646 | 0.054455 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3009 | 32.2333 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9646 | 0.054455 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3009 | 32.2333 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9646 | 0.054455 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3009 | 1970 | 3300.8672 | 0.97924 | 1.0985 | 0.0054333 | 32.2333
1.971 | 2.075 | 0.056632 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.3883 | 32.5154 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9656 | 0.054456 | 1.0987 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3034 | 32.2415 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9656 | 0.054456 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3034 | 32.2415 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9656 | 0.054456 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3034 | 1971 | 3303.3928 | 0.97924 | 1.0985 | 0.0054333 | 32.2415
1.972 | 2.0761 | 0.056633 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.3909 | 32.5236 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9666 | 0.054457 | 1.0987 | 1.0986 | 1.0985 | 1.0985 | 0.97924 | 3.3059 | 32.2497 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9666 | 0.054457 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3059 | 32.2497 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9666 | 0.054457 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97924 | 3.3059 | 1972 | 3305.9192 | 0.97924 | 1.0985 | 0.0054333 | 32.2497
1.973 | 2.0771 | 0.056634 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.3934 | 32.5319 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9676 | 0.054457 | 1.0987 | 1.0986 | 1.0985 | 1.0985 | 0.97925 | 3.3084 | 32.258 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9676 | 0.054457 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97925 | 3.3084 | 32.258 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9676 | 0.054457 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97925 | 3.3084 | 1973 | 3308.4461 | 0.97925 | 1.0985 | 0.0054333 | 32.258
1.974 | 2.0782 | 0.056634 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.396 | 32.5401 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9686 | 0.054458 | 1.0987 | 1.0986 | 1.0985 | 1.0985 | 0.97925 | 3.311 | 32.2662 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9686 | 0.054458 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97925 | 3.311 | 32.2662 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9686 | 0.054458 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97925 | 3.311 | 1974 | 3310.9737 | 0.97925 | 1.0985 | 0.0054333 | 32.2662
1.975 | 2.0792 | 0.056635 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.3986 | 32.5484 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9696 | 0.054459 | 1.0987 | 1.0986 | 1.0985 | 1.0985 | 0.97925 | 3.3135 | 32.2744 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9696 | 0.054459 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97925 | 3.3135 | 32.2744 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9696 | 0.054459 | 1.0985 | 1.0985 | 1.0985 | 1.0985 | 0.97925 | 3.3135 | 1975 | 3313.502 | 0.97925 | 1.0985 | 0.0054333 | 32.2744
1.976 | 2.0803 | 0.056636 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4012 | 32.5567 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9706 | 0.05446 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97925 | 3.316 | 32.2826 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9706 | 0.05446 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97925 | 3.316 | 32.2826 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9706 | 0.05446 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97925 | 3.316 | 1976 | 3316.0309 | 0.97925 | 1.0986 | 0.0054333 | 32.2826
1.977 | 2.0813 | 0.056636 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4038 | 32.5649 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9716 | 0.05446 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97925 | 3.3186 | 32.2908 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9716 | 0.05446 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97925 | 3.3186 | 32.2908 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9716 | 0.05446 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97925 | 3.3186 | 1977 | 3318.5604 | 0.97925 | 1.0986 | 0.0054333 | 32.2908
1.978 | 2.0823 | 0.056637 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4064 | 32.5732 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9726 | 0.054461 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3211 | 32.299 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9726 | 0.054461 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3211 | 32.299 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9726 | 0.054461 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3211 | 1978 | 3321.0906 | 0.97926 | 1.0986 | 0.0054333 | 32.299
1.979 | 2.0834 | 0.056637 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.409 | 32.5814 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9736 | 0.054462 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3236 | 32.3072 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9736 | 0.054462 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3236 | 32.3072 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9736 | 0.054462 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3236 | 1979 | 3323.6214 | 0.97926 | 1.0986 | 0.0054333 | 32.3072
1.98 | 2.0844 | 0.056638 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4116 | 32.5896 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9746 | 0.054463 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3262 | 32.3154 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9746 | 0.054463 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3262 | 32.3154 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9746 | 0.054463 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3262 | 1980 | 3326.1529 | 0.97926 | 1.0986 | 0.0054333 | 32.3154
1.981 | 2.0855 | 0.056639 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4141 | 32.5979 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9756 | 0.054463 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3287 | 32.3236 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9756 | 0.054463 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3287 | 32.3236 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9756 | 0.054463 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97926 | 3.3287 | 1981 | 3328.685 | 0.97926 | 1.0986 | 0.0054333 | 32.3236
1.982 | 2.0865 | 0.056639 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4167 | 32.6061 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9766 | 0.054464 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3312 | 32.3318 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9766 | 0.054464 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3312 | 32.3318 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9766 | 0.054464 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3312 | 1982 | 3331.2178 | 0.97927 | 1.0986 | 0.0054333 | 32.3318
1.983 | 2.0875 | 0.05664 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4193 | 32.6144 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9776 | 0.054465 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3338 | 32.34 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9776 | 0.054465 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3338 | 32.34 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9776 | 0.054465 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3338 | 1983 | 3333.7512 | 0.97927 | 1.0986 | 0.0054333 | 32.34
1.984 | 2.0886 | 0.056641 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4219 | 32.6226 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9786 | 0.054466 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3363 | 32.3482 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9786 | 0.054466 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3363 | 32.3482 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9786 | 0.054466 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3363 | 1984 | 3336.2852 | 0.97927 | 1.0986 | 0.0054333 | 32.3482
1.985 | 2.0896 | 0.056641 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4245 | 32.6308 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9796 | 0.054466 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3388 | 32.3564 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9796 | 0.054466 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3388 | 32.3564 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9796 | 0.054466 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3388 | 1985 | 3338.8199 | 0.97927 | 1.0986 | 0.0054333 | 32.3564
1.986 | 2.0907 | 0.056642 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4271 | 32.6391 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9806 | 0.054467 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3414 | 32.3646 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9806 | 0.054467 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3414 | 32.3646 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9806 | 0.054467 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97927 | 3.3414 | 1986 | 3341.3552 | 0.97927 | 1.0986 | 0.0054333 | 32.3646
1.987 | 2.0917 | 0.056642 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4297 | 32.6473 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9816 | 0.054468 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3439 | 32.3728 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9816 | 0.054468 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3439 | 32.3728 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9816 | 0.054468 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3439 | 1987 | 3343.8912 | 0.97928 | 1.0986 | 0.0054333 | 32.3728
1.988 | 2.0927 | 0.056643 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4323 | 32.6555 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9826 | 0.054469 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3464 | 32.3809 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9826 | 0.054469 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3464 | 32.3809 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9826 | 0.054469 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3464 | 1988 | 3346.4278 | 0.97928 | 1.0986 | 0.0054333 | 32.3809
1.989 | 2.0938 | 0.056644 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4349 | 32.6638 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9836 | 0.054469 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.349 | 32.3891 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9836 | 0.054469 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.349 | 32.3891 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9836 | 0.054469 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.349 | 1989 | 3348.965 | 0.97928 | 1.0986 | 0.0054333 | 32.3891
1.99 | 2.0948 | 0.056644 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4375 | 32.672 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9846 | 0.05447 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3515 | 32.3973 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9846 | 0.05447 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3515 | 32.3973 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9846 | 0.05447 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.3515 | 1990 | 3351.5029 | 0.97928 | 1.0986 | 0.0054333 | 32.3973
1.991 | 2.0959 | 0.056645 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4401 | 32.6802 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9856 | 0.054471 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.354 | 32.4055 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9856 | 0.054471 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.354 | 32.4055 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9856 | 0.054471 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97928 | 3.354 | 1991 | 3354.0414 | 0.97928 | 1.0986 | 0.0054333 | 32.4055
1.992 | 2.0969 | 0.056646 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4427 | 32.6884 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9866 | 0.054472 | 1.0987 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3566 | 32.4136 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9866 | 0.054472 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3566 | 32.4136 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9866 | 0.054472 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3566 | 1992 | 3356.5806 | 0.97929 | 1.0986 | 0.0054333 | 32.4136
1.993 | 2.098 | 0.056646 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4453 | 32.6966 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9876 | 0.054472 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3591 | 32.4218 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9876 | 0.054472 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3591 | 32.4218 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9876 | 0.054472 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3591 | 1993 | 3359.1204 | 0.97929 | 1.0986 | 0.0054333 | 32.4218
1.994 | 2.099 | 0.056647 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4479 | 32.7049 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9886 | 0.054473 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3617 | 32.43 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9886 | 0.054473 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3617 | 32.43 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9886 | 0.054473 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3617 | 1994 | 3361.6609 | 0.97929 | 1.0986 | 0.0054333 | 32.43
1.995 | 2.1 | 0.056647 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4505 | 32.7131 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9896 | 0.054474 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3642 | 32.4382 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9896 | 0.054474 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3642 | 32.4382 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9896 | 0.054474 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3642 | 1995 | 3364.202 | 0.97929 | 1.0986 | 0.0054333 | 32.4382
1.996 | 2.1011 | 0.056648 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4531 | 32.7213 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9906 | 0.054475 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3667 | 32.4463 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9906 | 0.054475 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3667 | 32.4463 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9906 | 0.054475 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.97929 | 3.3667 | 1996 | 3366.7437 | 0.97929 | 1.0986 | 0.0054333 | 32.4463
1.997 | 2.1021 | 0.056649 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4557 | 32.7295 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9916 | 0.054475 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3693 | 32.4545 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9916 | 0.054475 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3693 | 32.4545 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9916 | 0.054475 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3693 | 1997 | 3369.2861 | 0.9793 | 1.0986 | 0.0054333 | 32.4545
1.998 | 2.1032 | 0.056649 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4583 | 32.7377 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9926 | 0.054476 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3718 | 32.4627 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9926 | 0.054476 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3718 | 32.4627 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9926 | 0.054476 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3718 | 1998 | 3371.8291 | 0.9793 | 1.0986 | 0.0054333 | 32.4627
1.999 | 2.1042 | 0.05665 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4609 | 32.7459 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9936 | 0.054477 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3744 | 32.4708 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9936 | 0.054477 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3744 | 32.4708 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9936 | 0.054477 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3744 | 1999 | 3374.3727 | 0.9793 | 1.0986 | 0.0054333 | 32.4708
2 | 2.1052 | 0.056651 | 1.1033 | 1.1034 | 1.1034 | 1.1034 | 3.4635 | 32.7541 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9946 | 0.054478 | 1.0988 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3769 | 32.479 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9946 | 0.054478 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3769 | 32.479 | 0.0063 | 0.005 | 0.0054333 | 0.64005 | 1.9946 | 0.054478 | 1.0986 | 1.0986 | 1.0986 | 1.0986 | 0.9793 | 3.3769 | 2000 | 3376.917 | 0.9793 | 1.0986 | 0.0054333 | 32.479

## Graph (hidden)
|  |  | Re/10^5 |  |  |  |  | delta*/L
L/k | Column | L/k |  | L/k =400 | L/k = 600 | L/k = 10^3 | L/k = 2000 | L/k = 4000 | L/k =10^4 | L/k=30000 | L/k = 10^5 | L/k = 10^7
400 | 2 | 400 | 1 | 0.0054 | 0.0054 | 0.0054 | 0.0054 | 0.0054 | 0.0054 | 0.0054 | 0.0054 | 0.0054
600 | 3 | 600 | 1.2 | 0.0051 | 0.0051 | 0.0051 | 0.0051 | 0.0051 | 0.0051 | 0.0051 | 0.0051 | 0.0051
1000 | 4 | 1000 | 1.4 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047 | 0.0047
2000 | 5 | 2000 | 1.6 | 0.0044 | 0.0044 | 0.0044 | 0.0044 | 0.0044 | 0.0044 | 0.0044 | 0.0044 | 0.0044
4000 | 6 | 4000 | 1.8 | 0.0041 | 0.0041 | 0.0041 | 0.0041 | 0.0041 | 0.0041 | 0.0041 | 0.0041 | 0.0041
10000 | 7 | 10000 | 2 | 0.0038 | 0.0038 | 0.0038 | 0.0038 | 0.0038 | 0.0038 | 0.0038 | 0.0038 | 0.0038
30000 | 8 | 30000 | 2.3 | 0.0036 | 0.0036 | 0.0036 | 0.0036 | 0.0036 | 0.0036 | 0.0036 | 0.0036 | 0.0036
100000 | 9 | 100000 | 2.6 | 0.0033 | 0.0033 | 0.0033 | 0.0033 | 0.0033 | 0.0033 | 0.0033 | 0.0033 | 0.0033
10000000 | 10 | 10000000 | 3 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031 | 0.0031
|  |  | 3.5 | 0.0028 | 0.0028 | 0.0028 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027 | 0.0027
Interpolation ratio |  |  | 4 | 0.0029 | 0.0028 | 0.0027 | 0.0026 | 0.0025 | 0.0024 | 0.0023 | 0.0023 | 0.0023
4 |  |  | 4.5 | 0.0035 | 0.0032 | 0.0029 | 0.0026 | 0.0024 | 0.0023 | 0.0022 | 0.0021 | 0.0021
1000 |  |  | 5 | 0.0042 | 0.0038 | 0.0033 | 0.0028 | 0.0025 | 0.0023 | 0.0021 | 0.002 | 0.002
2000 |  |  | 5.5 | 0.005 | 0.0044 | 0.0038 | 0.0032 | 0.0027 | 0.0023 | 0.0021 | 0.002 | 0.002
Ratio = | 0.66667 |  | 6 | 0.0056 | 0.0048 | 0.0041 | 0.0039 | 0.0027 | 0.0024 | 0.0022 | 0.0021 | 0.002
|  |  | 6.5 | 0.006 | 0.0053 | 0.0045 | 0.0036 | 0.003 | 0.0025 | 0.0023 | 0.0022 | 0.0021
|  |  | 7 | 0.0063 | 0.0055 | 0.0047 | 0.0038 | 0.0032 | 0.0026 | 0.0024 | 0.0023 | 0.0022
|  |  | 7.5 | 0.0065 | 0.0057 | 0.0048 | 0.0039 | 0.0033 | 0.0027 | 0.0024 | 0.0023 | 0.0022
|  |  | 8 | 0.0067 | 0.0058 | 0.0049 | 0.004 | 0.0034 | 0.0028 | 0.0025 | 0.0024 | 0.0023
|  |  | 8.5 | 0.0068 | 0.006 | 0.0051 | 0.0042 | 0.0034 | 0.0028 | 0.0025 | 0.0024 | 0.0023
|  |  | 9 | 0.007 | 0.0061 | 0.0052 | 0.0043 | 0.0035 | 0.0029 | 0.0025 | 0.0024 | 0.0023
|  |  | 10 | 0.0072 | 0.0063 | 0.0054 | 0.0044 | 0.0036 | 0.0029 | 0.0026 | 0.0024 | 0.0023
|  |  | 12 | 0.0075 | 0.0065 | 0.0055 | 0.0045 | 0.0037 | 0.003 | 0.0026 | 0.0025 | 0.0023
|  |  | 14 | 0.0077 | 0.0067 | 0.0057 | 0.0046 | 0.0038 | 0.0031 | 0.0027 | 0.0025 | 0.0023
|  |  | 16 | 0.0078 | 0.0068 | 0.0058 | 0.0047 | 0.0039 | 0.0032 | 0.0027 | 0.0025 | 0.0023
|  |  | 18 | 0.0079 | 0.0069 | 0.0059 | 0.0048 | 0.0039 | 0.0032 | 0.0027 | 0.0025 | 0.0023
|  |  | 20 | 0.0081 | 0.0071 | 0.006 | 0.0048 | 0.004 | 0.0032 | 0.0027 | 0.0025 | 0.0023
|  |  | 23 | 0.0082 | 0.0072 | 0.0061 | 0.0049 | 0.0041 | 0.0033 | 0.0027 | 0.0025 | 0.0023
|  |  | 26 | 0.0083 | 0.0073 | 0.0062 | 0.005 | 0.0041 | 0.0033 | 0.0027 | 0.0025 | 0.0022
|  |  | 30 | 0.0084 | 0.0074 | 0.0063 | 0.005 | 0.0042 | 0.0033 | 0.0027 | 0.0024 | 0.0022
|  |  | 35 | 0.0085 | 0.0074 | 0.0063 | 0.0051 | 0.0042 | 0.0033 | 0.0027 | 0.0024 | 0.0022
|  |  | 40 | 0.0086 | 0.0075 | 0.0063 | 0.0051 | 0.0042 | 0.0033 | 0.0027 | 0.0024 | 0.0022
|  |  | 45 | 0.0086 | 0.0075 | 0.0063 | 0.0051 | 0.0042 | 0.0033 | 0.0027 | 0.0024 | 0.0022
|  |  | 50 | 0.0087 | 0.0076 | 0.0064 | 0.0052 | 0.0042 | 0.0033 | 0.0027 | 0.0024 | 0.0021
|  |  | 60 | 0.0087 | 0.0076 | 0.0064 | 0.0052 | 0.0042 | 0.0033 | 0.0027 | 0.0023 | 0.002
|  |  | 70 | 0.0088 | 0.0077 | 0.0065 | 0.0052 | 0.0042 | 0.0033 | 0.0027 | 0.0023 | 0.002
|  |  | 80 | 0.0088 | 0.0077 | 0.0065 | 0.0052 | 0.0043 | 0.0033 | 0.0027 | 0.0023 | 0.0019
|  |  | 90 | 0.0088 | 0.0077 | 0.0065 | 0.0052 | 0.0043 | 0.0033 | 0.0027 | 0.0022 | 0.0018
|  |  | 100 | 0.0088 | 0.0077 | 0.0065 | 0.0052 | 0.0043 | 0.0033 | 0.0027 | 0.0022 | 0.0018
|  |  | 200 | 0.0089 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0027 | 0.0021 | 0.0017
|  |  | 300 | 0.0089 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0027 | 0.0021 | 0.0016
|  |  | 400 | 0.0089 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0027 | 0.002 | 0.0015
|  |  | 500 | 0.0089 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0027 | 0.002 | 0.0014
|  |  | 600 | 0.009 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0026 | 0.002 | 0.0014
|  |  | 700 | 0.009 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0026 | 0.002 | 0.0014
|  |  | 800 | 0.009 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0026 | 0.002 | 0.0013
|  |  | 900 | 0.009 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0026 | 0.002 | 0.0013
|  |  | 1000 | 0.009 | 0.0078 | 0.0066 | 0.0053 | 0.0043 | 0.0033 | 0.0026 | 0.002 | 0.0013